## Equipment Database (hidden)
PH | Preaheater
AS | Hydrator Reactor
BM | Ball Mill
KD | Kiln Drive
KN | Kiln
WF | Weight Feeder
PM | Pump Motor
PC | Pan Conveyor
WP | Water Pump
FV | Flow Valve
IV |  | Pending
DG | Diverter Gate
BV | Bin Vibrator
CA | Air Compresor
VB | Vibrating Bin
HM | Hammer Mill
DF | Ducon Fan
FH | Firing Hood
BC | Belt Conveyor
VF | Vibrating Feeder
VS | Vibrating Screen
FN | Fan
BE | Bucket Elevator
RC | Roll Crusher
RA | Rotary Air Lock
SC | Screw Conveyor
SS | Selector Switch
MS | Motion Switch
DM | Damper
CL | Cooler
TT | Temperature Transmitter
FT | Flow Transmitter
PT | Pressure Transmitter
DI | Digital Input
ZSC | Position Sense Closed
ZSO | Position Sense Opened
AT | Analyzer Transmitter
LS | Limit Switch
IT | Current Transmitter
ST | Speed Transmitter
VT | Vibration Transmitter
LT | Level Transmitter
LL | Level Low Indication (Digital)
LH | Level High Indication (Digital)
LLL | Level Low Low Indication (Digital)
LHH | Level High High Indication (Digital
WT | Weight Transmitter
TE | Temperature Element (Thermocouple)
BS | Bin Screen
WS | Weight Scale
PS | Paddle Switch

## Field Device Key
Field Device Key - AMP Part II Project at Nelson
While adherence to ISA Standards is desirable, legacy equipment identifiers must be maintained for continuity.
First Characters |  | Second Characters |  | Third Optional Characters |  | .
First 2 or 3 characters represent a type of device. |  | A series of numbers in series as shown below for each area. Care should be taken to use current numbers as assigned in the plant. In the case where there are no current numbers then the designer may assign a unique number. |  | The last part is optional and provides additional descriptors or a suffix for multiple IO points.
PH | PreHeater | 5XX | Fuel Handling | ZSC | Position Sense Closed
DM | Damper | 3XX | Stone Feeding | ZSO | Position Sense Opened
KN | Kiln | 4XX | Lime Handling (Front, Back and Dust Blending Systems) | A,B, C | Multiple IO on same device
FN | Fan | 7XX | Hydrator | _1, _2 | Multiple IO on same device
CL | Cooler | 13XX | Kiln 1 Preheater, Kiln, Baghouse, | SV | Solenoid valve - Ex: PH1305SV1
BC | Belt Conveyor | 16XX | Kiln 1 Solid Fuel Components
BE | Bucket Elevator | 23XX | Kiln 2 Preheater, Kiln, Baghouse,
SC | Screw Conveyor | 26XX | Kiln 2 Solid Fuel Components
PC | Apron Pan Conveyor
BM | Ball Mill
KD | Kiln Drive
FV | Flow Valve
TT | Temperature Transmitter
FT | Flow Transmitter
PT | Pressure Transmitter
DI | Digital Input | TAGS
ZSC | Position Sense Closed | XX-XXXX_IT | AMPS
ZSO | Position Sense Opened | XX-XXXX_SPT | SPEED
AT | Analyzer Transmitter | XX-XXXX_ZT | VFD HERTZ / DAMPER POSITION / TPH
SS | Selector Switch | XX-XXXX_LT | LEVEL
LS | Limit Switch | XX-XXXX_DPT | DIFERENTIAL PREASSURE
IT | Current Transmitter | XX-XXXX_PT | PREASSURE
ST | Speed Transmitter | XX-XXXX_TE_OUTLET | TEMPERATURE OUTLET
VT | Vibration Transmitter | XX-XXXX_TE_INLET | TEMPERATURE INLET
LT | Level Transmitter | XX-XXXX_TE | TEMPERATURE
LL | Level Low Indication (Digital) | XX-XXXX_TE_DISCHARGE | TEMPERATURE DISCHARGE
LH | Level High Indication (Digital) | XX-XXXX_TE_OUTBOARD | TEMPERATURE OUTBOARD
LLL | Level Low Low Indication (Digital) | XX-XXXX_TE_FEEDEND | TEMPERATURE FEED END
LHH | Level High High Indication (Digital | XX-XXXX On EtherNet | SPEED DRIVE
VS | Vibratory Screen | XX-XXXX_AUX | AUX / FEEDBACK
VF | Vibratory Feeder | XX-XXXX_COIL | RUN
DG | Diverter Gate | K2FZ01_TT
WT | Weight Transmitter
RA | Rotary Airlock
TE | Temperature Element (Thermocouple)
AS | Hydrator Reactor
HM | HammerMill Motor
PM | Pump Motor
RC | Roll Crusher
SL | SILO
MD | MODULE
ANSI/ISA S5.1

## USCNEL (NEW)
L´Hoist - Nelson Plant. Automation Modernization Project No.: 185
[25 empty] | HOLA |  |  | HOLA
Tags Mapped
ID | AREA | MODULE (PLC5) | RACK (XX) | SLOT (XX) | CHANNEL (ZZ) | MODULE (CLX) | RACK (XX)2 | SLOT (XX)2 | CHANNEL (ZZ)2 | TAG | TAG PLC5 | Syntaxis | DESCRIPTION | Device Type | Notes | EU | V.MIN | V.MAX | LL | L | H | HH | HMI | Tarjeta Nombre | Column1 | Tipo | TAG PLC | TAG IO Controller CLX | Assignation CLX | Programming Comments | TAG AOI | AOI | Column2 | 0=Tag Created 1=Tag Found 2=TagVerified | Nombre de Programa | Task | Nombre de Rutina | AREA2
0 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH1 | 1756-IF16 | 1 | 9 | 0 | VS_432_IT | N42:0 | VS | VS 4432 AMPS FRONT SYSTEM VIBRATORY SCREEN | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 50 | MCR4_R01 | I.Ch | INPUT | VS_432_IT_IO | MCR4_R01:9:I.Ch0Data | VS_432_IT_IO:=MCR4_R01:9:I.Ch0Data; //VS 4432 AMPS FRONT SYSTEM VIBRATORY SCREEN |  | _VS4432_IT | P_AIn | Val | 1 | Front_Handling_TaskD | Task_D | _VS4432_IT | Front handling
1 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH2 | 1756-IF16 | 1 | 9 | 1 | K2FZ01_TE | N42:1 | TT | TEMPERATURE KILN 2 FIRING ZONE |  | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR4_R01 | I.Ch | INPUT | K2FZ01_TE_IO | MCR4_R01:9:I.Ch1Data | K2FZ01_TE_IO:=MCR4_R01:9:I.Ch1Data; //TEMPERATURE KILN 2 FIRING ZONE |  | _K2FZ01_TE | P_AIn | Val | 1 |  |  |  | Kiln 2
2 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH3 | 1756-IF16 | 1 | 9 | 2 | K1FZ01_TE | N42:2 | TT | TEMPERATURE KILN 1 FIRING ZONE |  | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR4_R01 | I.Ch | INPUT | K1FZ01_TE_IO | MCR4_R01:9:I.Ch2Data | K1FZ01_TE_IO:=MCR4_R01:9:I.Ch2Data; //TEMPERATURE KILN 1 FIRING ZONE |  | _K1FZ01_TE | P_AIn | Val | 1 |  |  |  | Kiln 2
3 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH4 | 1756-IF16 | 1 | 9 | 3 |  | N42:3 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:9:I.Ch3Data | //MCR4_R01:9:I.Ch3Data SPARE
4 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH5 | 1756-IF16 | 1 | 9 | 4 | FN2605_ST | N42:4 | FN | FN 2605 VFD HERTZ KILN 2 MILL EXHAUST FAN | FEEDBACK FROM DRIVE | EU: Hertz; V.MIN: 0; V.MAX: 60 | MCR4_R01 | I.Ch | INPUT | FN2605_ST_IO | MCR4_R01:9:I.Ch4Data | FN2605_ST_IO:=MCR4_R01:9:I.Ch4Data; //FN 2605 VFD HERTZ KILN 2 MILL EXHAUST FAN |  | _FN2605_HZ | P_AIn | Val | 1 | Kiln2_Main_TaskD | Task_D | _FN2605_HZ | Kiln 2 exhaust fan Task D
5 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH6 | 1756-IF16 | 1 | 9 | 5 | FN2605_1_IT | N42:5 | FN | FN 2605 VFD AMPS KILN 2 MILL EXHAUST FAN | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 200 | MCR4_R01 | I.Ch | INPUT | FN2605_1_IT_IO | MCR4_R01:9:I.Ch5Data | FN2605_1_IT_IO:=MCR4_R01:9:I.Ch5Data; //FN 2605 VFD AMPS KILN 2 MILL EXHAUST FAN |  | _FN2605_1_IT | P_AIn | Val | 1 |  |  |  | Kiln 2 main task D
6 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH7 | 1756-IF16 | 1 | 9 | 6 | FV2273_ZT | N42:6 | FV | FV 2273 DAMPER POSITION KILN 2 COAL CM DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2273_ZT_IO | MCR4_R01:9:I.Ch6Data | FV2273_ZT_IO:=MCR4_R01:9:I.Ch6Data; //FV 2273 DAMPER POSITION KILN 2 COAL CM DAMPER |  | _FV2273_ZT | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _FV2273_ZT | Kiln 2 solid fuel system task D
7 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH8 | 1756-IF16 | 1 | 9 | 7 | FV2272_ZT | N42:7 | FV | FV 2272 DAMPER POSITION KILN 2 COAL CM TEMPERING TEE | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2272_ZT_IO | MCR4_R01:9:I.Ch7Data | FV2272_ZT_IO:=MCR4_R01:9:I.Ch7Data; //FV 2272 DAMPER POSITION KILN 2 COAL CM TEMPERING TEE |  | _FV2272_ZT | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _FV2272_ZT | Kiln 2 solid fuel system task D
8 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH9 | 1756-IF16 | 1 | 9 | 8 | FV2310N_ZT | N42:8 | FV | FV 2310-N DAMPER POSITION KILN 2 NORTH COOLER DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2310N_ZT_IO | MCR4_R01:9:I.Ch8Data | FV2310N_ZT_IO:=MCR4_R01:9:I.Ch8Data; //FV 2310-N DAMPER POSITION KILN 2 NORTH COOLER DAMPER |  | _FV2310N_ZT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FV2310N_ZT | Discharge cooler Task D
9 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH10 | 1756-IF16 | 1 | 9 | 9 | FV2310S_ZT | N42:9 | FV | FV 2310-S DAMPER POSITION KILN 2 SOUTH COOLER DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2310S_ZT_IO | MCR4_R01:9:I.Ch9Data | FV2310S_ZT_IO:=MCR4_R01:9:I.Ch9Data; //FV 2310-S DAMPER POSITION KILN 2 SOUTH COOLER DAMPER |  | _FV2310S_ZT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FV2310S_ZT | Kiln 2 Discharge cooler task D
10 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH11 | 1756-IF16 | 1 | 9 | 10 | FV2310W_ZT | N42:10 | FV | FV 2310-W DAMPER POSITION KILN 2 WEST COOLER DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2310W_ZT_IO | MCR4_R01:9:I.Ch10Data | FV2310W_ZT_IO:=MCR4_R01:9:I.Ch10Data; //FV 2310-W DAMPER POSITION KILN 2 WEST COOLER DAMPER |  | _FV2310W_ZT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FV2310W_ZT | Kiln 2 Discharge cooler task D
11 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH12 | 1756-IF16 | 1 | 9 | 11 | FV2310E_ZT | N42:11 | FV | FV 2310-E DAMPER POSITION KILN 2 EAST COOLER DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2310E_ZT_IO | MCR4_R01:9:I.Ch11Data | FV2310E_ZT_IO:=MCR4_R01:9:I.Ch11Data; //FV 2310-E DAMPER POSITION KILN 2 EAST COOLER DAMPER |  | _FV2310E_ZT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FV2310E_ZT | Kiln 2 Discharge cooler task D
12 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH13 | 1756-IF16 | 1 | 9 | 12 | FV2211_ZT | N42:12 | FV | FV 2211 DAMPER POSITION KILN 2 AIR/FUEL DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2211_ZT_IO | MCR4_R01:9:I.Ch12Data | FV2211_ZT_IO:=MCR4_R01:9:I.Ch12Data; //FV 2211 DAMPER POSITION KILN 2 AIR/FUEL DAMPER |  | _FV2211_ZT | P_AIn | Val |  |  |  |  | FV 2-211 AIR/FUEL DAMPER CONTROL KILN 2 LAD 203
13 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH14 | 1756-IF16 | 1 | 9 | 13 | FV2228_ZT | N42:13 | FV | FV 2228 DAMPER POSITION KILN 2 COOLER DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2228_ZT_IO | MCR4_R01:9:I.Ch13Data | FV2228_ZT_IO:=MCR4_R01:9:I.Ch13Data; //FV 2228 DAMPER POSITION KILN 2 COOLER DAMPER |  | _FV2228_ZT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FV2228_ZT | Kiln 2 Discharge cooler task D
14 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH15 | 1756-IF16 | 1 | 9 | 14 | FV2220_ZT | N42:14 | FV | FV 2220 DAMPER POSITION KILN 2 TEMP AIR DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2220_ZT_IO | MCR4_R01:9:I.Ch14Data | FV2220_ZT_IO:=MCR4_R01:9:I.Ch14Data; //FV 2220 DAMPER POSITION KILN 2 TEMP AIR DAMPER |  | _FV2220_ZT | P_AIn | Val |  |  |  |  | KILN 2 TEMP AIR DAMPER
15 | MCR4 R1G0M0 | 1771-IFE | 1 | 0 | CH16 | 1756-IF16 | 1 | 9 | 15 | FV2216_ZT | N42:15 | FV | FV 2216 DAMPER POSITION ID FAN INLET DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2216_ZT_IO | MCR4_R01:9:I.Ch15Data | FV2216_ZT_IO:=MCR4_R01:9:I.Ch15Data; //FV 2216 DAMPER POSITION ID FAN INLET DAMPER |  | _FV2216_ZT | P_AIn | Val |  |  |  |  | FN 2314_PBS KILN 2 VFD LAD 207
16 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH1 | 1756-IF16 | 1 | 10 | 0 | FV2215_ZT | N46:0 | FV | FV 2215 DAMPER POSITION KILN 2 TEMPERING AIR DAMPER | BECK ACTUATOR | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | FV2215_ZT_IO | MCR4_R01:10:I.Ch0Data | FV2215_ZT_IO:=MCR4_R01:10:I.Ch0Data; //FV 2215 DAMPER POSITION KILN 2 TEMPERING AIR DAMPER |  | _FV2215_ZT | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _FV2215_ZT | Kiln2 Solid Fuel system Task D
17 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH2 | 1756-IF16 | 1 | 10 | 1 | BE4424_1_IT | N46:1 | BE | BE 4424-1 AMPS FRONT SYSTEM BUCKET ELEVATOR | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 75 | MCR4_R01 | I.Ch | INPUT | BE4424_1_IT_IO | MCR4_R01:10:I.Ch1Data | BE4424_1_IT_IO:=MCR4_R01:10:I.Ch1Data; //BE 4424-1 AMPS FRONT SYSTEM BUCKET ELEVATOR |  | _BE44241_IT | P_AIn | Val | 1 | Front_Handling_TaskD | Task_D | _BE44241_IT | Front Handling Task D
18 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH3 | 1756-IF16 | 1 | 10 | 2 | BE4424_2_IT | N46:2 | BE | BE 4424-2 AMPS FRONT SYSTEM BUCKET ELEVATOR | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 75 | MCR4_R01 | I.Ch | INPUT | BE4424_2_IT_IO | MCR4_R01:10:I.Ch2Data | BE4424_2_IT_IO:=MCR4_R01:10:I.Ch2Data; //BE 4424-2 AMPS FRONT SYSTEM BUCKET ELEVATOR |  | _BE44242_IT | P_AIn | Val | 1 | Front_Handling_TaskD | Task_D | _BE44242_IT | Front Handling Task D
19 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH4 | 1756-IF16 | 1 | 10 | 3 | BC4506_WT | N46:3 | BC | BC 4506 TPH COAL SYSTEM BELT CONVEYOR (0-200 TPH) | RAMSEY BELT SCALE | EU: Tons per Hour; V.MIN: 0; V.MAX: 200 | MCR4_R01 | I.Ch | INPUT | BC4506_WT_IO | MCR4_R01:10:I.Ch3Data | BC4506_WT_IO:=MCR4_R01:10:I.Ch3Data; //BC 4506 TPH COAL SYSTEM BELT CONVEYOR (0-200 TPH) |  | _WS4506_WT | P_AIn | Sts_PV | 1 |  |  |  | Fuel Handling Task D
20 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH5 | 1756-IF16 | 1 | 10 | 4 | BC4504C_WT | N46:4 | BC | BC 4504-C TPH COAL SYSTEM BELT CONVEYOR (0-100 TPH) | RAMSEY BELT SCALE | EU: Tons per Hour; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | BC4504C_WT_IO | MCR4_R01:10:I.Ch4Data | BC4504C_WT_IO:=MCR4_R01:10:I.Ch4Data; //BC 4504-C TPH COAL SYSTEM BELT CONVEYOR (0-100 TPH) |  | _WS4504C_WT | P_AIn | Val | 1 |  |  |  | Fuel Handling Task D
21 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH6 | 1756-IF16 | 1 | 10 | 5 | KD2308_SPT | N46:5 | KD | KD 2308 SPEED KILN 2 DRIVE |  | Notes: KD-2-308 On EtherNet; EU: % Speed; V.MIN: 0; V.MAX: 1.557 | MCR4_R01 | I.Ch | INPUT | KD2308_SPT_IO | MCR4_R01:10:I.Ch5Data | KD2308_SPT_IO:=MCR4_R01:10:I.Ch5Data; //KD 2308 SPEED KILN 2 DRIVE |  | _KD2308_SPT | P_AIn | Val |  |  |  |  | Ladder 223 KILN 2
22 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH7 | 1756-IF16 | 1 | 10 | 6 | KD2308_LT | N46:6 | KD | KD 2308 % LOAD KILN 2 DRIVE |  | Notes: KD-2-308 On EtherNet; EU: % Load; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | KD2308_LT_IO | MCR4_R01:10:I.Ch6Data | KD2308_LT_IO:=MCR4_R01:10:I.Ch6Data; //KD 2308 % LOAD KILN 2 DRIVE |  | _KD2308_LT | P_AIn | Val |  |  |  |  | Ladder 223 KILN 2
23 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH8 | 1756-IF16 | 1 | 10 | 7 | BC401_WT | N46:7 | BC | WF 401 BC RATE (TPH) | RAMSEY BELT SCALE | EU: Tons per Hour; V.MIN: 0; V.MAX: 250 | MCR4_R01 | I.Ch | INPUT | BC401_WT_IO | MCR4_R01:10:I.Ch7Data | BC401_WT_IO:=MCR4_R01:10:I.Ch7Data; //WF 401 BC RATE (TPH) |  | _BC401_WT | P_AIn | Val | 0 |  |  |  | Ladder 352
24 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH9 | 1756-IF16 | 1 | 10 | 8 | KD1308_LT | N46:8 |  | KD 1308 % LOAD KILN 1 DRIVE |  | Notes: KD-2-308 On EtherNet; EU: % Load; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | KD1308_LT_IO | MCR4_R01:10:I.Ch8Data | KD1308_LT_IO:=MCR4_R01:10:I.Ch8Data; //KD 1308 % LOAD KILN 1 DRIVE |  | _KD1308_LT | P_AIn | Val | 1 |  |  |  | Kiln 1 main task D
25 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH10 | 1756-IF16 | 1 | 10 | 9 | WF1601_WT | N46:9 | WF | WF 1601 (TPH) | RAMSEY BELT SCALE | EU: Tons per Hour; V.MIN: 0; V.MAX: 15 | MCR4_R01 | I.Ch | INPUT | WF1601_WT_IO | MCR4_R01:10:I.Ch9Data | WF1601_WT_IO:=MCR4_R01:10:I.Ch9Data; //WF 1601 (TPH) |  | _WT1601_WS | P_AIn | Val | 1 | Kiln1_Solid_Fuel_System_TaskD | Task_D | _WT1601_WS | Kiln 1 solid Fuel system Task D
26 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH11 | 1756-IF16 | 1 | 10 | 10 | BM2602_LT | N46:10 | BM | BM 2602 LEVEL KILN 2 BALL MILL | MICROWAVE LEVELTRANSMITTER | EU: % Level; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | BM2602_LT_IO | MCR4_R01:10:I.Ch10Data | BM2602_LT_IO:=MCR4_R01:10:I.Ch10Data; //BM 2602 LEVEL KILN 2 BALL MILL |  | _BM2602_LT | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _BM2602_LT | Kiln 2 Solid fuel system task D
27 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH12 | 1756-IF16 | 1 | 10 | 11 | WF2601_WT | N46:11 | WF | WF 2601 RATE (TPH) KILN 2 COAL WEIGH FEEDER | RAMSEY BELT SCALE | EU: Tons per Hour; V.MIN: 0; V.MAX: 15 | MCR4_R01 | I.Ch | INPUT | WF2601_WT_IO | MCR4_R01:10:I.Ch11Data | WF2601_WT_IO:=MCR4_R01:10:I.Ch11Data; //WF 2601 RATE (TPH) KILN 2 COAL WEIGH FEEDER |  | _WF2601_FT | P_AIn | Val |  | Kiln2_Solid_Fuel_System_TaskD | Task_D | _WF2601_FT
28 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH13 | 1756-IF16 | 1 | 10 | 12 |  | N46:12 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:10:I.Ch12Data | //MCR4_R01:10:I.Ch12Data SPARE
29 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH14 | 1756-IF16 | 1 | 10 | 13 |  | N46:13 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:10:I.Ch13Data | //MCR4_R01:10:I.Ch13Data SPARE
30 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH15 | 1756-IF16 | 1 | 10 | 14 | KN2261_1_PT | N46:14 | KN | PT 2261 PRESSURE KILN 2 FIRING HOOD DRAFT | ROSEMOUNT | EU: "WC; V.MIN: 0; V.MAX: 1 | MCR4_R01 | I.Ch | INPUT | KN2261_1_PT_IO | MCR4_R01:10:I.Ch14Data | KN2261_1_PT_IO:=MCR4_R01:10:I.Ch14Data; //PT 2261 PRESSURE KILN 2 FIRING HOOD DRAFT |  | _KN2261_1_PT | P_AIn | Val
31 | MCR4 R1G0M1 | 1771-IFE | 1 | 1 | CH16 | 1756-IF16 | 1 | 10 | 15 | FN2312_IT | N46:15 | FN | FN 2312 AMPS KILN 2 COOLER FAN |  | Notes: FN-2312 On EherNet; EU: Ampers; V.MIN: 0; V.MAX: 250 | MCR4_R01 | I.Ch | INPUT | FN2312_IT_IO | MCR4_R01:10:I.Ch15Data | FN2312_IT_IO:=MCR4_R01:10:I.Ch15Data; //FN 2312 AMPS KILN 2 COOLER FAN |  | _FN2312_IT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FN2312_IT | Kiln 2 Discharguecooler Task D
32 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH1 | 1756-IF16 | 1 | 11 | 0 | FN2605_2_IT | N47:0 | FN | FN 2605 AMPS KILN 2 CM EXHAUST FAN | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 200 | MCR4_R01 | I.Ch | INPUT | FN2605_2_IT_IO | MCR4_R01:11:I.Ch0Data | FN2605_2_IT_IO:=MCR4_R01:11:I.Ch0Data; //FN 2605 AMPS KILN 2 CM EXHAUST FAN |  | _FN2605_IT | P_AIn | Val | 1 | Kiln2_Main_TaskD | Task_D | _FN2605_IT | Kiln 2 Main Task D
33 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH2 | 1756-IF16 | 1 | 11 | 1 | BE4423_IT | N47:1 | BE | BE 4423 AMPS FRONT SYSTEM BUCKET ELEVATOR | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 50 | MCR4_R01 | I.Ch | INPUT | BE4423_IT_IO | MCR4_R01:11:I.Ch1Data | BE4423_IT_IO:=MCR4_R01:11:I.Ch1Data; //BE 4423 AMPS FRONT SYSTEM BUCKET ELEVATOR |  | _BE4423_IT | P_AIn | Val | 1 | Silo1A_Recycle_TaskD | Task_D | _BE4423_IT | Silo 1A Recycle Task D
34 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH3 | 1756-IF16 | 1 | 11 | 2 | BM2602_B_LT | N47:2 | BM | KILN 2 BM 2-602 LT LEVEL VIB | MICROWAVE LEVEL TRANSMITTER | EU: % Level; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | BM2602_B_LT_IO | MCR4_R01:11:I.Ch2Data | BM2602_B_LT_IO:=MCR4_R01:11:I.Ch2Data; //KILN 2 BM 2-602 LT LEVEL VIB |  | _BM2602_LT | P_AIn | Val | 0 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _BM2602_LT | BM 2602 RUN KILN 2 BALL MILL
35 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH4 | 1756-IF16 | 1 | 11 | 3 | RC4522_1_IT | N47:3 | RC | RC 4522-1 AMPS COAL SYSTEM ROLL CRUSHER MOTOR #1 | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | RC4522_1_IT_IO | MCR4_R01:11:I.Ch3Data | RC4522_1_IT_IO:=MCR4_R01:11:I.Ch3Data; //RC 4522-1 AMPS COAL SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC4522_1_IT | P_AIn | Val | 1 |  |  |  | Fuel Hadnling
36 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH5 | 1756-IF16 | 1 | 11 | 4 |  | N47:4 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:11:I.Ch4Data | //MCR4_R01:11:I.Ch4Data SPARE
37 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH6 | 1756-IF16 | 1 | 11 | 5 | RC4522_2_IT | N47:5 | RC | RC 4522-2 AMPS COAL SYSTEM ROLL CRUSHER MOTOR #2 | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch | INPUT | RC4522_2_IT_IO | MCR4_R01:11:I.Ch5Data | RC4522_2_IT_IO:=MCR4_R01:11:I.Ch5Data; //RC 4522-2 AMPS COAL SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC4522_2_IT | P_AIn | Val | 1 |  |  |  | Fuel Handling
38 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH7 | 1756-IF16 | 1 | 11 | 6 | SC4413_IT | N47:6 | SC | SC 4413 AMPS FRONT SYSTEM SCREW CONVEYOR | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 50 | MCR4_R01 | I.Ch | INPUT | SC4413_IT_IO | MCR4_R01:11:I.Ch6Data | SC4413_IT_IO:=MCR4_R01:11:I.Ch6Data; //SC 4413 AMPS FRONT SYSTEM SCREW CONVEYOR |  | _SC4413_IT | P_AIn | Val | 1 | Front_Handling_TaskD | Task_D | _SC4413_IT | Front Handling
39 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH8 | 1756-IF16 | 1 | 11 | 7 |  | N47:7 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:11:I.Ch7Data | //MCR4_R01:11:I.Ch7Data SPARE
40 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH9 | 1756-IF16 | 1 | 11 | 8 |  | N47:8 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:11:I.Ch8Data | //MCR4_R01:11:I.Ch8Data SPARE
41 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH10 | 1756-IF16 | 1 | 11 | 9 |  | N47:9 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch | INPUT |  | MCR4_R01:11:I.Ch9Data | //MCR4_R01:11:I.Ch9Data SPARE
42 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH11 | 1756-IF16 | 1 | 11 | 10 | BE521_IT | N47:10 | BE | BE-521 AMPS 4-20mA 0-75AMPS | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 75 | MCR4_R01 | I.Ch | INPUT | BE521_IT_IO | MCR4_R01:11:I.Ch10Data | BE521_IT_IO:=MCR4_R01:11:I.Ch10Data; //BE-521 AMPS 4-20mA 0-75AMPS |  | _BE4521_IT | P_AIn | Val | 1 | Fuel_Handling_TaskD | Task_D | _BE4521_IT | Fuel Handling
43 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH12 | 1756-IF16 | 1 | 11 | 11 | CL310_DPT | N47:11 | CL | PRESSURE KILN 2 COOLER PITOT TUBE DIFFERENTIAL | ROSEMOUNT | EU: "WC; V.MIN: 0; V.MAX: 3 | MCR4_R01 | I.Ch | INPUT | CL310_DPT_IO | MCR4_R01:11:I.Ch11Data | CL310_DPT_IO:=MCR4_R01:11:I.Ch11Data; //PRESSURE KILN 2 COOLER PITOT TUBE DIFFERENTIAL |  | _CL310_DPT | P_AIn | Val | 0
44 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH13 | 1756-IF16 | 1 | 11 | 12 | FN2312_PT | N47:12 | FN | FN 2312 PRESSURE KILN 2 COOLER FAN DISCHARGE | ROSEMOUNT | EU: "WC; V.MIN: 0; V.MAX: 20 | MCR4_R01 | I.Ch | INPUT | FN2312_PT_IO | MCR4_R01:11:I.Ch12Data | FN2312_PT_IO:=MCR4_R01:11:I.Ch12Data; //FN 2312 PRESSURE KILN 2 COOLER FAN DISCHARGE |  | _FN2312_PT | P_AIn | Val | 1 | Kiln2_Discharge_Cooler_TaskD | Task_D | _FN2312_PT | Kiln 2 Dischargue cooler
45 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH14 | 1756-IF16 | 1 | 11 | 13 | BM2602_PT | N47:13 | BM | BM 2602 PRESSURE KILN 2 CM DIFFERENTIAL (PT 2203) | ROSEMOUNT | EU: "WC; V.MIN: 0; V.MAX: 5 | MCR4_R01 | I.Ch | INPUT | BM2602_PT_IO | MCR4_R01:11:I.Ch13Data | BM2602_PT_IO:=MCR4_R01:11:I.Ch13Data; //BM 2602 PRESSURE KILN 2 CM DIFFERENTIAL (PT 2203) |  | _BM2602_PT | P_AIn | Val | 0 |  |  |  | Kiln 2
46 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH15 | 1756-IF16 | 1 | 11 | 14 | KN2261_2_PT | N47:14 | KN | PT 2205 PRESSURE KILN 2 COAL BURNER PRESSURE | ROSEMOUNT | EU: "WC; V.MIN: 0; V.MAX: 10 | MCR4_R01 | I.Ch | INPUT | KN2261_2_PT_IO | MCR4_R01:11:I.Ch14Data | KN2261_2_PT_IO:=MCR4_R01:11:I.Ch14Data; //PT 2205 PRESSURE KILN 2 COAL BURNER PRESSURE |  | _KN2261_2_PT | P_AIn | Val |  |  |  |  | NO ESTA
47 | MCR4 R1G1M0 | 1771-IFE | 1 | 2 | CH16 | 1756-IF16 | 1 | 11 | 15 | BM2602_IT | N47:15 | BM | BM 2602 AMPS KILN 2 COAL BALL MILL | CURRENT TRANSFORMER | EU: Ampers; V.MIN: 0; V.MAX: 75 | MCR4_R01 | I.Ch | INPUT | BM2602_IT_IO | MCR4_R01:11:I.Ch15Data | BM2602_IT_IO:=MCR4_R01:11:I.Ch15Data; //BM 2602 AMPS KILN 2 COAL BALL MILL |  | _BM2602_IT | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _BM2602_IT | Kiln 2 solid fuel system task D
48 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH1+ | 1756-IRT8I | 1 | 13 | 0 | BM2602_1_TE_OUTLET | N55:0 | BM | BM 2602 TEMPERATURE KILN 2 COAL BALL MILL OUTLET | THERMOCOUPLE TYPE J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR4_R01 | I.Ch[ | INPUT | BM2602_1_TE_OUTLET_IO | MCR4_R01:13:I.Ch[0].Data | BM2602_1_TE_OUTLET_IO:=MCR4_R01:13:I.Ch[0].Data; //BM 2602 TEMPERATURE KILN 2 COAL BALL MILL OUTLET |  | _BM2602_1_TE_OUTLET | P_AIn | Val | 0
49 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH2+ | 1756-IRT8I | 1 | REMOVE | 1 |  | N55:1 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[1].Data | //MCR4_R01:REMOVE:I.Ch[1].Data SPARE
50 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH3+ | 1756-IRT8I | 1 | REMOVE | 2 |  | N55:2 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[2].Data | //MCR4_R01:REMOVE:I.Ch[2].Data SPARE
51 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH4+ | 1756-IRT8I | 1 | REMOVE | 3 |  | N55:3 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[3].Data | //MCR4_R01:REMOVE:I.Ch[3].Data SPARE
52 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH5+ | 1756-IRT8I | 1 | 13 | 1 | BM2602_TE_INLET | N55:4 | BM | BM 2602 TEMPERATURE KILN 2 COAL BALL MILL INLET | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR4_R01 | I.Ch[ | INPUT | BM2602_TE_INLET_IO | MCR4_R01:13:I.Ch[1].Data | BM2602_TE_INLET_IO:=MCR4_R01:13:I.Ch[1].Data; //BM 2602 TEMPERATURE KILN 2 COAL BALL MILL INLET |  | _BM2602_TE_INLET | P_AIn | Val | 0
53 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH6+ | 1756-IRT8I | 1 | 13 | 2 | FV2272_TE | N55:5 | FV | FV 2272 TEMPERATURE KILN 2 FUEL CROSS AIR | TC Type J | Notes: Display Only; EU: °F; V.MIN: 0; V.MAX: 100 | MCR4_R01 | I.Ch[ | INPUT | FV2272_TE_IO | MCR4_R01:13:I.Ch[2].Data | FV2272_TE_IO:=MCR4_R01:13:I.Ch[2].Data; //FV 2272 TEMPERATURE KILN 2 FUEL CROSS AIR |  | _FV2272_TE | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _FV2272_TE | Kiln 2 Solid fuel system task D
54 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH7+ | 1756-IRT8I | 1 | 13 | 3 | CL2310_1_TE_DISCHARGE | N55:6 | CL | CO 2-310 TEMPERATURE KILN 2 COOLER DISCHARGE | TC Type J | EU: °F; V.MIN: 0; V.MAX: 2000 | MCR4_R01 | I.Ch[ | INPUT | CL2310_1_TE_DISCHARGE_IO | MCR4_R01:13:I.Ch[3].Data | CL2310_1_TE_DISCHARGE_IO:=MCR4_R01:13:I.Ch[3].Data; //CO 2-310 TEMPERATURE KILN 2 COOLER DISCHARGE |  | _CL2310_1_TE_DISCHARGE | P_AIn | Val | 0
55 | MCR4 R1G1M1 | 1771-IXE | 1 | 3 | CH8+ | 1756-IRT8I | 1 | 13 | 4 | BM2602_TE_OUTBOARD | N55:7 | BM | BM 2602 TEMPERATURE KILN 2 COAL CM OUTBOARD BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 500 | MCR4_R01 | I.Ch[ | INPUT | BM2602_TE_OUTBOARD_IO | MCR4_R01:13:I.Ch[4].Data | BM2602_TE_OUTBOARD_IO:=MCR4_R01:13:I.Ch[4].Data; //BM 2602 TEMPERATURE KILN 2 COAL CM OUTBOARD BEARING |  | _BM2602_TE_OUTBOARD | P_AIn | Val | 0
56 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH1+ | 1756-IRT8I | 1 | 14 | 0 | BM2602_TE_INBOARD | N56:0 | BM | BM 2602 TEMPERATURE KILN 2 COAL CM INBOARD BEARING | TC Type K | EU: °F; V.MIN: 0; V.MAX: 500 | MCR4_R01 | I.Ch[ | INPUT | BM2602_TE_INBOARD_IO | MCR4_R01:14:I.Ch[0].Data | BM2602_TE_INBOARD_IO:=MCR4_R01:14:I.Ch[0].Data; //BM 2602 TEMPERATURE KILN 2 COAL CM INBOARD BEARING |  | _BM2602_TE_INBOARD | P_AIn | Val | 0
57 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH2+ | 1756-IRT8I | 1 | 14 | 1 | CL2310_2_TE_DISCHARGE | N56:1 | CL | CO 2-310 TEMPERATURE KILN 2 COOLER DISCHARGE |  | EU: °F; V.MIN: 0; V.MAX: 2000 | MCR4_R01 | I.Ch[ | INPUT | CL2310_2_TE_DISCHARGE_IO | MCR4_R01:14:I.Ch[1].Data | CL2310_2_TE_DISCHARGE_IO:=MCR4_R01:14:I.Ch[1].Data; //CO 2-310 TEMPERATURE KILN 2 COOLER DISCHARGE |  | CL2310_2_TE_DISCHARGE | P_AIn | Val | 0
58 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH3+ | 1756-IRT8I | 1 | 14 | 2 |  | N56:2 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:14:I.Ch[2].Data | //MCR4_R01:14:I.Ch[2].Data SPARE | bar: Notes
59 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH4+ | 1756-IRT8I | 1 | 14 | 3 | FV2308N_TE | N56:3 | FV | FV 2308-N TEMPERATURE KILN 2 NORTH COOLER |  | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR4_R01 | I.Ch[ | INPUT | FV2308N_TE_IO | MCR4_R01:14:I.Ch[3].Data | FV2308N_TE_IO:=MCR4_R01:14:I.Ch[3].Data; //FV 2308-N TEMPERATURE KILN 2 NORTH COOLER |  | _FV2308N_TE | P_AIn | Val | 1 |  |  |  | Kiln 2 Dischargue coolerTask D
60 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH5+ | 1756-IRT8I | 1 | 14 | 4 | FV2308S_TE | N56:4 | FV | FV 2308-S TEMPERATURE KILN 2 SOUTH COOLER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR4_R01 | I.Ch[ | INPUT | FV2308S_TE_IO | MCR4_R01:14:I.Ch[4].Data | FV2308S_TE_IO:=MCR4_R01:14:I.Ch[4].Data; //FV 2308-S TEMPERATURE KILN 2 SOUTH COOLER |  | _FV2308S_TE | P_AIn | Val | 1 |  |  |  | Kiln 2 Dischargue coolerTask D
61 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH6+ | 1756-IRT8I | 1 | 14 | 5 | FV2308W_TE | N56:5 | FV | FV 2308-W TEMPERATURE KILN 2 WEST COOLER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR4_R01 | I.Ch[ | INPUT | FV2308W_TE_IO | MCR4_R01:14:I.Ch[5].Data | FV2308W_TE_IO:=MCR4_R01:14:I.Ch[5].Data; //FV 2308-W TEMPERATURE KILN 2 WEST COOLER |  | _FV2308W_TE | P_AIn | Val | 1 |  |  |  | Kiln 2 Dischargue coolerTask D
62 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH7+ | 1756-IRT8I | 1 | 14 | 6 | FV2308E_TE | N56:6 | FV | FV 2308-E TEMPERATURE KILN 2 EAST COOLER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR4_R01 | I.Ch[ | INPUT | FV2308E_TE_IO | MCR4_R01:14:I.Ch[6].Data | FV2308E_TE_IO:=MCR4_R01:14:I.Ch[6].Data; //FV 2308-E TEMPERATURE KILN 2 EAST COOLER |  | _FV2308E_TE | P_AIn | Val | 1 |  |  |  | Kiln 2 Dischargue coolerTask D
63 | MCR4 R1G2M0 | 1771-IXE | 1 | 4 | CH8+ | 1756-IRT8I | 1 | REMOVE | 7 |  | N56:7 | [12 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[7].Data | //MCR4_R01:REMOVE:I.Ch[7].Data
64 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH1+ | 1756-IRT8I | 1 | 14 | 7 | BM2602_2_TE_OUTLET | N57:0 | BM | TEMPERATURE KILN 2 SECONDARY AIR #2 Thermocouple | TC Type K | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR4_R01 | I.Ch[ | INPUT | BM2602_2_TE_OUTLET_IO | MCR4_R01:14:I.Ch[7].Data | BM2602_2_TE_OUTLET_IO:=MCR4_R01:14:I.Ch[7].Data; //TEMPERATURE KILN 2 SECONDARY AIR #2 Thermocouple |  | _BM2602_2_TE_OUTLET | P_AIn | Val | 0
65 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH2+ | 1756-IRT8I | 1 | REMOVE | 1 |  | N57:1 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[1].Data | //MCR4_R01:REMOVE:I.Ch[1].Data SPARE
66 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH3+ | 1756-IRT8I | 1 | REMOVE | 2 |  | N57:2 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[2].Data | //MCR4_R01:REMOVE:I.Ch[2].Data SPARE
67 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH4+ | 1756-IRT8I | 1 | REMOVE | 3 |  | N57:3 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[3].Data | //MCR4_R01:REMOVE:I.Ch[3].Data SPARE
68 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH5+ | 1756-IRT8I | 1 | 13 | 5 | FN2605_TE | N57:4 | FN | FN 2605 TEMPERATURE KILN 2 FUEL EXHAUST FAN DUCT | TC Type K | EU: °F; V.MIN: 0; V.MAX: 900 | MCR4_R01 | I.Ch[ | INPUT | FN2605_TE_IO | MCR4_R01:13:I.Ch[5].Data | FN2605_TE_IO:=MCR4_R01:13:I.Ch[5].Data; //FN 2605 TEMPERATURE KILN 2 FUEL EXHAUST FAN DUCT |  | _FN2605_TE_INLET | P_AIn | Val | 1 | Kiln2_Main_TaskD | Task_D | _FN2605_TE_INLET | Kiln 2 Main Task D
69 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH6+ | 1756-IRT8I | 1 | REMOVE | 5 |  | N57:5 |  | SPARE | [10 empty] | MCR4_R01 | I.Ch[ | INPUT |  | MCR4_R01:REMOVE:I.Ch[5].Data | //MCR4_R01:REMOVE:I.Ch[5].Data SPARE
70 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH7+ | 1756-IRT8I | 1 | 13 | 6 | BM1602_TE_FEEDEND | N57:6 | BM | 1-602 FEED END TEMP | TC Type K | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR4_R01 | I.Ch[ | INPUT | BM1602_TE_FEEDEND_IO | MCR4_R01:13:I.Ch[6].Data | BM1602_TE_FEEDEND_IO:=MCR4_R01:13:I.Ch[6].Data; //1-602 FEED END TEMP |  | _BM1602_TE_FEEDEND | P_AIn | Val | 0
71 | MCR4 R1G2M1 | 1771-IXE | 1 | 5 | CH8+ | 1756-IRT8I | 1 | 13 | 7 | BM1602_TE_DISCHARGE | N57:7 | BM | 1-602 DISCHARGE END TEMP | TC Type K | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR4_R01 | I.Ch[ | INPUT | BM1602_TE_DISCHARGE_IO | MCR4_R01:13:I.Ch[7].Data | BM1602_TE_DISCHARGE_IO:=MCR4_R01:13:I.Ch[7].Data; //1-602 DISCHARGE END TEMP |  | _BM1602_TE_DISCHARGE | P_AIn | Val | 0
72 | MCR4 R1G3M0 | 1771-OFE | 1 | 6 | 1 CH1+ | 1756-OF8I | 1 | 12 | 0 | WF2601_SPT | N50:0 | WF | WF 2601 SPEED KILN 2 COAL WEIGH FEEDER | POWERFLEX 252B | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR4_R01 | O.Ch[ | OUTPUT | WF2601_SPT_IO | MCR4_R01:12:O.Ch[0].Data | MCR4_R01:12:O.Ch[0].Data:=WF2601_SPT_IO; //WF 2601 SPEED KILN 2 COAL WEIGH FEEDER |  | _WF2601_SPT | P_VSD | Out_SpeedRef | 1 |  |  |  | VSD NO ESTA
73 | MCR4 R1G3M0 | 1771-OFE | 1 | 6 | 3 CH2+ | 1756-OF8I | 1 | 12 | 1 | VF2311_SPT | N50:1 | VF | VF 2311 SPEED KILN 2 COOLER DISCHARGE VIBRATING FEEDER | SYNTRON FEEDRE | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR4_R01 | O.Ch[ | OUTPUT | VF2311_SPT_IO | MCR4_R01:12:O.Ch[1].Data | MCR4_R01:12:O.Ch[1].Data:=VF2311_SPT_IO; //VF 2311 SPEED KILN 2 COOLER DISCHARGE VIBRATING FEEDER |  | _VF2311_YS | P_DIn | Sts_PV | 1 | Kiln2_Main_TaskB | Task_B | _VF2311_YS | Kiln 2 Dischargue cooler Task B
74 | MCR4 R1G3M0 | 1771-OFE | 1 | 6 | 5 CH3+ | 1756-OF8I | 1 | 12 | 2 | FN2605_SPT | N50:2 | FN | FN 2605 VFD SPEED KILN 2 MILL EXHAUST FAN | POWERFLEX 400 | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR4_R01 | O.Ch[ | OUTPUT | FN2605_SPT_IO | MCR4_R01:12:O.Ch[2].Data | MCR4_R01:12:O.Ch[2].Data:=FN2605_SPT_IO; //FN 2605 VFD SPEED KILN 2 MILL EXHAUST FAN |  | _FN2605_M01 | P_VSD | Out_SpeedRef | 1 |  |  |  | Kiln main Task C
75 | MCR4 R1G3M0 | 1771-OFE | 1 | 6 | 7 CH4+ | 1756-OF8I | 1 | 12 | 3 |  | N50:3 |  | SPARE |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR4_R01 | O.Ch[ | OUTPUT |  | MCR4_R01:12:O.Ch[3].Data | //MCR4_R01:12:O.Ch[3].Data SPARE
76 | [5 empty] | 1756-OF8I | 1 | 12 | 4 |  | N50:4 |  | SPARE | [10 empty] | MCR4_R01 | O.Ch[ | OUTPUT |  | MCR4_R01:12:O.Ch[4].Data | //MCR4_R01:12:O.Ch[4].Data SPARE
77 | [5 empty] | 1756-OF8I | 1 | 12 | 5 |  | N50:5 |  | SPARE | [10 empty] | MCR4_R01 | O.Ch[ | OUTPUT |  | MCR4_R01:12:O.Ch[5].Data | //MCR4_R01:12:O.Ch[5].Data SPARE
78 | [5 empty] | 1756-OF8I | 1 | 12 | 6 |  | N50:6 |  | SPARE | [10 empty] | MCR4_R01 | O.Ch[ | OUTPUT |  | MCR4_R01:12:O.Ch[6].Data | //MCR4_R01:12:O.Ch[6].Data SPARE
79 | [5 empty] | 1756-OF8I | 1 | 12 | 7 |  | N50:7 |  | SPARE | [10 empty] | MCR4_R01 | O.Ch[ | OUTPUT |  | MCR4_R01:12:O.Ch[7].Data | //MCR4_R01:12:O.Ch[7].Data SPARE
80 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 00 | 1756-IA16 | 1 | 0 | 00 | PC4421_MS | I:014/0 | PC | PC 4421 FDBK FRONT SYSTEM PAN CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | PC4421_MS_IO | MCR4_R01:0:I.Data.00 | PC4421_MS_IO:=MCR4_R01:0:I.Data.00; //PC 4421 FDBK FRONT SYSTEM PAN CONVEYOR |  | _PC4421_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _PC4421_MS | Front Handling Tasb B
81 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 01 | 1756-IA16 | 1 | 0 | 01 | RA2612_1_AUX | I:014/1 | RA | RA 2612 AUX FDBK KILN 2 COAL ROTARY AIRLOCK | [10 empty] | MCR4_R01 | I.Data | INPUT | RA2612_1_AUX_IO | MCR4_R01:0:I.Data.01 | RA2612_1_AUX_IO:=MCR4_R01:0:I.Data.01; //RA 2612 AUX FDBK KILN 2 COAL ROTARY AIRLOCK |  | _RA2612_1_M01 | P_Motor | Sts_Running | 1 |  |  |  | Kiln 2 Solid Fuel system Task C
82 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 02 | 1756-IA16 | 1 | 0 | 02 | PC4420_MS | I:014/2 | KD | PC 4420 FDBK FRONT SYSTEM PAN CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | PC4420_MS_IO | MCR4_R01:0:I.Data.02 | PC4420_MS_IO:=MCR4_R01:0:I.Data.02; //PC 4420 FDBK FRONT SYSTEM PAN CONVEYOR |  | _PC4420_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _PC4420_MS | Front Handling Task B | bar: Notes to EU
83 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 03 | 1756-IA16 | 1 | 0 | 03 | SC4413_MS | I:014/3 | KD | SC 4413 FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | SC4413_MS_IO | MCR4_R01:0:I.Data.03 | SC4413_MS_IO:=MCR4_R01:0:I.Data.03; //SC 4413 FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4413_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _SC4413_MS | Front Handling Task B | bar: Notes to EU
84 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 04 | 1756-IA16 | 1 | 0 | 04 | SL401A_LIH | I:014/4 | SI | SILO 1A HI LEVEL FRONT SYSTEM |  | Notes: Display only | MCR4_R01 | I.Data | INPUT | SL401A_LIH_IO | MCR4_R01:0:I.Data.04 | SL401A_LIH_IO:=MCR4_R01:0:I.Data.04; //SILO 1A HI LEVEL FRONT SYSTEM |  | _SL401A_LIH | P_AIn | Val | 1 |  |  |  | Falta agregar Add on
85 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 05 | 1756-IA16 | 1 | 0 | 05 | SL402A_LIH | I:014/5 | SI | SILO 2A HI LEVEL FRONT SYSTEM |  | Notes: Display only | MCR4_R01 | I.Data | INPUT | SL402A_LIH_IO | MCR4_R01:0:I.Data.05 | SL402A_LIH_IO:=MCR4_R01:0:I.Data.05; //SILO 2A HI LEVEL FRONT SYSTEM |  | _SL402A_LIH | P_AIn | Val | 1 |  |  |  | Falta agregar Add on
86 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 06 | 1756-IA16 | 1 | 0 | 06 | SL403A_LIH | I:014/6 | SI | SILO 3A HI LEVEL FRONT SYSTEM |  | Notes: Display only | MCR4_R01 | I.Data | INPUT | SL403A_LIH_IO | MCR4_R01:0:I.Data.06 | SL403A_LIH_IO:=MCR4_R01:0:I.Data.06; //SILO 3A HI LEVEL FRONT SYSTEM |  | _SL403A_LIH | P_AIn | Val | 1 |  |  |  | Falta agregar Add on
87 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 07 | 1756-IA16 | 1 | 0 | 07 |  | I:014/7 |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:0:I.Data.07 | //MCR4_R01:0:I.Data.07 SPARE
88 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 10 | 1756-IA16 | 1 | 0 | 08 | CA4441_AUX | I:014/10 | CA | CA 4441 FDBK LIMEHANDLING AIR COMPRESSOR | [10 empty] | MCR4_R01 | I.Data | INPUT | CA4441_AUX_IO | MCR4_R01:0:I.Data.08 | CA4441_AUX_IO:=MCR4_R01:0:I.Data.08; //CA 4441 FDBK LIMEHANDLING AIR COMPRESSOR |  | _CA4441_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _CA4441_M01 | Front Handling Task C
89 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 11 | 1756-IA16 | 1 | 0 | 09 | WF2601_WQS | I:014/11 | WF | WF 2601 TOTALIZER KILN 2 COAL WEIGH BELT |  | EU: Tons; V.MIN: 0; V.MAX: 300 | MCR4_R01 | I.Data | INPUT | WF2601_WQS_IO | MCR4_R01:0:I.Data.09 | WF2601_WQS_IO:=MCR4_R01:0:I.Data.09; //WF 2601 TOTALIZER KILN 2 COAL WEIGH BELT |  | _WF2601_FT | P_AIn | Val | 1 | Kiln2_Solid_Fuel_System_TaskD | Task_D | _WF2601_FT | KilN Solid Fuel System Task D
90 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 12 | 1756-IA16 | 1 | 0 | 10 | FN2326_AUX | I:014/12 | FN | FN 2326 AUX FDBK KILN 2 H2O COOLING FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN2326_AUX_IO | MCR4_R01:0:I.Data.10 | FN2326_AUX_IO:=MCR4_R01:0:I.Data.10; //FN 2326 AUX FDBK KILN 2 H2O COOLING FAN |  | _FN2326_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _FN2326_M01 | Kiln 2 Main Task C
91 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 13 | 1756-IA16 | 1 | 0 | 11 | WP23261_AUX | I:014/13 | WP | WP 2326-1 AUX FDBK KILN 2 H2O PUMP #2 | [10 empty] | MCR4_R01 | I.Data | INPUT | WP23261_AUX_IO | MCR4_R01:0:I.Data.11 | WP23261_AUX_IO:=MCR4_R01:0:I.Data.11; //WP 2326-1 AUX FDBK KILN 2 H2O PUMP #2 |  | _WP23261_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _WP23261_M01 | Kiln 2 Main Task C
92 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 14 | 1756-IA16 | 1 | 0 | 12 | WP23262_AUX | I:014/14 | WP | WP 2326-2 AUX FDBK KILN 2 H2O PUMP #2 | [10 empty] | MCR4_R01 | I.Data | INPUT | WP23262_AUX_IO | MCR4_R01:0:I.Data.12 | WP23262_AUX_IO:=MCR4_R01:0:I.Data.12; //WP 2326-2 AUX FDBK KILN 2 H2O PUMP #2 |  | _WP23262_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _WP23262_M01 | Kiln 2 Main Task C
93 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 15 | 1756-IA16 | 1 | 0 | 13 | PL00_PAL | I:014/15 | PS | ALARM LOW PLANT AIR PRESSURE | [10 empty] | MCR4_R01 | I.Data | INPUT | PL00_PAL_IO | MCR4_R01:0:I.Data.13 | PL00_PAL_IO:=MCR4_R01:0:I.Data.13; //ALARM LOW PLANT AIR PRESSURE |  | _PL00_PAL | P_DIn | Sts_PV
94 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 16 | 1756-IA16 | 1 | 0 | 14 | BE4423_MS | I:014/16 |  | BE 4423 MOTION SWITCH FRONT SYSTEM BUCKET ELEVATOR |  | Notes: HMI ONLY | MCR4_R01 | I.Data | INPUT | BE4423_MS_IO | MCR4_R01:0:I.Data.14 | BE4423_MS_IO:=MCR4_R01:0:I.Data.14; //BE 4423 MOTION SWITCH FRONT SYSTEM BUCKET ELEVATOR |  | _BE4423_MS | P_DIn | Sts_PV | 1 | Silo1A_Recycle_TaskB | Task_B | _BE4423_MS | Front Handling Task B
95 | MCR4 R1G4M0 | 1771-IAD | 1 | 8 | 17 | 1756-IA16 | 1 | 0 | 15 | WF2601_AUX | I:014/17 | WF | WF 2601 AUX FDBK KILN 2 COAL WEIGH FEEDER | [10 empty] | MCR4_R01 | I.Data | INPUT | WF2601_AUX_IO | MCR4_R01:0:I.Data.15 | WF2601_AUX_IO:=MCR4_R01:0:I.Data.15; //WF 2601 AUX FDBK KILN 2 COAL WEIGH FEEDER |  | _WF2601_M01 | P_VSD | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _WF2601_M01 | Kiln 2 Solid fuel System Task C
96 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-0 | 1756-OA16I | 1 | 5 | 0 |  | O:014/0 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:5:O.Data.0 | //MCR4_R01:5:O.Data.0 SPARE
97 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-1 | 1756-OA16I | 1 | 5 | 1 | FN2308_A_COIL | O:014/1 | FN | FN 2308-A RUN KILN 2 NOSE RING FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN2308_A_COIL_IO | MCR4_R01:5:O.Data.1 | MCR4_R01:5:O.Data.1:=FN2308_A_COIL_IO; //FN 2308-A RUN KILN 2 NOSE RING FAN |  | _FN2308_A_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _FN2308_A_M01 | Kiln 2 Main Task C
98 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-2 | 1756-OA16I | 1 | 5 | 2 | PM2602_1_COIL | O:014/2 | PM | PM 2602-1 RUN KILN 2 HI-LIFT PUMP #1 | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PM2602_1_COIL_IO | MCR4_R01:5:O.Data.2 | MCR4_R01:5:O.Data.2:=PM2602_1_COIL_IO; //PM 2602-1 RUN KILN 2 HI-LIFT PUMP #1 |  | _PM26021_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _PM26021_M01 | Kiln 2 Solid Fuel System Task C
99 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-3 | 1756-OA16I | 1 | 5 | 3 | PM2602_2_COIL | O:014/3 | PM | PM 2602-2 RUN KILN 2 HI-LIFT PUMP #2 | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PM2602_2_COIL_IO | MCR4_R01:5:O.Data.3 | MCR4_R01:5:O.Data.3:=PM2602_2_COIL_IO; //PM 2602-2 RUN KILN 2 HI-LIFT PUMP #2 |  | _PM26022_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _PM26022_M01 | Kiln 2 Solid Fuel System Task C
100 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-4 | 1756-OA16I | 1 | 5 | 4 | RA2606_COIL | O:014/4 | RA | RA 2606 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR4_R01 | O.Data | OUTPUT | RA2606_COIL_IO | MCR4_R01:5:O.Data.4 | MCR4_R01:5:O.Data.4:=RA2606_COIL_IO; //RA 2606 RUN KILN 2 ROTARY AIRLOCK |  | _RA2606_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _RA2606_M01 | Kiln 2 Solid Fuel System Task C | bar: V.MAX to HH
101 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-5 | 1756-OA16I | 1 | 5 | 5 | RA2612_2_COIL | O:014/5 | RA | RA 2612 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR4_R01 | O.Data | OUTPUT | RA2612_2_COIL_IO | MCR4_R01:5:O.Data.5 | MCR4_R01:5:O.Data.5:=RA2612_2_COIL_IO; //RA 2612 RUN KILN 2 ROTARY AIRLOCK |  | _RA2612_2_M01 | P_Motor | PCmd_Start | 1 |  |  |  | Falta agregar Add on | bar: Notes to EU
102 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-6 | 1756-OA16I | 1 | 5 | 6 | WF2601_COIL | O:014/6 | WF | WF 2601 RUN KILN 2 WEIGH FEEDER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | WF2601_COIL_IO | MCR4_R01:5:O.Data.6 | MCR4_R01:5:O.Data.6:=WF2601_COIL_IO; //WF 2601 RUN KILN 2 WEIGH FEEDER |  | _WF2601_M01 | P_VSD | PCmd_StartFwd | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _WF2601_M01 | Kiln 2 Solid Fuel Systema Task C | bar: Notes to EU
103 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-7 | 1756-OA16I | 1 | 5 | 7 |  | O:014/7 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:5:O.Data.7 | //MCR4_R01:5:O.Data.7 SPARE
104 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-10 | 1756-OA16I | 1 | 5 | 8 |  | O:014/10 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:5:O.Data.8 | //MCR4_R01:5:O.Data.8 SPARE
105 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-11 | 1756-OA16I | 1 | 5 | 9 |  | O:014/11 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:5:O.Data.9 | //MCR4_R01:5:O.Data.9 SPARE
106 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-12 | 1756-OA16I | 1 | 5 | 10 |  | O:014/12 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:5:O.Data.10 | //MCR4_R01:5:O.Data.10 SPARE
107 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-13 | 1756-OA16I | 1 | 5 | 11 | VF2311_COIL | O:014/13 | VF | VF 2311 RUN KILN 2 COOLER DISCHARGE VIBRATING FEEDER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | VF2311_COIL_IO | MCR4_R01:5:O.Data.11 | MCR4_R01:5:O.Data.11:=VF2311_COIL_IO; //VF 2311 RUN KILN 2 COOLER DISCHARGE VIBRATING FEEDER |  | _VF2311_M01 | P_VSD | PCmd_StartFwd | 1 | Kiln2_Discharge_Cooler_TaskC | Task_C | _VF2311_M01 | Kiln 2Dischargue Cooler Task C
108 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-14 | 1756-OA16I | 1 | 5 | 12 | FN2326_COIL | O:014/14 | FN | FN 2326 RUN KILN 2 H20 COOLING FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN2326_COIL_IO | MCR4_R01:5:O.Data.12 | MCR4_R01:5:O.Data.12:=FN2326_COIL_IO; //FN 2326 RUN KILN 2 H20 COOLING FAN |  | _FN2326_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _FN2326_M01 | Kiln 2 Main Task C
109 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-15 | 1756-OA16I | 1 | 5 | 13 | WP23261_COIL | O:014/15 | WP | WP 2326-1 RUN KILN 2 H20 PUMP #1 | [10 empty] | MCR4_R01 | O.Data | OUTPUT | WP23261_COIL_IO | MCR4_R01:5:O.Data.13 | MCR4_R01:5:O.Data.13:=WP23261_COIL_IO; //WP 2326-1 RUN KILN 2 H20 PUMP #1 |  | _WP23261_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _WP23261_M01 | Kiln 2 Main Task C
110 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-16 | 1756-OA16I | 1 | 5 | 14 | WP23262_COIL | O:014/16 | WP | WP 2326-2 RUN KILN 2 H20 PUMP #2 | [10 empty] | MCR4_R01 | O.Data | OUTPUT | WP23262_COIL_IO | MCR4_R01:5:O.Data.14 | MCR4_R01:5:O.Data.14:=WP23262_COIL_IO; //WP 2326-2 RUN KILN 2 H20 PUMP #2 |  | _WP23262_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _WP23262_M01 | Kiln 2 Main
111 | MCR4 R1G4M1 | 1771-ODD | 1 | 9 | L1-17 | 1756-OA16I | 1 | 5 | 15 | FN47621_COIL | O:014/17 | FN | FN 4762-1 RUN LIMEHANDLING DC FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN47621_COIL_IO | MCR4_R01:5:O.Data.15 | MCR4_R01:5:O.Data.15:=FN47621_COIL_IO; //FN 4762-1 RUN LIMEHANDLING DC FAN |  | _FN7621_M01 | P_Motor | PCmd_Start | 0 | Front_Handling_TaskC | Task_C | _FN7621_M01 | Lime Handling
112 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 00 | 1756-IA16 | 1 | 1 | 00 | PM46101_AUX | I:015/0 | PM | PM 4610-1 AUX FDBK GENERAL PLANT LGT OFF DIESEL PUMP #1 | [10 empty] | MCR4_R01 | I.Data | INPUT | PM46101_AUX_IO | MCR4_R01:1:I.Data.00 | PM46101_AUX_IO:=MCR4_R01:1:I.Data.00; //PM 4610-1 AUX FDBK GENERAL PLANT LGT OFF DIESEL PUMP #1 |  | _PM46101_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _PM46101_M01 | Kiln 1 Main
113 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 01 | 1756-IA16 | 1 | 1 | 01 | PM46102_AUX | I:015/1 | PM | PM 4610-2 AUX FDBK GENERAL PLANT LGT OFF DIESEL PUMP #2 | [10 empty] | MCR4_R01 | I.Data | INPUT | PM46102_AUX_IO | MCR4_R01:1:I.Data.01 | PM46102_AUX_IO:=MCR4_R01:1:I.Data.01; //PM 4610-2 AUX FDBK GENERAL PLANT LGT OFF DIESEL PUMP #2 |  | _PM46102_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _PM46102_M01 | Kiln 1 Main
114 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 02 | 1756-IA16 | 1 | 1 | 02 | BE44241_MS | I:015/2 | BE | BE 4424-1 FDBK FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE44241_MS_IO | MCR4_R01:1:I.Data.02 | BE44241_MS_IO:=MCR4_R01:1:I.Data.02; //BE 4424-1 FDBK FRONT SYSTEM BUCKET ELEVATOR |  | _BE44241_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _BE44241_MS | Front Handling | bar: Notes
115 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 03 | 1756-IA16 | 1 | 1 | 03 | BE44241_AUX | I:015/3 | BE | BE 4424-1 AUX FDBK FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE44241_AUX_IO | MCR4_R01:1:I.Data.03 | BE44241_AUX_IO:=MCR4_R01:1:I.Data.03; //BE 4424-1 AUX FDBK FRONT SYSTEM BUCKET ELEVATOR |  | _BE44241_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _BE44241_M01 | Front Handling
116 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 04 | 1756-IA16 | 1 | 1 | 04 | BE44242_AUX | I:015/4 | BE | BE 4424-2 AUX FDBK FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE44242_AUX_IO | MCR4_R01:1:I.Data.04 | BE44242_AUX_IO:=MCR4_R01:1:I.Data.04; //BE 4424-2 AUX FDBK FRONT SYSTEM BUCKET ELEVATOR |  | _BE44242_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _BE44242_M01 | Front Handling
117 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 05 | 1756-IA16 | 1 | 1 | 05 | BM2602_FQS | I:015/5 | BM | BM 2602 LUBE COUNTER KILN 2 BALL MILL | [10 empty] | MCR4_R01 | I.Data | INPUT | BM2602_FQS_IO | MCR4_R01:1:I.Data.05 | BM2602_FQS_IO:=MCR4_R01:1:I.Data.05; //BM 2602 LUBE COUNTER KILN 2 BALL MILL |  | _BM2602_FQS | P_DIn | Sts_PV | 0
118 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 06 | 1756-IA16 | 1 | 1 | 06 | BC4504C_WQS | I:015/6 | BC | BC 4504-C 0.1 TON PULSE COAL SYSTEM BELT CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BC4504C_WQS_IO | MCR4_R01:1:I.Data.06 | BC4504C_WQS_IO:=MCR4_R01:1:I.Data.06; //BC 4504-C 0.1 TON PULSE COAL SYSTEM BELT CONVEYOR |  | _BC4504C_WQS | P_DIn | Sts_PV | 0
119 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 07 | 1756-IA16 | 1 | 1 | 07 | BE4423_AUX | I:015/7 | BE | BE 4423 FDBK FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE4423_AUX_IO | MCR4_R01:1:I.Data.07 | BE4423_AUX_IO:=MCR4_R01:1:I.Data.07; //BE 4423 FDBK FRONT SYSTEM BUCKET ELEVATOR |  | _BE4423_M01 | P_Motor | Sts_Running | 1 | Silo1A_Recycle_TaskC | Task_C | _BE4423_M01 | Front Handling
120 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 10 | 1756-IA16 | 1 | 1 | 08 | BC4506_WQS | I:015/10 | BC | BC 4506 0.1 TON PULSE COAL SYSTEM BELT CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BC4506_WQS_IO | MCR4_R01:1:I.Data.08 | BC4506_WQS_IO:=MCR4_R01:1:I.Data.08; //BC 4506 0.1 TON PULSE COAL SYSTEM BELT CONVEYOR |  | _BC4506_WQS | P_DIn | Sts_PV | 0
121 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 11 | 1756-IA16 | 1 | 1 | 09 | BE44242_MS | I:015/11 | BE | BE 4424-2 FDBK FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE44242_MS_IO | MCR4_R01:1:I.Data.09 | BE44242_MS_IO:=MCR4_R01:1:I.Data.09; //BE 4424-2 FDBK FRONT SYSTEM BUCKET ELEVATOR |  | _BE44242_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _BE44242_MS | Front Handing | bar: Notes
122 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 12 | 1756-IA16 | 1 | 1 | 10 | BE4521_JOG_SET | I:015/12 | BE | BE 4521 JOG PLUG IN COAL SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE4521_JOG_SET_IO | MCR4_R01:1:I.Data.10 | BE4521_JOG_SET_IO:=MCR4_R01:1:I.Data.10; //BE 4521 JOG PLUG IN COAL SYSTEM BUCKET ELEVATOR |  | _BE4521_M01 | P_Motor | Sts_Ext | 1 | Fuel_Handling_TaskC | Task_C | _BE4521_M01 | Fuel Handling | bar: Notes
123 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 13 | 1756-IA16 | 1 | 1 | 11 | BE4521_PB_JOG | I:015/13 | BE | BE 4521 JOG COAL SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | I.Data | INPUT | BE4521_PB_JOG_IO | MCR4_R01:1:I.Data.11 | BE4521_PB_JOG_IO:=MCR4_R01:1:I.Data.11; //BE 4521 JOG COAL SYSTEM BUCKET ELEVATOR |  | _BE4521_M01 | P_Motor | Sts_Jogging | 1 | Fuel_Handling_TaskC | Task_C | _BE4521_M01 | Fuel Handling | bar: Notes
124 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 14 | 1756-IA16 | 1 | 1 | 12 | SC4426_MS | I:015/14 | SC | SC 4426 FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | SC4426_MS_IO | MCR4_R01:1:I.Data.12 | SC4426_MS_IO:=MCR4_R01:1:I.Data.12; //SC 4426 FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4426_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _SC4426_MS | Front Handling | bar: Notes
125 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 15 | 1756-IA16 | 1 | 1 | 13 | SC4425_MS | I:015/15 | SC | SC 4425 FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | SC4425_MS_IO | MCR4_R01:1:I.Data.13 | SC4425_MS_IO:=MCR4_R01:1:I.Data.13; //SC 4425 FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4425_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _SC4425_MS | Front Handling | bar: Notes
126 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 16 | 1756-IA16 | 1 | 1 | 14 |  | I:015/16 |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:1:I.Data.14 | //MCR4_R01:1:I.Data.14 SPARE | bar: Notes to EU
127 | MCR4 R1G5M0 | 1771-IAD | 1 | 10 | 17 | 1756-IA16 | 1 | 1 | 15 | SC4426_AUX | I:015/17 | SC | SC 4426 FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | SC4426_AUX_IO | MCR4_R01:1:I.Data.15 | SC4426_AUX_IO:=MCR4_R01:1:I.Data.15; //SC 4426 FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4426_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _SC4426_M01 | Front Handling
128 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-0 | 1756-OA16I | 1 | 6 | 0 | BE44241_COIL | O:015/0 | BE | BE 4424-1 RUN FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BE44241_COIL_IO | MCR4_R01:6:O.Data.0 | MCR4_R01:6:O.Data.0:=BE44241_COIL_IO; //BE 4424-1 RUN FRONT SYSTEM BUCKET ELEVATOR |  | _BE44241_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _BE44241_M01 | Front Handling
129 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-1 | 1756-OA16I | 1 | 6 | 1 | BE44242_COIL | O:015/1 | BE | BE 4424-2 RUN FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BE44242_COIL_IO | MCR4_R01:6:O.Data.1 | MCR4_R01:6:O.Data.1:=BE44242_COIL_IO; //BE 4424-2 RUN FRONT SYSTEM BUCKET ELEVATOR |  | _BE44242_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _BE44242_M01 | Front Handling
130 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-2 | 1756-OA16I | 1 | 6 | 2 | VS4432_COIL | O:015/2 | VS | VS 4432 RUN FRONT SYSTEM VIBRATING SCREEN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | VS4432_COIL_IO | MCR4_R01:6:O.Data.2 | MCR4_R01:6:O.Data.2:=VS4432_COIL_IO; //VS 4432 RUN FRONT SYSTEM VIBRATING SCREEN |  | _VS4432_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _VS4432_M01 | Front Handling
131 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-3 | 1756-OA16I | 1 | 6 | 3 | SC4413_COIL | O:015/3 | SC | SC 4413 RUN FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | SC4413_COIL_IO | MCR4_R01:6:O.Data.3 | MCR4_R01:6:O.Data.3:=SC4413_COIL_IO; //SC 4413 RUN FRONT SYSTEM SCREW CONVEYOR |  | _SC4413_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _SC4413_M01 | Front Handling
132 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-4 | 1756-OA16I | 1 | 6 | 4 | BE4423_COIL | O:015/4 | BE | BE 4423 RUN FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BE4423_COIL_IO | MCR4_R01:6:O.Data.4 | MCR4_R01:6:O.Data.4:=BE4423_COIL_IO; //BE 4423 RUN FRONT SYSTEM BUCKET ELEVATOR |  | _BE4423_M01 | P_Motor | PCmd_Start | 1 | Silo1A_Recycle_TaskC | Task_C | _BE4423_M01 | Front Handling | bar: Notes
133 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-5 | 1756-OA16I | 1 | 6 | 5 | PC4421_COIL | O:015/5 | PC | PC 4421 RUN FRONT SYSTEM PAN CONVEYOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PC4421_COIL_IO | MCR4_R01:6:O.Data.5 | MCR4_R01:6:O.Data.5:=PC4421_COIL_IO; //PC 4421 RUN FRONT SYSTEM PAN CONVEYOR |  | _PC4421_M01 | P_Motor | PCmd_On | 1 | Front_Handling_TaskC | Task_C | _PC4421_M01 | Front Handling
134 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-6 | 1756-OA16I | 1 | 6 | 6 | FN2312_COIL | O:015/6 | FN | FN 2312 RUN KILN 2 COOLER FAN | FN-2312 on EtherNet / Delete this point | Notes: TBD | MCR4_R01 | O.Data | OUTPUT | FN2312_COIL_IO | MCR4_R01:6:O.Data.6 | MCR4_R01:6:O.Data.6:=FN2312_COIL_IO; //FN 2312 RUN KILN 2 COOLER FAN | FN-2312 on Ethernet / Delete this point / TBD | _FN2312_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Discharge_Cooler_TaskC | Task_C | _FN2312_M01 | Kiln 2 Dischargue Cooler
135 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-7 | 1756-OA16I | 1 | 6 | 7 | FN2605_1_COIL | O:015/7 | FN | FN 2605 KILN 2 EXHAUST FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN2605_1_COIL_IO | MCR4_R01:6:O.Data.7 | MCR4_R01:6:O.Data.7:=FN2605_1_COIL_IO; //FN 2605 KILN 2 EXHAUST FAN |  | _FN2605_M01 | P_Motor | PCmd_Start | 1 |  |  |  | Kiln 2 Main | bar: Notes
136 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-10 | 1756-OA16I | 1 | 6 | 8 | BM2602_COIL | O:015/10 | BM | BM 2602 RUN KILN 2 BALL MILL | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BM2602_COIL_IO | MCR4_R01:6:O.Data.8 | MCR4_R01:6:O.Data.8:=BM2602_COIL_IO; //BM 2602 RUN KILN 2 BALL MILL |  | _BM2602_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _BM2602_M01 | Kiln 2 Solid Fuel System
137 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-11 | 1756-OA16I | 1 | 6 | 9 | SC4425_COIL | O:015/11 | SC | SC 4425 RUN FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | SC4425_COIL_IO | MCR4_R01:6:O.Data.9 | MCR4_R01:6:O.Data.9:=SC4425_COIL_IO; //SC 4425 RUN FRONT SYSTEM SCREW CONVEYOR |  | _SC4425_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _SC4425_M01 | Front Handling
138 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-12 | 1756-OA16I | 1 | 6 | 10 | SC4426_COIL | O:015/12 | SC | SC 4426 RUN FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | SC4426_COIL_IO | MCR4_R01:6:O.Data.10 | MCR4_R01:6:O.Data.10:=SC4426_COIL_IO; //SC 4426 RUN FRONT SYSTEM SCREW CONVEYOR |  | _SC4426_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _SC4426_M01 | Front Handling
139 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-13 | 1756-OA16I | 1 | 6 | 11 | VS4432_YAY | O:015/13 | VS | VS 4432 START UP ALARM | [10 empty] | MCR4_R01 | O.Data | OUTPUT | VS4432_YAY_IO | MCR4_R01:6:O.Data.11 | MCR4_R01:6:O.Data.11:=VS4432_YAY_IO; //VS 4432 START UP ALARM |  | _VS4432_YAY | P_Dout | PCmd_On | 1 | Front_Handling_TaskB | Task_B | _VS4432_YAY | Front Handling
140 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-14 | 1756-OA16I | 1 | 6 | 12 | BM2602_YAY | O:015/14 | BM | BM 2602 KILN 2 BALL MILL START UP ALARM | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BM2602_YAY_IO | MCR4_R01:6:O.Data.12 | MCR4_R01:6:O.Data.12:=BM2602_YAY_IO; //BM 2602 KILN 2 BALL MILL START UP ALARM |  | _BM2602_YAY | P_Dout | PCmd_On | 1 | Kiln2_Solid_Fuel_System_TaskB | Task_B | _BM2602_YAY | Kiln 2 Solid Fuel System
141 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-15 | 1756-OA16I | 1 | 6 | 13 | PM46102_COIL | O:015/15 | PM | PM 4610-2 RUN GENERAL PLANT LGT OFF DIESEL PUMP #2 | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PM46102_COIL_IO | MCR4_R01:6:O.Data.13 | MCR4_R01:6:O.Data.13:=PM46102_COIL_IO; //PM 4610-2 RUN GENERAL PLANT LGT OFF DIESEL PUMP #2 |  | _PM46102_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _PM46102_M01 | Kiln 1
142 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-16 | 1756-OA16I | 1 | 6 | 14 |  | O:015/16 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:6:O.Data.14 | //MCR4_R01:6:O.Data.14 SPARE | bar: Notes to EU
143 | MCR4 R1G5M1 | 1771-ODD | 1 | 11 | L1-17 | 1756-OA16I | 1 | 6 | 15 | FN2215_COIL | O:015/17 | FN | FN 2215 RUN KILN 2 BECK FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN2215_COIL_IO | MCR4_R01:6:O.Data.15 | MCR4_R01:6:O.Data.15:=FN2215_COIL_IO; //FN 2215 RUN KILN 2 BECK FAN |  | _FN2215_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _FN2215_M01 | Kin 2
144 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 00 | 1756-IA16 | 1 | 2 | 00 | PC4420_AUX | I:016/0 | PC | PC 4420 AUX FDBK FRONT SYSTEM PAN CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | PC4420_AUX_IO | MCR4_R01:2:I.Data.00 | PC4420_AUX_IO:=MCR4_R01:2:I.Data.00; //PC 4420 AUX FDBK FRONT SYSTEM PAN CONVEYOR |  | _PC4420_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _PC4420_M01 | Front Handling
145 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 01 | 1756-IA16 | 1 | 2 | 01 | FN2605_SSA | I:016/1 | FN | FN 2605 AUTO KILN 2 MILL EXHAUST FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN2605_SSA_IO | MCR4_R01:2:I.Data.01 | FN2605_SSA_IO:=MCR4_R01:2:I.Data.01; //FN 2605 AUTO KILN 2 MILL EXHAUST FAN |  | _FN2605_SSA | P_DIn | Sts_PV | 1 | Kiln2_Main_TaskB | Task_B | _FN2605_SSA | Kiln 2 | bar: Notes
146 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 02 | 1756-IA16 | 1 | 2 | 02 | BE4521_MS | I:016/2 | BE | BE 4521 FUEL SYSTEM BUCKET ELEVATOR MOTION SWITCH | [10 empty] | MCR4_R01 | I.Data | INPUT | BE4521_MS_IO | MCR4_R01:2:I.Data.02 | BE4521_MS_IO:=MCR4_R01:2:I.Data.02; //BE 4521 FUEL SYSTEM BUCKET ELEVATOR MOTION SWITCH |  | _BE4521_MS | P_DIn | Sts_PV | 1 | Fuel_Handling_TaskB | Task_B | _BE4521_MS | Fuel Handling | bar: Notes
147 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 03 | 1756-IA16 | 1 | 2 | 03 |  | I:016/3 |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:2:I.Data.03 | //MCR4_R01:2:I.Data.03 SPARE | bar: Notes to EU
148 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 04 | 1756-IA16 | 1 | 2 | 04 | FN2308_A_AUX | I:016/4 | FN | FN 2308-A AUX FDBK KILN 2 NOSE RING FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN2308_A_AUX_IO | MCR4_R01:2:I.Data.04 | FN2308_A_AUX_IO:=MCR4_R01:2:I.Data.04; //FN 2308-A AUX FDBK KILN 2 NOSE RING FAN |  | _FN2308_A_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _FN2308_A_M01 | Kin 2 Solid Fuel System
149 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 05 | 1756-IA16 | 1 | 2 | 05 | PM26021_AUX | I:016/5 | PM | PM 2602-1 AUX FDBK KILN 2 HI LIFT PUMP #1 | [10 empty] | MCR4_R01 | I.Data | INPUT | PM26021_AUX_IO | MCR4_R01:2:I.Data.05 | PM26021_AUX_IO:=MCR4_R01:2:I.Data.05; //PM 2602-1 AUX FDBK KILN 2 HI LIFT PUMP #1 |  | _PM26021_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _PM26021_M01 | Kin 2 Solid Fuel System
150 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 06 | 1756-IA16 | 1 | 2 | 06 | PM26022_AUX | I:016/6 | PM | PM 2602-2 AUX FDBK KILN 2 HI LIFT PUMP #2 | [10 empty] | MCR4_R01 | I.Data | INPUT | PM26022_AUX_IO | MCR4_R01:2:I.Data.06 | PM26022_AUX_IO:=MCR4_R01:2:I.Data.06; //PM 2602-2 AUX FDBK KILN 2 HI LIFT PUMP #2 |  | _PM26022_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _PM26022_M01 | Kin 2 Solid Fuel System
151 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 07 | 1756-IA16 | 1 | 2 | 07 | RA2606_AUX | I:016/7 | RA | RA 2606 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR4_R01 | I.Data | INPUT | RA2606_AUX_IO | MCR4_R01:2:I.Data.07 | RA2606_AUX_IO:=MCR4_R01:2:I.Data.07; //RA 2606 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA2606_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _RA2606_M01 | Kin 2 Solid Fuel System
152 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 10 | 1756-IA16 | 1 | 2 | 08 | FN2215_AUX | I:016/10 | FN | FN 2215 AUX FDBK KILN 2 BECK FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN2215_AUX_IO | MCR4_R01:2:I.Data.08 | FN2215_AUX_IO:=MCR4_R01:2:I.Data.08; //FN 2215 AUX FDBK KILN 2 BECK FAN |  | _FN2215_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _FN2215_M01 | Kiln 2
153 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 11 | 1756-IA16 | 1 | 2 | 09 |  | I:016/11 |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:2:I.Data.09 | //MCR4_R01:2:I.Data.09 SPARE | bar: Notes to EU
154 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 12 | 1756-IA16 | 1 | 2 | 10 | PC4421_AUX | I:016/12 | PC | PC 4421 AUX FDBK FRONT SYSTEM PAN CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | PC4421_AUX_IO | MCR4_R01:2:I.Data.10 | PC4421_AUX_IO:=MCR4_R01:2:I.Data.10; //PC 4421 AUX FDBK FRONT SYSTEM PAN CONVEYOR |  | _PC4421_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _PC4421_M01 | Back Handling
155 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 13 | 1756-IA16 | 1 | 2 | 11 | VF2311_AUX | I:016/13 | VF | VF 2311 AUX FDBK KILN 2 COOLER DISCHARGE VIBRATING FEEDER | [10 empty] | MCR4_R01 | I.Data | INPUT | VF2311_AUX_IO | MCR4_R01:2:I.Data.11 | VF2311_AUX_IO:=MCR4_R01:2:I.Data.11; //VF 2311 AUX FDBK KILN 2 COOLER DISCHARGE VIBRATING FEEDER |  | _VF2311_M01 | P_VSD | Sts_Running | 1 | Kiln2_Discharge_Cooler_TaskC | Task_C | _VF2311_M01 | Kiln 2 Dischargue cooler
156 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 14 | 1756-IA16 | 1 | 2 | 12 | RA2612_AUX | I:016/14 | RA | RA 2612 AUX FDBK KILN 2 COAL COAL MILL ROTARY AIRLOCK | [10 empty] | MCR4_R01 | I.Data | INPUT | RA2612_AUX_IO | MCR4_R01:2:I.Data.12 | RA2612_AUX_IO:=MCR4_R01:2:I.Data.12; //RA 2612 AUX FDBK KILN 2 COAL COAL MILL ROTARY AIRLOCK | // MCR4_R01:2:I.Data.12; Pending to review | _RA2612_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _RA2612_M01 | Lkiln 2 Soid fuel System
157 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 15 | 1756-IA16 | 1 | 2 | 13 | FN4437B_AUX | I:016/15 | FN | FN 4437 AUX FDBK FRONT SYSTEM DUST COLLECTOR FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN4437B_AUX_IO | MCR4_R01:2:I.Data.13 | FN4437B_AUX_IO:=MCR4_R01:2:I.Data.13; //FN 4437 AUX FDBK FRONT SYSTEM DUST COLLECTOR FAN |  | _FN4437B_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _FN4437B_M01 | Front Handling
158 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 16 | 1756-IA16 | 1 | 2 | 14 | VS4432_AUX | I:016/16 | VS | VS 4432 AUX FDBK FRONT SYSTEM VIBRATING SCREEN | [10 empty] | MCR4_R01 | I.Data | INPUT | VS4432_AUX_IO | MCR4_R01:2:I.Data.14 | VS4432_AUX_IO:=MCR4_R01:2:I.Data.14; //VS 4432 AUX FDBK FRONT SYSTEM VIBRATING SCREEN |  | _VS4432_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _VS4432_M01 | Front Handling
159 | MCR4 R1G6M0 | 1771-IAD | 1 | 12 | 17 | 1756-IA16 | 1 | 2 | 15 | SC4413_AUX | I:016/17 | SC | SC 4413 AUX FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | SC4413_AUX_IO | MCR4_R01:2:I.Data.15 | SC4413_AUX_IO:=MCR4_R01:2:I.Data.15; //SC 4413 AUX FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4413_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _SC4413_M01 | Front Handling
160 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-0 | 1756-OA16I | 1 | 7 | 0 |  | O:016/0 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:7:O.Data.0 | //MCR4_R01:7:O.Data.0 SPARE
161 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-1 | 1756-OA16I | 1 | 7 | 1 |  | O:016/1 |  | SPARE | [10 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:7:O.Data.1 | //MCR4_R01:7:O.Data.1 SPARE
162 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-2 | 1756-OA16I | 1 | 7 | 2 | FV2215_XY_A | O:016/2 | FV | FV 2215 OPEN KILN 2 COAL MILL TEMPERING TEE | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2215_XY_A_IO | MCR4_R01:7:O.Data.2 | MCR4_R01:7:O.Data.2:=FV2215_XY_A_IO; //FV 2215 OPEN KILN 2 COAL MILL TEMPERING TEE |  | _FV2215_XY_A | NA | NA | 1 | Kiln2_Main_TaskC | Task_C | _FV2215 | No esta
163 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-3 | 1756-OA16I | 1 | 7 | 3 | FV2215_XY_B | O:016/3 | FV | FV 2215 CLOSE KILN 2 COAL MILL TEMPERING TEE | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2215_XY_B_IO | MCR4_R01:7:O.Data.3 | MCR4_R01:7:O.Data.3:=FV2215_XY_B_IO; //FV 2215 CLOSE KILN 2 COAL MILL TEMPERING TEE |  | _FV2215_XY_B | NA | NA |  | Kiln2_Main_TaskC | Task_C | _FV2215
164 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-4 | 1756-OA16I | 1 | 7 | 4 | FV2220_XY_A | O:016/4 | FV | FV 2220 OPEN KILN 2 TEMPERING AIR DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2220_XY_A_IO | MCR4_R01:7:O.Data.4 | MCR4_R01:7:O.Data.4:=FV2220_XY_A_IO; //FV 2220 OPEN KILN 2 TEMPERING AIR DAMPER |  | _FV2220_XY_A | NA | NA | 1
165 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-5 | 1756-OA16I | 1 | 7 | 5 | FV2220_XY_B | O:016/5 | FV | FV 2220 CLOSE KILN 2 TEMPERING AIR DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2220_XY_B_IO | MCR4_R01:7:O.Data.5 | MCR4_R01:7:O.Data.5:=FV2220_XY_B_IO; //FV 2220 CLOSE KILN 2 TEMPERING AIR DAMPER |  | _FV2220_XY_B | NA | NA
166 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-6 | 1756-OA16I | 1 | 7 | 6 | PM46101_COIL | O:016/6 | PM | PM 4610-1 RUN GENERAL PLANT LGT OFF DIESEL PUMP #1 | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PM46101_COIL_IO | MCR4_R01:7:O.Data.6 | MCR4_R01:7:O.Data.6:=PM46101_COIL_IO; //PM 4610-1 RUN GENERAL PLANT LGT OFF DIESEL PUMP #1 |  | _PM46101_M01 | P_Motor | PCmd_Start |  | Kiln2_Main_TaskC | Task_C | _PM46101_M01 | Kiln 1
167 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-7 | 1756-OA16I | 1 | 7 | 7 | FN4430_COIL | O:016/7 | FN | FN 4430 RUN FRONT SYSTEM DC FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN4430_COIL_IO | MCR4_R01:7:O.Data.7 | MCR4_R01:7:O.Data.7:=FN4430_COIL_IO; //FN 4430 RUN FRONT SYSTEM DC FAN |  | _FN4452_M01 | P_Motor | PCmd_Start | 1 | Dust_Blending_TaskC | Task_C | _FN4452_M01 | Duste Blending
168 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-10 | 1756-OA16I | 1 | 7 | 8 | FN4437B_COIL | O:016/10 | FN | FN 4437-B RUN FRONT SYSTEM DC FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN4437B_COIL_IO | MCR4_R01:7:O.Data.8 | MCR4_R01:7:O.Data.8:=FN4437B_COIL_IO; //FN 4437-B RUN FRONT SYSTEM DC FAN |  | _FN4437B_M01 | P_Motor | PCmd_Start |  | Front_Handling_TaskC | Task_C | _FN4437B_M01 | Front Handling
169 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-11 | 1756-OA16I | 1 | 7 | 9 | CA4441_COIL | O:016/11 | CA | CA 4441 RUN FRONT SYSTEM AIR COMPRESSOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | CA4441_COIL_IO | MCR4_R01:7:O.Data.9 | MCR4_R01:7:O.Data.9:=CA4441_COIL_IO; //CA 4441 RUN FRONT SYSTEM AIR COMPRESSOR |  | _CA4441_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _CA4441_M01 | Front Handling
170 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-12 | 1756-OA16I | 1 | 7 | 10 | BC4514_16_YAY | O:016/12 | HORN | BC 4514 & BC 4516 ALARM HORN FUEL SYSTEM BELT CONVEYORS | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BC4514_16_YAY_IO | MCR4_R01:7:O.Data.10 | MCR4_R01:7:O.Data.10:=BC4514_16_YAY_IO; //BC 4514 & BC 4516 ALARM HORN FUEL SYSTEM BELT CONVEYORS |  | _BC4514_16_YAY | P_Dout | PCmd_On | 1 | Fuel_Handling_TaskB | Task_B | _BC4514_16_YAY | Fuel Handling
171 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-13 | 1756-OA16I | 1 | 7 | 11 |  | O:016/13 |  | BAD CH (SPARE) | Delete | [9 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:7:O.Data.11 | //MCR4_R01:7:O.Data.11 BAD CH (SPARE)
172 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-14 | 1756-OA16I | 1 | 7 | 12 | BM2602_UY | O:016/14 | LB | BM 2602 KILN 2 BALL MILL LUBE | [10 empty] | MCR4_R01 | O.Data | OUTPUT | BM2602_UY_IO | MCR4_R01:7:O.Data.12 | MCR4_R01:7:O.Data.12:=BM2602_UY_IO; //BM 2602 KILN 2 BALL MILL LUBE |  | _BM2602_UY | P_DIn | Sts_PV | 0
173 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-15 | 1756-OA16I | 1 | 7 | 13 | IV2211_15_XY | O:016/15 | IV | IV 2211 & IV 2215 OPEN KILN 2 ISOLATION DAMPERS | [10 empty] | MCR4_R01 | O.Data | OUTPUT | IV2211_15_XY_IO | MCR4_R01:7:O.Data.13 | MCR4_R01:7:O.Data.13:=IV2211_15_XY_IO; //IV 2211 & IV 2215 OPEN KILN 2 ISOLATION DAMPERS |  | _IV2211_15_XY | NA | NA
174 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-16 | 1756-OA16I | 1 | 7 | 14 |  | O:016/16 |  | BAD CH (SPARE) | Delete | [9 empty] | MCR4_R01 | O.Data | OUTPUT |  | MCR4_R01:7:O.Data.14 | //MCR4_R01:7:O.Data.14 BAD CH (SPARE)
175 | MCR4 R1G6M1 | 1771-ODD | 1 | 13 | L1-17 | 1756-OA16I | 1 | 7 | 15 | PL00_YAY_A | O:016/17 | HORN | WARNING HORN FRONT & BACK SYSTEM BELT OR PAN CONVEYORS | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PL00_YAY_A_IO | MCR4_R01:7:O.Data.15 | MCR4_R01:7:O.Data.15:=PL00_YAY_A_IO; //WARNING HORN FRONT & BACK SYSTEM BELT OR PAN CONVEYORS |  | _PL00_YAY_A | P_Dout | PCmd_On
176 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 00 | 1756-IA16 | 1 | 3 | 00 | FN4452_AUX | I:017/0 | FN | FN 4452 FDBK DUST BLENDING DUST COLLECTOR FAN RUNNING | [10 empty] | MCR4_R01 | I.Data | INPUT | FN4452_AUX_IO | MCR4_R01:3:I.Data.00 | FN4452_AUX_IO:=MCR4_R01:3:I.Data.00; //FN 4452 FDBK DUST BLENDING DUST COLLECTOR FAN RUNNING |  | _FN4452_M01 | P_Motor | Sts_Running | 1 | Dust_Blending_TaskC | Task_C | _FN4452_M01 | Duste Blending
177 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 01 | 1756-IA16 | 1 | 3 | 01 | BIN4461_LAH | I:017/1 | BN | DUST BIN 4461 ALARM DUST BLENDING HI LEVEL | [10 empty] | MCR4_R01 | I.Data | INPUT | BIN4461_LAH_IO | MCR4_R01:3:I.Data.01 | BIN4461_LAH_IO:=MCR4_R01:3:I.Data.01; //DUST BIN 4461 ALARM DUST BLENDING HI LEVEL |  | _BIN4461_LAH | P_DIn | Sts_PV | 0
178 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 02 | 1756-IA16 | 1 | 3 | 02 | KN2COALBIN_LAL | I:017/2 | TBD | #2 COAL BIN ALARM KILN 2 COAL LO LEVEL | Not in program///Check HMI / Keep this reserved for this | Notes: TBD | MCR4_R01 | I.Data | INPUT | KN2COALBIN_LAL_IO | MCR4_R01:3:I.Data.02 | KN2COALBIN_LAL_IO:=MCR4_R01:3:I.Data.02; //#2 COAL BIN ALARM KILN 2 COAL LO LEVEL | // Not in program / Check HMI / Keep this res / TBD | _KN2COALBIN_LAL | P_DIn | Sts_PV
179 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 03 | 1756-IA16 | 1 | 3 | 03 | IV211_ZSO | I:017/3 | IV | IV 2211 LIMIT SWITCH KILN 2 ISOLATION DAMPER OPEN | [10 empty] | MCR4_R01 | I.Data | INPUT | IV211_ZSO_IO | MCR4_R01:3:I.Data.03 | IV211_ZSO_IO:=MCR4_R01:3:I.Data.03; //IV 2211 LIMIT SWITCH KILN 2 ISOLATION DAMPER OPEN |  | _IV211_ZSO | NA | NA |  | Kiln2_Solid_Fuel_System_TaskC | Task_C | _IV211_ZS
180 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 04 | 1756-IA16 | 1 | 3 | 04 | IV211_ZSC | I:017/4 | IV | IV 2211 LIMIT SWITCH KILN 2 ISOLATION DAMPER CLOSED | [10 empty] | MCR4_R01 | I.Data | INPUT | IV211_ZSC_IO | MCR4_R01:3:I.Data.04 | IV211_ZSC_IO:=MCR4_R01:3:I.Data.04; //IV 2211 LIMIT SWITCH KILN 2 ISOLATION DAMPER CLOSED |  | _IV211_ZSC | NA | NA |  | Kiln2_Solid_Fuel_System_TaskC | Task_C | _IV211_ZS
181 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 05 | 1756-IA16 | 1 | 3 | 05 | IV2215_ZSO | I:017/5 | IV | IV 2215 LIMIT SWITCH KILN 2 ISOLATION DAMPER OPEN | [10 empty] | MCR4_R01 | I.Data | INPUT | IV2215_ZSO_IO | MCR4_R01:3:I.Data.05 | IV2215_ZSO_IO:=MCR4_R01:3:I.Data.05; //IV 2215 LIMIT SWITCH KILN 2 ISOLATION DAMPER OPEN |  | _IV2215_ZSO | NA | NA |  | Kiln2_Solid_Fuel_System_TaskC | Task_C | _IV2215_ZS
182 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 06 | 1756-IA16 | 1 | 3 | 06 | IV2215_ZSC | I:017/6 | IV | IV 2215 LIMIT SWITCH KILN 2 ISOLATION DAMPER CLOSED | [10 empty] | MCR4_R01 | I.Data | INPUT | IV2215_ZSC_IO | MCR4_R01:3:I.Data.06 | IV2215_ZSC_IO:=MCR4_R01:3:I.Data.06; //IV 2215 LIMIT SWITCH KILN 2 ISOLATION DAMPER CLOSED |  | _IV2215_ZSC | NA | NA |  | Kiln2_Solid_Fuel_System_TaskC | Task_C | _IV2215_ZS
183 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 07 | 1756-IA16 | 1 | 3 | 07 | WF161_WQS | I:017/7 | WF | WF 1601 WEIGH BELT PULSE (0.1 TON / PULSE) | [10 empty] | MCR4_R01 | I.Data | INPUT | WF161_WQS_IO | MCR4_R01:3:I.Data.07 | WF161_WQS_IO:=MCR4_R01:3:I.Data.07; //WF 1601 WEIGH BELT PULSE (0.1 TON / PULSE) |  | _WF161_WQS | P_DIn | Sts_PV
184 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 10 | 1756-IA16 | 1 | 3 | 08 | WF2601_PCD | I:017/10 | WF | WF 2601 WEIGH BELT PLUGGED CHUTE | [10 empty] | MCR4_R01 | I.Data | INPUT | WF2601_PCD_IO | MCR4_R01:3:I.Data.08 | WF2601_PCD_IO:=MCR4_R01:3:I.Data.08; //WF 2601 WEIGH BELT PLUGGED CHUTE |  | _WF2601_PCD | P_AIn | Val | bar: Notes
185 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 11 | 1756-IA16 | 1 | 3 | 09 | FN4430_AUX | I:017/11 | FN | FN 4430 AUX FDBK FRONT SYSTEM DC FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN4430_AUX_IO | MCR4_R01:3:I.Data.09 | FN4430_AUX_IO:=MCR4_R01:3:I.Data.09; //FN 4430 AUX FDBK FRONT SYSTEM DC FAN |  | _FN4452_M01 | P_Motor | Sts_Running | 1 | Dust_Blending_TaskC | Task_C | _FN4452_M01 | Duste Blending
186 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 12 | 1756-IA16 | 1 | 3 | 10 | FN44195_AUX | I:017/12 | FN | FN 4419-5 AUX FDBK FRONT SYSTEM DC FAN | Check Pysically/ Keep this point | Notes: TBD | MCR4_R01 | I.Data | INPUT | FN44195_AUX_IO | MCR4_R01:3:I.Data.10 | FN44195_AUX_IO:=MCR4_R01:3:I.Data.10; //FN 4419-5 AUX FDBK FRONT SYSTEM DC FAN |  | NA | NA | NA
187 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 13 | 1756-IA16 | 1 | 3 | 11 | FN47621_AUX | I:017/13 | FN | FN 4762-1 AUX FDBK LIMEHANDLING DC FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN47621_AUX_IO | MCR4_R01:3:I.Data.11 | FN47621_AUX_IO:=MCR4_R01:3:I.Data.11; //FN 4762-1 AUX FDBK LIMEHANDLING DC FAN |  | _FN47621_M01 | P_Motor | Sts_Running | 0
188 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 14 | 1756-IA16 | 1 | 3 | 12 |  | I:017/14 |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:3:I.Data.12 | //MCR4_R01:3:I.Data.12 SPARE
189 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 15 | 1756-IA16 | 1 | 3 | 13 | FN2605_AUX | I:017/15 | FN | FN 2605 AUX FDBK KILN 2 EXHAUST FAN | [10 empty] | MCR4_R01 | I.Data | INPUT | FN2605_AUX_IO | MCR4_R01:3:I.Data.13 | FN2605_AUX_IO:=MCR4_R01:3:I.Data.13; //FN 2605 AUX FDBK KILN 2 EXHAUST FAN |  | _FN2605_M01 | P_VSD | Sts_Running | 1 |  |  |  | Kiln 2
190 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 16 | 1756-IA16 | 1 | 3 | 14 | BM2602_AUX | I:017/16 | BM | BM 2602 AUX FDBK KILN 2 BALL MILL | [10 empty] | MCR4_R01 | I.Data | INPUT | BM2602_AUX_IO | MCR4_R01:3:I.Data.14 | BM2602_AUX_IO:=MCR4_R01:3:I.Data.14; //BM 2602 AUX FDBK KILN 2 BALL MILL |  | _BM2602_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _BM2602_M01 | Kiln 2 Solid Fuel System
191 | MCR4 R1G7M0 | 1771-IAD | 1 | 14 | 17 | 1756-IA16 | 1 | 3 | 15 | SC4425_AUX | I:017/17 | SC | SC 4425 AUX FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R01 | I.Data | INPUT | SC4425_AUX_IO | MCR4_R01:3:I.Data.15 | SC4425_AUX_IO:=MCR4_R01:3:I.Data.15; //SC 4425 AUX FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4425_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _SC4425_M01 | Front Handling
192 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-0 | 1756-OA16I | 1 | 8 | 0 | FN4452_COIL | O:017/0 | FN | FN 4452 RUN DUST BLENDING DUST COLLECTOR FAN | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FN4452_COIL_IO | MCR4_R01:8:O.Data.0 | MCR4_R01:8:O.Data.0:=FN4452_COIL_IO; //FN 4452 RUN DUST BLENDING DUST COLLECTOR FAN |  | _FN4452_M01 | P_Motor | PCmd_Start |  | Dust_Blending_TaskC | Task_C | _FN4452_M01 | bar: Notes
193 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-1 | 1756-OA16I | 1 | 8 | 1 | FV2310N_XY_A | O:017/1 |  | FV 2310-N OPEN KILN 2 NORTH COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310N_XY_A_IO | MCR4_R01:8:O.Data.1 | MCR4_R01:8:O.Data.1:=FV2310N_XY_A_IO; //FV 2310-N OPEN KILN 2 NORTH COOLER DAMPER |  | _FV2310N_XY_A | NA | NA
194 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-2 | 1756-OA16I | 1 | 8 | 2 | FV2310N_XY_B | O:017/2 |  | FV 2310-N CLOSE KILN 2 NORTH COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310N_XY_B_IO | MCR4_R01:8:O.Data.2 | MCR4_R01:8:O.Data.2:=FV2310N_XY_B_IO; //FV 2310-N CLOSE KILN 2 NORTH COOLER DAMPER |  | _FV2310N_XY_B | NA | NA
195 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-3 | 1756-OA16I | 1 | 8 | 3 | FV2310S_XY_A | O:017/3 |  | FV 2310-S OPEN KILN 2 SOUTH COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310S_XY_A_IO | MCR4_R01:8:O.Data.3 | MCR4_R01:8:O.Data.3:=FV2310S_XY_A_IO; //FV 2310-S OPEN KILN 2 SOUTH COOLER DAMPER |  | _FV2310S_XY_A | NA | NA
196 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-4 | 1756-OA16I | 1 | 8 | 4 | FV2310S_XY_B | O:017/4 |  | FV 2310-S CLOSE KILN 2 SOUTH COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310S_XY_B_IO | MCR4_R01:8:O.Data.4 | MCR4_R01:8:O.Data.4:=FV2310S_XY_B_IO; //FV 2310-S CLOSE KILN 2 SOUTH COOLER DAMPER |  | _FV2310S_XY_B | NA | NA
197 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-5 | 1756-OA16I | 1 | 8 | 5 | FV2310W_XY_A | O:017/5 |  | FV 2310-W OPEN KILN 2 WEST COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310W_XY_A_IO | MCR4_R01:8:O.Data.5 | MCR4_R01:8:O.Data.5:=FV2310W_XY_A_IO; //FV 2310-W OPEN KILN 2 WEST COOLER DAMPER |  | _FV2310W_XY_A | NA | NA
198 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-6 | 1756-OA16I | 1 | 8 | 6 | FV2310W_XY_B | O:017/6 |  | FV 2310-W CLOSE KILN 2 WEST COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310W_XY_B_IO | MCR4_R01:8:O.Data.6 | MCR4_R01:8:O.Data.6:=FV2310W_XY_B_IO; //FV 2310-W CLOSE KILN 2 WEST COOLER DAMPER |  | _FV2310W_XY_B | NA | NA
199 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-7 | 1756-OA16I | 1 | 8 | 7 | FV2310E_XY_A | O:017/7 |  | FV 2310-E OPEN KILN 2 EAST COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310E_XY_A_IO | MCR4_R01:8:O.Data.7 | MCR4_R01:8:O.Data.7:=FV2310E_XY_A_IO; //FV 2310-E OPEN KILN 2 EAST COOLER DAMPER |  | _FV2310E_XY_A | NA | NA
200 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-10 | 1756-OA16I | 1 | 8 | 8 | FV2310E_XY_B | O:017/10 |  | FV 2310-E CLOSE KILN 2 EAST COOLER DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2310E_XY_B_IO | MCR4_R01:8:O.Data.8 | MCR4_R01:8:O.Data.8:=FV2310E_XY_B_IO; //FV 2310-E CLOSE KILN 2 EAST COOLER DAMPER |  | _FV2310E_XY_B | NA | NA
201 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-11 | 1756-OA16I | 1 | 8 | 9 | FV2272_XY_A | O:017/11 |  | FV 2272 OPEN KILN 2 BALL MILL BYPASS DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2272_XY_A_IO | MCR4_R01:8:O.Data.9 | MCR4_R01:8:O.Data.9:=FV2272_XY_A_IO; //FV 2272 OPEN KILN 2 BALL MILL BYPASS DAMPER |  | _FV2272_XY_A | NA | NA |  | Kiln2_Main_TaskC | Task_C | _FV2272
202 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-12 | 1756-OA16I | 1 | 8 | 10 | FV2272_XY_B | O:017/12 |  | FV 2272 CLOSE KILN 2 BALL MILL BYPASS DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2272_XY_B_IO | MCR4_R01:8:O.Data.10 | MCR4_R01:8:O.Data.10:=FV2272_XY_B_IO; //FV 2272 CLOSE KILN 2 BALL MILL BYPASS DAMPER |  | _FV2272_XY_B | NA | NA |  | Kiln2_Main_TaskC | Task_C | _FV2272
203 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-13 | 1756-OA16I | 1 | 8 | 11 | FV2273_XY_A | O:017/13 |  | FV 2273 OPEN KILN 2 COAL BM BYPASS TEMPERING TEE | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2273_XY_A_IO | MCR4_R01:8:O.Data.11 | MCR4_R01:8:O.Data.11:=FV2273_XY_A_IO; //FV 2273 OPEN KILN 2 COAL BM BYPASS TEMPERING TEE |  | _FV2273_XY_A | NA | NA |  | Kiln2_Main_TaskC | Task_C | _FV2273 | bar: Notes
204 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-14 | 1756-OA16I | 1 | 8 | 12 | FV2273_XY_B | O:017/14 |  | FV 2273 CLOSE KILN 2 COAL BM BYPASS TEMPERING TEE | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2273_XY_B_IO | MCR4_R01:8:O.Data.12 | MCR4_R01:8:O.Data.12:=FV2273_XY_B_IO; //FV 2273 CLOSE KILN 2 COAL BM BYPASS TEMPERING TEE |  | _FV2273_XY_B | NA | NA |  | Kiln2_Main_TaskC | Task_C | _FV2273
205 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-15 | 1756-OA16I | 1 | 8 | 13 | FV2211_XY_A | O:017/15 |  | FV 2211 OPEN KILN 2 AIR/FUEL DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2211_XY_A_IO | MCR4_R01:8:O.Data.13 | MCR4_R01:8:O.Data.13:=FV2211_XY_A_IO; //FV 2211 OPEN KILN 2 AIR/FUEL DAMPER |  | _FV2211_XY_A | NA | NA
206 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-16 | 1756-OA16I | 1 | 8 | 14 | FV2211_XY_B | O:017/16 |  | FV 2211 CLOSE KILN 2 AIR/FUEL DAMPER | [10 empty] | MCR4_R01 | O.Data | OUTPUT | FV2211_XY_B_IO | MCR4_R01:8:O.Data.14 | MCR4_R01:8:O.Data.14:=FV2211_XY_B_IO; //FV 2211 CLOSE KILN 2 AIR/FUEL DAMPER |  | _FV2211_XY_B | NA | NA
207 | MCR4 R1G7M1 | 1771-ODD | 1 | 15 | L1-17 | 1756-OA16I | 1 | 8 | 15 | PC4420_COIL | O:017/17 | PC | PC 4420 RUN FRONT SYSTEM PAN CONVEYOR | [10 empty] | MCR4_R01 | O.Data | OUTPUT | PC4420_COIL_IO | MCR4_R01:8:O.Data.15 | MCR4_R01:8:O.Data.15:=PC4420_COIL_IO; //PC 4420 RUN FRONT SYSTEM PAN CONVEYOR |  | _PC4420_M01 | P_Motor | PCmd_On |  | Kiln2_Main_TaskC | Task_C | _PC4420_M01 | Kiln 1
208 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH1+ | 1756-IRT8I | 2 | 8 | 0 | KL1301NE_TE | N43:0 |  | TEMPERATURE KILN 1 UPHILL NE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1301NE_TE_IO | MCR2_R02:8:I.Ch[0].Data | KL1301NE_TE_IO:= MCR2_R02:8:I.Ch[0].Data; //TEMPERATURE KILN 1 UPHILL NE TRUNION BEARING |  | _KL1301NE_TE | P_AIn | Val
209 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH2+ | 1756-IRT8I | 2 | 8 | 1 | KL1301NW_TE | N43:1 |  | TEMPERATURE KILN 1 UPHILL NW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1301NW_TE_IO | MCR2_R02:8:I.Ch[1].Data | KL1301NW_TE_IO:= MCR2_R02:8:I.Ch[1].Data; //TEMPERATURE KILN 1 UPHILL NW TRUNION BEARING |  | _KL1301NW_TE | P_AIn | Val
210 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH3+ | 1756-IRT8I | 2 | 8 | 2 | KL1301SW_TE | N43:2 |  | TEMPERATURE KILN 1 UPHILL SW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1301SW_TE_IO | MCR2_R02:8:I.Ch[2].Data | KL1301SW_TE_IO:= MCR2_R02:8:I.Ch[2].Data; //TEMPERATURE KILN 1 UPHILL SW TRUNION BEARING |  | _KL1301SW_TE | P_AIn | Val
211 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH4+ | 1756-IRT8I | 2 | 8 | 3 | KL1301SE_TE | N43:3 |  | TEMPERATURE KILN 1 UPHILL SE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1301SE_TE_IO | MCR2_R02:8:I.Ch[3].Data | KL1301SE_TE_IO:= MCR2_R02:8:I.Ch[3].Data; //TEMPERATURE KILN 1 UPHILL SE TRUNION BEARING |  | _KL1301SE_TE | P_AIn | Val
212 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH5+ | 1756-IRT8I | 2 | 8 | 4 | KL1302NE_TE | N43:4 |  | TEMPERATURE KILN 1 DOWNHILL NE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1302NE_TE_IO | MCR2_R02:8:I.Ch[4].Data | KL1302NE_TE_IO:= MCR2_R02:8:I.Ch[4].Data; //TEMPERATURE KILN 1 DOWNHILL NE TRUNION BEARING |  | _KL1302NE_TE | P_AIn | Val
213 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH6+ | 1756-IRT8I | 2 | 8 | 5 | KL1302NW_TE | N43:5 |  | TEMPERATURE KILN 1 DOWNHILL NW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1302NW_TE_IO | MCR2_R02:8:I.Ch[5].Data | KL1302NW_TE_IO:= MCR2_R02:8:I.Ch[5].Data; //TEMPERATURE KILN 1 DOWNHILL NW TRUNION BEARING |  | _KL1302NW_TE | P_AIn | Val
214 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH7+ | 1756-IRT8I | 2 | 8 | 6 | KL1302SW_TE | N43:6 |  | TEMPERATURE KILN 1 DOWNHILL SW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1302SW_TE_IO | MCR2_R02:8:I.Ch[6].Data | KL1302SW_TE_IO:= MCR2_R02:8:I.Ch[6].Data; //TEMPERATURE KILN 1 DOWNHILL SW TRUNION BEARING |  | _KL1302SW_TE | P_AIn | Val
215 | MCR2 R2G0M0 | 1771-IXE | 2 | 0 | CH8+ | 1756-IRT8I | 2 | 8 | 7 | KL1302SE_TE | N43:7 |  | TEMPERATURE KILN 1 DOWNHILL SE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL1302SE_TE_IO | MCR2_R02:8:I.Ch[7].Data | KL1302SE_TE_IO:= MCR2_R02:8:I.Ch[7].Data; //TEMPERATURE KILN 1 DOWNHILL SE TRUNION BEARING |  | _KL1302SE_TE | P_AIn | Val
216 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH1+ | 1756-IRT8I | 2 | 9 | 0 | KL2301NE_TE | N44:0 |  | TEMPERATURE KILN 2 UPHILL NE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2301NE_TE_IO | MCR2_R02:9:I.Ch[0].Data | KL2301NE_TE_IO:= MCR2_R02:9:I.Ch[0].Data; //TEMPERATURE KILN 2 UPHILL NE TRUNION BEARING |  | _KL2301NE_TE | P_AIn | Val
217 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH2+ | 1756-IRT8I | 2 | 9 | 1 | KL2301NW_TE | N44:1 |  | TEMPERATURE KILN 2 UPHILL NW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2301NW_TE_IO | MCR2_R02:9:I.Ch[1].Data | KL2301NW_TE_IO:= MCR2_R02:9:I.Ch[1].Data; //TEMPERATURE KILN 2 UPHILL NW TRUNION BEARING |  | _KL2301NW_TE | P_AIn | Val
218 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH3+ | 1756-IRT8I | 2 | 9 | 2 | KL2301SW_TE | N44:2 |  | TEMPERATURE KILN 2 UPHILL SW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2301SW_TE_IO | MCR2_R02:9:I.Ch[2].Data | KL2301SW_TE_IO:= MCR2_R02:9:I.Ch[2].Data; //TEMPERATURE KILN 2 UPHILL SW TRUNION BEARING |  | _KL2301SW_TE | P_AIn | Val
219 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH4+ | 1756-IRT8I | 2 | 9 | 3 | KL2301SE_TE | N44:3 |  | TEMPERATURE KILN 2 UPHILL SE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2301SE_TE_IO | MCR2_R02:9:I.Ch[3].Data | KL2301SE_TE_IO:= MCR2_R02:9:I.Ch[3].Data; //TEMPERATURE KILN 2 UPHILL SE TRUNION BEARING |  | _KL2301SE_TE | P_AIn | Val
220 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH5+ | 1756-IRT8I | 2 | 9 | 4 | KL2302NE_TE | N44:4 |  | TEMPERATURE KILN 2 DOWNHILL NE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2302NE_TE_IO | MCR2_R02:9:I.Ch[4].Data | KL2302NE_TE_IO:= MCR2_R02:9:I.Ch[4].Data; //TEMPERATURE KILN 2 DOWNHILL NE TRUNION BEARING |  | _KL2302NE_TE | P_AIn | Val
221 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH6+ | 1756-IRT8I | 2 | 9 | 5 | KL2302NW_TE | N44:5 |  | TEMPERATURE KILN 2 DOWNHILL NW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2302NW_TE_IO | MCR2_R02:9:I.Ch[5].Data | KL2302NW_TE_IO:= MCR2_R02:9:I.Ch[5].Data; //TEMPERATURE KILN 2 DOWNHILL NW TRUNION BEARING |  | _KL2302NW_TE | P_AIn | Val
222 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH7+ | 1756-IRT8I | 2 | 9 | 6 | KL2302SW_TE | N44:6 |  | TEMPERATURE KILN 2 DOWNHILL SW TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2302SW_TE_IO | MCR2_R02:9:I.Ch[6].Data | KL2302SW_TE_IO:= MCR2_R02:9:I.Ch[6].Data; //TEMPERATURE KILN 2 DOWNHILL SW TRUNION BEARING |  | _KL2302SW_TE | P_AIn | Val
223 | MCR2 R2G0M1 | 1771-IXE | 2 | 1 | CH8+ | 1756-IRT8I | 2 | 9 | 7 | KL2302SE_TE | N44:7 |  | TEMPERATURE KILN 2 DOWNHILL SE TRUNION BEARING | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR2_R02 | I.Ch[ | INPUT | KL2302SE_TE_IO | MCR2_R02:9:I.Ch[7].Data | KL2302SE_TE_IO:= MCR2_R02:9:I.Ch[7].Data; //TEMPERATURE KILN 2 DOWNHILL SE TRUNION BEARING |  | _KL2302SE_TE | P_AIn | Val
224 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH1 | 1756-IF16 | 2 | 7 | 0 | BC8302_IT | N45:0 | BC | BC 8302 AMPS STONE FEED BELT CONVEYOR |  | EU: Ampers; V.MIN: 0; V.MAX: 50 | MCR2_R02 | I.Ch | INPUT | BC8302_IT_IO | MCR2_R02:7:I.Ch0Data | BC8302_IT_IO:= MCR2_R02:7:I.Ch0Data; //BC 8302 AMPS STONE FEED BELT CONVEYOR |  | _BC8302_IT | P_AIn | Val | 1 | Stone_Feed_TaskD | Task_D | _BC8302_IT | Stone Feed
225 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH2 | 1756-IF16 | 2 | 7 | 1 |  | N45:1 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch1Data | // MCR2_R02:7:I.Ch1Data SPARE
226 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH3 | 1756-IF16 | 2 | 7 | 2 |  | N45:2 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch2Data | // MCR2_R02:7:I.Ch2Data SPARE
227 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH4 | 1756-IF16 | 2 | 7 | 3 |  | N45:3 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch3Data | // MCR2_R02:7:I.Ch3Data SPARE
228 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH5 | 1756-IF16 | 2 | 7 | 4 |  | N45:4 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch4Data | // MCR2_R02:7:I.Ch4Data SPARE
229 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH6 | 1756-IF16 | 2 | 7 | 5 |  | N45:5 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch5Data | // MCR2_R02:7:I.Ch5Data SPARE
230 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH7 | 1756-IF16 | 2 | 7 | 6 |  | N45:6 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch6Data | // MCR2_R02:7:I.Ch6Data SPARE
231 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH8 | 1756-IF16 | 2 | 7 | 7 |  | N45:7 |  | *BAD CHANNEL* (SPARE) | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch7Data | // MCR2_R02:7:I.Ch7Data *BAD CHANNEL* (SPARE)
232 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH9 | 1756-IF16 | 2 | 7 | 8 | VS328_IT | N45:8 | VS | 328 CHAT BIN SCREEN AMPS |  | EU: Ampers; V.MIN: 0; V.MAX: 20 | MCR2_R02 | I.Ch | INPUT | VS328_IT_IO | MCR2_R02:7:I.Ch8Data | VS328_IT_IO:= MCR2_R02:7:I.Ch8Data; //328 CHAT BIN SCREEN AMPS |  | _VS328_IT | P_AIn | Val
233 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH10 | 1756-IF16 | 2 | 7 | 9 |  | N45:9 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch9Data | // MCR2_R02:7:I.Ch9Data SPARE | bar: Notes to EU
234 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH11 | 1756-IF16 | 2 | 7 | 10 |  | N45:10 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch10Data | // MCR2_R02:7:I.Ch10Data SPARE | bar: Notes to EU
235 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH12 | 1756-IF16 | 2 | 7 | 11 |  | N45:11 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch11Data | // MCR2_R02:7:I.Ch11Data SPARE | bar: Notes to EU
236 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH13 | 1756-IF16 | 2 | 7 | 12 |  | N45:12 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch12Data | // MCR2_R02:7:I.Ch12Data SPARE | bar: Notes to EU
237 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH14 | 1756-IF16 | 2 | 7 | 13 |  | N45:13 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch13Data | // MCR2_R02:7:I.Ch13Data SPARE | bar: Notes to EU
238 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH15 | 1756-IF16 | 2 | 7 | 14 |  | N45:14 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch14Data | // MCR2_R02:7:I.Ch14Data SPARE
239 | MCR2 R2G1M0 | 1771-IFE | 2 | 2 | CH16 | 1756-IF16 | 2 | 7 | 15 |  | N45:15 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch | INPUT |  | MCR2_R02:7:I.Ch15Data | // MCR2_R02:7:I.Ch15Data SPARE
240 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH1+ | 1756-IRT8I | 2 | 10 | 0 | KL13EXIT_TE | N58:0 |  | TEMPERATURE KILN 1 EXIT | TC Type K | EU: °F; V.MIN: 0; V.MAX: 3000 | MCR2_R02 | I.Ch[ | INPUT | KL13EXIT_TE_IO | MCR2_R02:10:I.Ch[0].Data | KL13EXIT_TE_IO:= MCR2_R02:10:I.Ch[0].Data; //TEMPERATURE KILN 1 EXIT |  | _KL13EXIT_TE | P_AIn | Val
241 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH2+ | 1756-IRT8I | 2 | 10 | 1 | PL00_AT | N58:1 | TK | O2/CO Sample Probes Cooling Tank - Degrees F | TC Type K | Notes: Used in HMI only | MCR2_R02 | I.Ch[ | INPUT | PL00_AT_IO | MCR2_R02:10:I.Ch[1].Data | PL00_AT_IO:= MCR2_R02:10:I.Ch[1].Data; //O2/CO Sample Probes Cooling Tank - Degrees F |  | _PL00_AT | P_DIn | Sts_PV
242 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH3+ | 1756-IRT8I | 2 | 10 | 2 |  | N58:2 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:10:I.Ch[2].Data | // MCR2_R02:10:I.Ch[2].Data SPARE
243 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH4+ | 1756-IRT8I | 2 | 10 | 3 |  | N58:3 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:10:I.Ch[3].Data | // MCR2_R02:10:I.Ch[3].Data SPARE
244 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH5+ | 1756-IRT8I | 2 | 10 | 4 |  | N58:4 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:10:I.Ch[4].Data | // MCR2_R02:10:I.Ch[4].Data SPARE
245 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH6+ | 1756-IRT8I | 2 | 10 | 5 |  | N58:5 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:10:I.Ch[5].Data | // MCR2_R02:10:I.Ch[5].Data SPARE
246 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH7+ | 1756-IRT8I | 2 | 10 | 6 |  | N58:6 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:10:I.Ch[6].Data | // MCR2_R02:10:I.Ch[6].Data SPARE
247 | MCR2 R2G1M1 | 1771-IXE | 2 | 3 | CH8+ | 1756-IRT8I | 2 | 10 | 7 |  | N58:7 |  | SPARE | [10 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:10:I.Ch[7].Data | // MCR2_R02:10:I.Ch[7].Data SPARE
248 | MCR2 R2G2M0 | 1771-IR | 2 | 4 | CH1 | 1756-IRT8I | 2 | 11 | 0 |  | I:022/0 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[0].Data | // MCR2_R02:11:I.Ch[0].Data SPARE
249 | MCR2 R2G2M0 | 1771-IR | 2 | 4 | CH2 | 1756-IRT8I | 2 | 11 | 1 |  | I:022/1 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[1].Data | // MCR2_R02:11:I.Ch[1].Data SPARE
250 | MCR2 R2G2M0 | 1771-IR | 2 | 4 | CH3 | 1756-IRT8I | 2 | 11 | 2 |  | I:022/2 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[2].Data | // MCR2_R02:11:I.Ch[2].Data SPARE
251 | MCR2 R2G2M0 | 1771-IR | 2 | 4 | CH4 | 1756-IRT8I | 2 | 11 | 3 |  | I:022/3 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[3].Data | // MCR2_R02:11:I.Ch[3].Data SPARE
252 | MCR2 R2G2M0 | 1771-IR | 2 | 4 | CH5 | 1756-IRT8I | 2 | 11 | 4 |  | I:022/4 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[4].Data | // MCR2_R02:11:I.Ch[4].Data SPARE
253 | MCR2 R2G2M0 | 1771-IR | 2 | 4 | CH6 | 1756-IRT8I | 2 | 11 | 5 |  | I:022/5 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[5].Data | // MCR2_R02:11:I.Ch[5].Data SPARE
254 | [5 empty] | 1756-IRT8I | 2 | 11 | 6 |  | I:022/6 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[6].Data | // MCR2_R02:11:I.Ch[6].Data SPARE
255 | [5 empty] | 1756-IRT8I | 2 | 11 | 7 |  | I:022/7 |  | SPARE | RTD | [9 empty] | MCR2_R02 | I.Ch[ | INPUT |  | MCR2_R02:11:I.Ch[7].Data | // MCR2_R02:11:I.Ch[7].Data SPARE
256 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 00 | 1756-IA16 | 2 | 0 | 00 | BN210_LAH | I:023/0 | BN | BN 210 CHAT BIN HIGH LEVEL ALARM STONE FEED |  | Notes: For alarm and HMI only | MCR2_R02 | I.Data | INPUT | BN210_LAH_IO | MCR2_R02:0:I.Data.00 | BN210_LAH_IO:= MCR2_R02:0:I.Data.00; //BN 210 CHAT BIN HIGH LEVEL ALARM STONE FEED |  | _BN210_LAH | P_DIn | Sts_PV | 0
257 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 01 | 1756-IA16 | 2 | 0 | 01 | BN318_LAH | I:023/1 | BN | BN318 DUST BIN HIGH LEVEL ALARM KILN 1 |  | Notes: For alarm and HMI only | MCR2_R02 | I.Data | INPUT | BN318_LAH_IO | MCR2_R02:0:I.Data.01 | BN318_LAH_IO:= MCR2_R02:0:I.Data.01; //BN318 DUST BIN HIGH LEVEL ALARM KILN 1 |  | _BN318_LAH | P_DIn | Sts_PV | 0
258 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 02 | 1756-IA16 | 2 | 0 | 02 | LKD_1_SYSTEM | I:023/2 | TBD | LKD SYSTEM | [10 empty] | MCR2_R02 | I.Data | INPUT | LKD_1_SYSTEM_IO | MCR2_R02:0:I.Data.02 | LKD_1_SYSTEM_IO:= MCR2_R02:0:I.Data.02; //LKD SYSTEM |  | _LKD_1_SYSTEM | P_DIn | Sts_PV | 0 | bar: Notes to EU
259 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 03 | 1756-IA16 | 2 | 0 | 03 | LKD_2_SYSTEM | I:023/3 | TBD | LKD SYSTEM | [10 empty] | MCR2_R02 | I.Data | INPUT | LKD_2_SYSTEM_IO | MCR2_R02:0:I.Data.03 | LKD_2_SYSTEM_IO:= MCR2_R02:0:I.Data.03; //LKD SYSTEM |  | _LKD_2_SYSTEM | P_DIn | Sts_PV | 0 | bar: Notes to EU
260 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 04 | 1756-IA16 | 2 | 0 | 04 | TK_02_LAL | I:023/4 | TK | O2/CO SAMPLE PROBE COOLING TANK LEVEL LOW |  | Notes: For alarm and HMI only | MCR2_R02 | I.Data | INPUT | TK_02_LAL_IO | MCR2_R02:0:I.Data.04 | TK_02_LAL_IO:= MCR2_R02:0:I.Data.04; //O2/CO SAMPLE PROBE COOLING TANK LEVEL LOW |  | _TK_02_LAL | P_DIn | Sts_PV
261 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 05 | 1756-IA16 | 2 | 0 | 05 | TK_02_LAH | I:023/5 | TK | O2/CO SAMPLE PROBE COOLING TANK LEVEL HIGH |  | Notes: For alarm and HMI only | MCR2_R02 | I.Data | INPUT | TK_02_LAH_IO | MCR2_R02:0:I.Data.05 | TK_02_LAH_IO:= MCR2_R02:0:I.Data.05; //O2/CO SAMPLE PROBE COOLING TANK LEVEL HIGH |  | _TK_02_LAH | P_DIn | Sts_PV
262 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 06 | 1756-IA16 | 2 | 0 | 06 |  | I:023/6 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.06 | // MCR2_R02:0:I.Data.06 SPARE
263 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 07 | 1756-IA16 | 2 | 0 | 07 |  | I:023/7 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.07 | // MCR2_R02:0:I.Data.07 SPARE
264 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 10 | 1756-IA16 | 2 | 0 | 08 |  | I:023/10 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.08 | // MCR2_R02:0:I.Data.08 SPARE
265 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 11 | 1756-IA16 | 2 | 0 | 09 |  | I:023/11 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.09 | // MCR2_R02:0:I.Data.09 SPARE
266 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 12 | 1756-IA16 | 2 | 0 | 10 |  | I:023/12 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.10 | // MCR2_R02:0:I.Data.10 SPARE
267 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 13 | 1756-IA16 | 2 | 0 | 11 |  | I:023/13 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.11 | // MCR2_R02:0:I.Data.11 SPARE
268 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 14 | 1756-IA16 | 2 | 0 | 12 |  | I:023/14 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.12 | // MCR2_R02:0:I.Data.12 SPARE
269 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 15 | 1756-IA16 | 2 | 0 | 13 |  | I:023/15 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.13 | // MCR2_R02:0:I.Data.13 SPARE
270 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 16 | 1756-IA16 | 2 | 0 | 14 |  | I:023/16 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.14 | // MCR2_R02:0:I.Data.14 SPARE
271 | MCR2 R2G3M0 | 1771-IAD | 2 | 6 | 17 | 1756-IA16 | 2 | 0 | 15 |  | I:023/17 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:0:I.Data.15 | // MCR2_R02:0:I.Data.15 SPARE
272 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 00 | 1756-IA16 | 2 | 1 | 00 | SC1316_AUX | I:024/0 | SC | SC 1316 AUX FDBK KILN 1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | SC1316_AUX_IO | MCR2_R02:1:I.Data.00 | SC1316_AUX_IO:= MCR2_R02:1:I.Data.00; //SC 1316 AUX FDBK KILN 1 DUST SCREW CONVEYOR |  | _SC1316_M01 | P_Motor | Sts_Running | 0
273 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 01 | 1756-IA16 | 2 | 1 | 01 | SC1316A_AUX | I:024/1 | SC | SC 1316-A FDBK KILN 1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | SC1316A_AUX_IO | MCR2_R02:1:I.Data.01 | SC1316A_AUX_IO:= MCR2_R02:1:I.Data.01; //SC 1316-A FDBK KILN 1 DUST SCREW CONVEYOR |  | _SC1316A_M01 | P_Motor | Sts_Running | 0
274 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 02 | 1756-IA16 | 2 | 1 | 02 | BE1317_AUX | I:024/2 | BE | BE 1317 AUX FDBK KILN 1 DUST BUCKET ELEVATOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BE1317_AUX_IO | MCR2_R02:1:I.Data.02 | BE1317_AUX_IO:= MCR2_R02:1:I.Data.02; //BE 1317 AUX FDBK KILN 1 DUST BUCKET ELEVATOR |  | _BE1317_M01 | P_Motor | Sts_Running | 0
275 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 03 | 1756-IA16 | 2 | 1 | 03 | SC1318_AUX | I:024/3 | SC | SC 1318 AUX FDBK KILN 1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | SC1318_AUX_IO | MCR2_R02:1:I.Data.03 | SC1318_AUX_IO:= MCR2_R02:1:I.Data.03; //SC 1318 AUX FDBK KILN 1 DUST SCREW CONVEYOR |  | _SC1318_M01 | P_Motor | Sts_Running | 0
276 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 04 | 1756-IA16 | 2 | 1 | 04 | RA1319_AUX | I:024/4 | RA | RA 1319 FDBK KILN 1 PRIMARY DC ROTARY AIRLOCK | [10 empty] | MCR2_R02 | I.Data | INPUT | RA1319_AUX_IO | MCR2_R02:1:I.Data.04 | RA1319_AUX_IO:= MCR2_R02:1:I.Data.04; //RA 1319 FDBK KILN 1 PRIMARY DC ROTARY AIRLOCK |  | _RA1319_M01 | P_Motor | Sts_Running | 0
277 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 05 | 1756-IA16 | 2 | 1 | 05 | FN1321_AUX | I:024/5 | FN | FN 1321 FDBK KILN 1 DUST COLLECTOR FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | FN1321_AUX_IO | MCR2_R02:1:I.Data.05 | FN1321_AUX_IO:= MCR2_R02:1:I.Data.05; //FN 1321 FDBK KILN 1 DUST COLLECTOR FAN |  | _FN1321_M01 | P_Motor | Sts_Running | 0
278 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 06 | 1756-IA16 | 2 | 1 | 06 | BE1317_DI | I:024/6 | BE | BE 1-317 Jog Plug Inserted Kiln 1 Bucket Elevator | [10 empty] | MCR2_R02 | I.Data | INPUT | BE1317_DI_IO | MCR2_R02:1:I.Data.06 | BE1317_DI_IO:= MCR2_R02:1:I.Data.06; //BE 1-317 Jog Plug Inserted Kiln 1 Bucket Elevator |  | _BE1317_M01 | P_Motor | Sts_Ext | 0
279 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 07 | 1756-IA16 | 2 | 1 | 07 | BE1317_PB_JOG | I:024/7 | BE | BE 1-317 Jog Kiln 1 Bucket Elevator | [10 empty] | MCR2_R02 | I.Data | INPUT | BE1317_PB_JOG_IO | MCR2_R02:1:I.Data.07 | BE1317_PB_JOG_IO:= MCR2_R02:1:I.Data.07; //BE 1-317 Jog Kiln 1 Bucket Elevator |  | _BE1317_M01 | P_Motor | Sts_Jogging | 0
280 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 10 | 1756-IA16 | 2 | 1 | 08 | SC316A_MS | I:024/10 | SC | SC-316A MOTION SWITCH | [10 empty] | MCR2_R02 | I.Data | INPUT | SC316A_MS_IO | MCR2_R02:1:I.Data.08 | SC316A_MS_IO:= MCR2_R02:1:I.Data.08; //SC-316A MOTION SWITCH |  | _SC316A_MS | P_DIn | Sts_PV | bar: V.MIN to HH
281 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 11 | 1756-IA16 | 2 | 1 | 09 | PU326_LSL | I:024/11 | TK | K1 COOLING TANK FOR PU 326 LOW LEVEL SW | [10 empty] | MCR2_R02 | I.Data | INPUT | PU326_LSL_IO | MCR2_R02:1:I.Data.09 | PU326_LSL_IO:= MCR2_R02:1:I.Data.09; //K1 COOLING TANK FOR PU 326 LOW LEVEL SW |  | _PU326_LSL | P_DIn | Sts_PV
282 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 12 | 1756-IA16 | 2 | 1 | 10 |  | I:024/12 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:1:I.Data.10 | // MCR2_R02:1:I.Data.10 SPARE
283 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 13 | 1756-IA16 | 2 | 1 | 11 |  | I:024/13 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:1:I.Data.11 | // MCR2_R02:1:I.Data.11 SPARE
284 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 14 | 1756-IA16 | 2 | 1 | 12 |  | I:024/14 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:1:I.Data.12 | // MCR2_R02:1:I.Data.12 SPARE
285 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 15 | 1756-IA16 | 2 | 1 | 13 | BC8225_AUX | I:024/15 | BC | BC 8225 AUX FDBK STONE FEED CHAT BELT CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BC8225_AUX_IO | MCR2_R02:1:I.Data.13 | BC8225_AUX_IO:= MCR2_R02:1:I.Data.13; //BC 8225 AUX FDBK STONE FEED CHAT BELT CONVEYOR |  | _BC8225_M01 | P_Motor | Sts_Running | 1 | Stone_Feed_TaskC | Task_C | _BC8225_M01 | Stone Feed
286 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 16 | 1756-IA16 | 2 | 1 | 14 | MCR3_ALM | I:024/16 | MCR3 | ALARM FIRE IN MCR #3 | [10 empty] | MCR2_R02 | I.Data | INPUT | MCR3_ALM_IO | MCR2_R02:1:I.Data.14 | MCR3_ALM_IO:= MCR2_R02:1:I.Data.14; //ALARM FIRE IN MCR #3 |  | _MCR3_ALM | P_DIn | Sts_PV
287 | MCR2 R2G4M0 | 1771-IAD | 2 | 8 | 17 | 1756-IA16 | 2 | 1 | 15 | BE1317_MS | I:024/17 | BE | BE 1317 FDBK KILN 1 BUCKET ELEVATOR MOTION SWITCH | [10 empty] | MCR2_R02 | I.Data | INPUT | BE1317_MS_IO | MCR2_R02:1:I.Data.15 | BE1317_MS_IO:= MCR2_R02:1:I.Data.15; //BE 1317 FDBK KILN 1 BUCKET ELEVATOR MOTION SWITCH |  | _BE1317_MS | P_DIn | Sts_PV | 0
288 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-0 | 1756-OA16I | 2 | REMOVE | 0 |  | O:024/0 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.0 | // MCR2_R02:REMOVE:O.Data.0 SPARE
289 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-1 | 1756-OA16I | 2 | REMOVE | 1 |  | O:024/1 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.1 | // MCR2_R02:REMOVE:O.Data.1 SPARE
290 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-2 | 1756-OA16I | 2 | REMOVE | 2 |  | O:024/2 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.2 | // MCR2_R02:REMOVE:O.Data.2 SPARE
291 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-3 | 1756-OA16I | 2 | REMOVE | 3 |  | O:024/3 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.3 | // MCR2_R02:REMOVE:O.Data.3 SPARE
292 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-4 | 1756-OA16I | 2 | REMOVE | 4 |  | O:024/4 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.4 | // MCR2_R02:REMOVE:O.Data.4 SPARE
293 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-5 | 1756-OA16I | 2 | REMOVE | 5 |  | O:024/5 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.5 | // MCR2_R02:REMOVE:O.Data.5 SPARE
294 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-6 | 1756-OA16I | 2 | REMOVE | 6 |  | O:024/6 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.6 | // MCR2_R02:REMOVE:O.Data.6 SPARE
295 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-7 | 1756-OA16I | 2 | REMOVE | 7 |  | O:024/7 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.7 | // MCR2_R02:REMOVE:O.Data.7 SPARE
296 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-10 | 1756-OA16I | 2 | REMOVE | 8 |  | O:024/10 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.8 | // MCR2_R02:REMOVE:O.Data.8 SPARE
297 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-11 | 1756-OA16I | 2 | REMOVE | 9 |  | O:024/11 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.9 | // MCR2_R02:REMOVE:O.Data.9 SPARE
298 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-12 | 1756-OA16I | 2 | REMOVE | 10 |  | O:024/12 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.10 | // MCR2_R02:REMOVE:O.Data.10 SPARE
299 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-13 | 1756-OA16I | 2 | REMOVE | 11 |  | O:024/13 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.11 | // MCR2_R02:REMOVE:O.Data.11 SPARE
300 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-14 | 1756-OA16I | 2 | REMOVE | 12 |  | O:024/14 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.12 | // MCR2_R02:REMOVE:O.Data.12 SPARE
301 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-15 | 1756-OA16I | 2 | REMOVE | 13 |  | O:024/15 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.13 | // MCR2_R02:REMOVE:O.Data.13 SPARE
302 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-16 | 1756-OA16I | 2 | REMOVE | 14 |  | O:024/16 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.14 | // MCR2_R02:REMOVE:O.Data.14 SPARE
303 | MCR2 R2G4M1 | 1771-ODD | 2 | 9 | L1-17 | 1756-OA16I | 2 | REMOVE | 15 |  | O:024/17 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:REMOVE:O.Data.15 | // MCR2_R02:REMOVE:O.Data.15 SPARE
304 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 00 | 1756-IA16 | 2 | 2 | 00 | PNY_SLOCK_DI | I:025/0 | PNY | PONY MOTOR CHAIN BOX SAFETY INTERLOCK | [10 empty] | MCR2_R02 | I.Data | INPUT | PNY_SLOCK_DI_IO | MCR2_R02:2:I.Data.00 | PNY_SLOCK_DI_IO:= MCR2_R02:2:I.Data.00; //PONY MOTOR CHAIN BOX SAFETY INTERLOCK |  | _PNY_SLOCK_DI | P_DIn | Sts_PV
305 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 01 | 1756-IA16 | 2 | 2 | 01 |  | I:025/1 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.01 | // MCR2_R02:2:I.Data.01 SPARE
306 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 02 | 1756-IA16 | 2 | 2 | 02 | KN1_CAN_PAL | I:025/2 | PS | KILN 1 AIR CANNONS LOW PRESSURE | [10 empty] | MCR2_R02 | I.Data | INPUT | KN1_CAN_PAL_IO | MCR2_R02:2:I.Data.02 | KN1_CAN_PAL_IO:= MCR2_R02:2:I.Data.02; //KILN 1 AIR CANNONS LOW PRESSURE |  | _KN1_CAN_PAL | P_DIn | Sts_PV
307 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 03 | 1756-IA16 | 2 | 2 | 03 | PM13052_AUX | I:025/3 | PM | PM 1305-2 AUX FDBK KILN 1 PH HYDRUALIC PUMP | [10 empty] | MCR2_R02 | I.Data | INPUT | PM13052_AUX_IO | MCR2_R02:2:I.Data.03 | PM13052_AUX_IO:= MCR2_R02:2:I.Data.03; //PM 1305-2 AUX FDBK KILN 1 PH HYDRUALIC PUMP |  | _PM13052_M01 | P_Motor | Sts_Running | 1 | Kiln1_Preheater_TaskC | Task_C | _PM13052_M01 | Kiln 1 Preheater
308 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 04 | 1756-IA16 | 2 | 2 | 04 | PM13051_AUX | I:025/4 | PM | PM 1305-1 AUX FDBK KILN 1 PH HYDRUALIC PUMP | [10 empty] | MCR2_R02 | I.Data | INPUT | PM13051_AUX_IO | MCR2_R02:2:I.Data.04 | PM13051_AUX_IO:= MCR2_R02:2:I.Data.04; //PM 1305-1 AUX FDBK KILN 1 PH HYDRUALIC PUMP |  | _PM13051_M01 | P_Motor | Sts_Running | 1 | Kiln1_Preheater_TaskC | Task_C | _PM13051_M01 | Kiln 1 Preheater
309 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 05 | 1756-IA16 | 2 | 2 | 05 | FN1326_AUX | I:025/5 | FN | FN 1326 AUX FDBK KILN 1 H20 COOLING FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | FN1326_AUX_IO | MCR2_R02:2:I.Data.05 | FN1326_AUX_IO:= MCR2_R02:2:I.Data.05; //FN 1326 AUX FDBK KILN 1 H20 COOLING FAN |  | _FN1326_M01 | P_Motor | Sts_Running | 1 | Kiln1_Main_TaskC | Task_C | _FN1326_M01 | Kiln 1
310 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 06 | 1756-IA16 | 2 | 2 | 06 | WP13261_AUX | I:025/6 | WP | WP 1326-1 AUX FDBK KILN 1 WATER PUMP #1 | [10 empty] | MCR2_R02 | I.Data | INPUT | WP13261_AUX_IO | MCR2_R02:2:I.Data.06 | WP13261_AUX_IO:= MCR2_R02:2:I.Data.06; //WP 1326-1 AUX FDBK KILN 1 WATER PUMP #1 |  | _WP13261_M01 | P_Motor | Sts_Running | 1 | Kiln1_Main_TaskC | Task_C | _WP13261_M01 | Kiln 1
311 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 07 | 1756-IA16 | 2 | 2 | 07 | WP13262_AUX | I:025/7 | WP | WP 1326-2 AUX FDBK KILN 1 WATER PUMP #2 | [10 empty] | MCR2_R02 | I.Data | INPUT | WP13262_AUX_IO | MCR2_R02:2:I.Data.07 | WP13262_AUX_IO:= MCR2_R02:2:I.Data.07; //WP 1326-2 AUX FDBK KILN 1 WATER PUMP #2 |  | _WP13262_M01 | P_Motor | Sts_Running | 1 | Kiln1_Main_TaskC | Task_C | _WP13262_M01 | Kiln 1
312 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 10 | 1756-IA16 | 2 | 2 | 08 |  | I:025/10 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.08 | // MCR2_R02:2:I.Data.08 SPARE
313 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 11 | 1756-IA16 | 2 | 2 | 09 |  | I:025/11 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.09 | // MCR2_R02:2:I.Data.09 SPARE
314 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 12 | 1756-IA16 | 2 | 2 | 10 | FN1307A_SSA | I:025/12 |  | FN 1-307-A AUTO KILN 1 TRANSFER CHUTE COOLING FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | FN1307A_SSA_IO | MCR2_R02:2:I.Data.10 | FN1307A_SSA_IO:= MCR2_R02:2:I.Data.10; //FN 1-307-A AUTO KILN 1 TRANSFER CHUTE COOLING FAN |  | _FN1307A_SSA | P_DIn | Sts_PV | 1 | Kiln1_Main_TaskB | Task_B | _FN1307A_SSA | Kin 1
315 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 13 | 1756-IA16 | 2 | 2 | 11 |  | I:025/13 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.11 | // MCR2_R02:2:I.Data.11 SPARE
316 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 14 | 1756-IA16 | 2 | 2 | 12 | FN1307_AUX | I:025/14 | FN | FN 1-307-A AUX FDBK KILN 1 TRANSFER CHUTE COOLING FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | FN1307_AUX_IO | MCR2_R02:2:I.Data.12 | FN1307_AUX_IO:= MCR2_R02:2:I.Data.12; //FN 1-307-A AUX FDBK KILN 1 TRANSFER CHUTE COOLING FAN |  | _FN1307A_M01 | P_Motor | Sts_Running | 1 | Kiln1_Main_TaskC | Task_C | _FN1307A_M01 | Kiln 1
317 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 15 | 1756-IA16 | 2 | 2 | 13 |  | I:025/15 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.13 | // MCR2_R02:2:I.Data.13 SPARE
318 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 16 | 1756-IA16 | 2 | 2 | 14 |  | I:025/16 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.14 | // MCR2_R02:2:I.Data.14 SPARE
319 | MCR2 R2G5M0 | 1771-IAD | 2 | 10 | 17 | 1756-IA16 | 2 | 2 | 15 |  | I:025/17 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:2:I.Data.15 | // MCR2_R02:2:I.Data.15 SPARE
320 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-0 | 1756-OA16I | 2 | 4 | 0 | FN1307A_COIL | O:025/0 | FN | FN 1307-A RUN KILN 1 TRANSFER CHUTE COOLING FAN | [10 empty] | MCR2_R02 | O.Data | OUTPUT | FN1307A_COIL_IO | MCR2_R02:4:O.Data.0 | MCR2_R02:4:O.Data.0:=FN1307A_COIL_IO; //FN 1307-A RUN KILN 1 TRANSFER CHUTE COOLING FAN |  | _FN1307A_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Main_TaskC | Task_C | _FN1307A_M01 | Kiln 1
321 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-1 | 1756-OA16I | 2 | 4 | 1 |  | O:025/1 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:4:O.Data.1 | // MCR2_R02:4:O.Data.1 SPARE
322 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-2 | 1756-OA16I | 2 | 4 | 2 |  | O:025/2 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:4:O.Data.2 | // MCR2_R02:4:O.Data.2 SPARE
323 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-3 | 1756-OA16I | 2 | 4 | 3 | PM13052_COIL | O:025/3 | PM | PM 1305-2 RUN KILN 1 PH HYDRAULIC PUMP #2 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | PM13052_COIL_IO | MCR2_R02:4:O.Data.3 | MCR2_R02:4:O.Data.3:=PM13052_COIL_IO; //PM 1305-2 RUN KILN 1 PH HYDRAULIC PUMP #2 |  | _PM13052_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Preheater_TaskC | Task_C | _PM13052_M01 | Kiln 1 Preheater
324 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-4 | 1756-OA16I | 2 | 4 | 4 | PM13051_COIL | O:025/4 | PM | PM 1305-1 RUN KILN 1 PH HYDRAULIC PUMP #1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | PM13051_COIL_IO | MCR2_R02:4:O.Data.4 | MCR2_R02:4:O.Data.4:=PM13051_COIL_IO; //PM 1305-1 RUN KILN 1 PH HYDRAULIC PUMP #1 |  | _PM13051_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Preheater_TaskC | Task_C | _PM13051_M01 | Kiln 1 Preheater
325 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-5 | 1756-OA16I | 2 | 4 | 5 | FN1326_COIL | O:025/5 | FN | FN 1326 RUN KILN 1 H20 COOLING FAN | [10 empty] | MCR2_R02 | O.Data | OUTPUT | FN1326_COIL_IO | MCR2_R02:4:O.Data.5 | MCR2_R02:4:O.Data.5:=FN1326_COIL_IO; //FN 1326 RUN KILN 1 H20 COOLING FAN |  | _FN1326_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Main_TaskC | Task_C | _FN1326_M01 | Kiln 1
326 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-6 | 1756-OA16I | 2 | 4 | 6 | WP13261_COIL | O:025/6 | WP | WP 1326-1 RUN KILN 1 WATER PUMP #1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | WP13261_COIL_IO | MCR2_R02:4:O.Data.6 | MCR2_R02:4:O.Data.6:=WP13261_COIL_IO; //WP 1326-1 RUN KILN 1 WATER PUMP #1 |  | _WP13261_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Main_TaskC | Task_C | _WP13261_M01 | Kiln 1
327 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-7 | 1756-OA16I | 2 | 4 | 7 | WP13262_COIL | O:025/7 | WP | WP 1326-2 RUN KILN 1 WATER PUMP #2 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | WP13262_COIL_IO | MCR2_R02:4:O.Data.7 | MCR2_R02:4:O.Data.7:=WP13262_COIL_IO; //WP 1326-2 RUN KILN 1 WATER PUMP #2 |  | _WP13262_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Main_TaskC | Task_C | _WP13262_M01 | Kiln 1
328 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-10 | 1756-OA16I | 2 | 4 | 8 |  | O:025/10 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:4:O.Data.8 | // MCR2_R02:4:O.Data.8 SPARE
329 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-11 | 1756-OA16I | 2 | 4 | 9 |  | O:025/11 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:4:O.Data.9 | // MCR2_R02:4:O.Data.9 SPARE
330 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-12 | 1756-OA16I | 2 | 4 | 10 | SC1316_COIL | O:025/12 | SC | SC 1316 RUN KILN 1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | SC1316_COIL_IO | MCR2_R02:4:O.Data.10 | MCR2_R02:4:O.Data.10:=SC1316_COIL_IO; //SC 1316 RUN KILN 1 DUST SCREW CONVEYOR |  | _SC1316_M01 | P_Motor | PCmd_Start
331 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-13 | 1756-OA16I | 2 | 4 | 11 | SC1316A_COIL | O:025/13 | SC | SC 1316-A RUN KILN 1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | SC1316A_COIL_IO | MCR2_R02:4:O.Data.11 | MCR2_R02:4:O.Data.11:=SC1316A_COIL_IO; //SC 1316-A RUN KILN 1 DUST SCREW CONVEYOR |  | _SC1316A_M01 | P_Motor | PCmd_Start | 0
332 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-14 | 1756-OA16I | 2 | 4 | 12 | BE1317_COIL | O:025/14 | BE | BE 1317 RUN KILN 1 DUST BUCKET ELEVATOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BE1317_COIL_IO | MCR2_R02:4:O.Data.12 | MCR2_R02:4:O.Data.12:=BE1317_COIL_IO; //BE 1317 RUN KILN 1 DUST BUCKET ELEVATOR |  | _BE1317_M01 | P_Motor | PCmd_Start | 0
333 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-15 | 1756-OA16I | 2 | 4 | 13 | SC1318_COIL | O:025/15 | SC | SC 1318 RUN KILN 1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | SC1318_COIL_IO | MCR2_R02:4:O.Data.13 | MCR2_R02:4:O.Data.13:=SC1318_COIL_IO; //SC 1318 RUN KILN 1 DUST SCREW CONVEYOR |  | _SC1318_M01 | P_Motor | PCmd_Start
334 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-16 | 1756-OA16I | 2 | 4 | 14 | FN1321_COIL | O:025/16 | FN | FN 1321 RUN KILN 1 DUST FAN | [10 empty] | MCR2_R02 | O.Data | OUTPUT | FN1321_COIL_IO | MCR2_R02:4:O.Data.14 | MCR2_R02:4:O.Data.14:=FN1321_COIL_IO; //FN 1321 RUN KILN 1 DUST FAN |  | _FN1321_M01 | P_Motor | PCmd_Start | 0
335 | MCR2 R2G5M1 | 1771-ODD | 2 | 11 | L1-17 | 1756-OA16I | 2 | 4 | 15 | BC8225_COIL | O:025/17 | BC | BC 8225 RUN STONE FEED CHAT BELT CONVEYOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BC8225_COIL_IO | MCR2_R02:4:O.Data.15 | MCR2_R02:4:O.Data.15:=BC8225_COIL_IO; //BC 8225 RUN STONE FEED CHAT BELT CONVEYOR |  | _BC8225_M01 | P_Motor | PCmd_Start | 1 | Stone_Feed_TaskC | Task_C | _BC8225_M01 | Stone Feed
336 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 00 | 1756-IA16 | 2 | REMOVE | 00 |  | I:026/0 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.00 | // MCR2_R02:REMOVE:I.Data.00 SPARE
337 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 01 | 1756-IA16 | 2 | REMOVE | 01 |  | I:026/1 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.01 | // MCR2_R02:REMOVE:I.Data.01 SPARE
338 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 02 | 1756-IA16 | 2 | 3 | 00 | WP3083_AUX | I:026/2 | WP | WP 308-3 Aux Contact General Plant O2 Probe Cooling Pump | [10 empty] | MCR2_R02 | I.Data | INPUT | WP3083_AUX_IO | MCR2_R02:3:I.Data.00 | WP3083_AUX_IO:= MCR2_R02:3:I.Data.00; //WP 308-3 Aux Contact General Plant O2 Probe Cooling Pump |  | _WP3083_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _WP3083_M01 | Kiln 2
339 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 03 | 1756-IA16 | 2 | REMOVE | 03 |  | I:026/3 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.03 | // MCR2_R02:REMOVE:I.Data.03 SPARE
340 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 04 | 1756-IA16 | 2 | REMOVE | 04 |  | I:026/4 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.04 | // MCR2_R02:REMOVE:I.Data.04 SPARE
341 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 05 | 1756-IA16 | 2 | REMOVE | 05 |  | I:026/5 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.05 | // MCR2_R02:REMOVE:I.Data.05 SPARE
342 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 06 | 1756-IA16 | 2 | REMOVE | 06 |  | I:026/6 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.06 | // MCR2_R02:REMOVE:I.Data.06 SPARE
343 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 07 | 1756-IA16 | 2 | REMOVE | 07 |  | I:026/7 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.07 | // MCR2_R02:REMOVE:I.Data.07 SPARE
344 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 10 | 1756-IA16 | 2 | REMOVE | 08 |  | I:026/10 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.08 | // MCR2_R02:REMOVE:I.Data.08 SPARE
345 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 11 | 1756-IA16 | 2 | REMOVE | 09 |  | I:026/11 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.09 | // MCR2_R02:REMOVE:I.Data.09 SPARE
346 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 12 | 1756-IA16 | 2 | REMOVE | 10 |  | I:026/12 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.10 | // MCR2_R02:REMOVE:I.Data.10 SPARE
347 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 13 | 1756-IA16 | 2 | REMOVE | 11 |  | I:026/13 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.11 | // MCR2_R02:REMOVE:I.Data.11 SPARE
348 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 14 | 1756-IA16 | 2 | REMOVE | 12 |  | I:026/14 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.12 | // MCR2_R02:REMOVE:I.Data.12 SPARE
349 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 15 | 1756-IA16 | 2 | REMOVE | 13 |  | I:026/15 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.13 | // MCR2_R02:REMOVE:I.Data.13 SPARE
350 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 16 | 1756-IA16 | 2 | REMOVE | 14 |  | I:026/16 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.14 | // MCR2_R02:REMOVE:I.Data.14 SPARE
351 | MCR2 R2G6M0 | 1771-IAD | 2 | 12 | 17 | 1756-IA16 | 2 | REMOVE | 15 |  | I:026/17 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.15 | // MCR2_R02:REMOVE:I.Data.15 SPARE
352 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-0 | 1756-OA16I | 2 | 5 | 0 | KN1_CAN1_SV | O:026/0 | SV | AIR CANNONS CANNON 1 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN1_SV_IO | MCR2_R02:5:O.Data.0 | MCR2_R02:5:O.Data.0:=KN1_CAN1_SV_IO; //AIR CANNONS CANNON 1 KILN 1 |  | NA | NA | NA
353 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-1 | 1756-OA16I | 2 | 5 | 1 | KN1_CAN2_SV | O:026/1 | SV | AIR CANNONS CANNON 2 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN2_SV_IO | MCR2_R02:5:O.Data.1 | MCR2_R02:5:O.Data.1:=KN1_CAN2_SV_IO; //AIR CANNONS CANNON 2 KILN 1 |  | NA | NA | NA
354 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-2 | 1756-OA16I | 2 | 5 | 2 | KN1_CAN3_SV | O:026/2 | SV | AIR CANNONS CANNON 3 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN3_SV_IO | MCR2_R02:5:O.Data.2 | MCR2_R02:5:O.Data.2:=KN1_CAN3_SV_IO; //AIR CANNONS CANNON 3 KILN 1 |  | NA | NA | NA
355 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-3 | 1756-OA16I | 2 | 5 | 3 | KN1_CAN4_SV | O:026/3 | SV | AIR CANNONS CANNON 4 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN4_SV_IO | MCR2_R02:5:O.Data.3 | MCR2_R02:5:O.Data.3:=KN1_CAN4_SV_IO; //AIR CANNONS CANNON 4 KILN 1 |  | NA | NA | NA
356 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-4 | 1756-OA16I | 2 | 5 | 4 | KN1_CAN5_SV | O:026/4 | SV | AIR CANNONS CANNON 5 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN5_SV_IO | MCR2_R02:5:O.Data.4 | MCR2_R02:5:O.Data.4:=KN1_CAN5_SV_IO; //AIR CANNONS CANNON 5 KILN 1 |  | NA | NA | NA
357 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-5 | 1756-OA16I | 2 | 5 | 5 | KN1_CAN6_SV | O:026/5 | SV | AIR CANNONS CANNON 6 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN6_SV_IO | MCR2_R02:5:O.Data.5 | MCR2_R02:5:O.Data.5:=KN1_CAN6_SV_IO; //AIR CANNONS CANNON 6 KILN 1 |  | NA | NA | NA
358 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-6 | 1756-OA16I | 2 | 5 | 6 | KN1_CAN7_SV | O:026/6 | SV | AIR CANNONS CANNON 7 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN7_SV_IO | MCR2_R02:5:O.Data.6 | MCR2_R02:5:O.Data.6:=KN1_CAN7_SV_IO; //AIR CANNONS CANNON 7 KILN 1 |  | NA | NA | NA
359 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-7 | 1756-OA16I | 2 | 5 | 7 | KN1_CAN8_SV | O:026/7 | SV | AIR CANNONS CANNON 8 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN8_SV_IO | MCR2_R02:5:O.Data.7 | MCR2_R02:5:O.Data.7:=KN1_CAN8_SV_IO; //AIR CANNONS CANNON 8 KILN 1 |  | NA | NA | NA
360 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-10 | 1756-OA16I | 2 | 5 | 8 | KN1_CAN9_SV | O:026/10 | SV | AIR CANNONS CANNON 9 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN9_SV_IO | MCR2_R02:5:O.Data.8 | MCR2_R02:5:O.Data.8:=KN1_CAN9_SV_IO; //AIR CANNONS CANNON 9 KILN 1 |  | NA | NA | NA
361 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-11 | 1756-OA16I | 2 | 5 | 9 | KN1_CAN10_SV | O:026/11 | SV | AIR CANNONS CANNON 10 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN10_SV_IO | MCR2_R02:5:O.Data.9 | MCR2_R02:5:O.Data.9:=KN1_CAN10_SV_IO; //AIR CANNONS CANNON 10 KILN 1 |  | NA | NA | NA
362 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-12 | 1756-OA16I | 2 | 5 | 10 | KN1_CAN_TCS_SV | O:026/12 | SV | AIR CANNON SOUTH XFER CHUTE KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN_TCS_SV_IO | MCR2_R02:5:O.Data.10 | MCR2_R02:5:O.Data.10:=KN1_CAN_TCS_SV_IO; //AIR CANNON SOUTH XFER CHUTE KILN 1 |  | NA | NA | NA
363 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-13 | 1756-OA16I | 2 | 5 | 11 | KN1_CAN_TCM_SV | O:026/13 | SV | AIR CANNON MIDDLE XFER CHUTE KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN_TCM_SV_IO | MCR2_R02:5:O.Data.11 | MCR2_R02:5:O.Data.11:=KN1_CAN_TCM_SV_IO; //AIR CANNON MIDDLE XFER CHUTE KILN 1 |  | NA | NA | NA
364 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-14 | 1756-OA16I | 2 | 5 | 12 | KN1_CAN_TCN_SV | O:026/14 | SV | AIR CANNON NORTH XFER CHUTE KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN_TCN_SV_IO | MCR2_R02:5:O.Data.12 | MCR2_R02:5:O.Data.12:=KN1_CAN_TCN_SV_IO; // AIR CANNON NORTH XFER CHUTE KILN 1 |  | NA | NA | NA
365 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-15 | 1756-OA16I | 2 | 5 | 13 | KN1_CAN15_SV | O:026/15 | SV | AIR CANNON 15 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN15_SV_IO | MCR2_R02:5:O.Data.13 | MCR2_R02:5:O.Data.13:=KN1_CAN15_SV_IO; //AIR CANNON 15 KILN 1 |  | NA | NA | NA
366 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-16 | 1756-OA16I | 2 | 5 | 14 | KN1_CAN14_SV | O:026/16 | SV | AIR CANNON 14 KILN 1 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | KN1_CAN14_SV_IO | MCR2_R02:5:O.Data.14 | MCR2_R02:5:O.Data.14:=KN1_CAN14_SV_IO; //AIR CANNON 14 KILN 1 |  | NA | NA | NA
367 | MCR2 R2G6M1 | 1771-ODD | 2 | 13 | L1-17 | 1756-OA16I | 2 | 5 | 15 |  | O:026/17 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:5:O.Data.15 | // MCR2_R02:5:O.Data.15 SPARE
368 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 00 | 1756-IA16 | 2 | REMOVE | 00 |  | I:027/0 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:REMOVE:I.Data.00 | // MCR2_R02:REMOVE:I.Data.00 SPARE
369 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 01 | 1756-IA16 | 2 | 3 | 01 | FN8213_SSA | I:027/1 |  | FN 8213 AUTO STONE FEED DC FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | FN8213_SSA_IO | MCR2_R02:3:I.Data.01 | FN8213_SSA_IO:= MCR2_R02:3:I.Data.01; //FN 8213 AUTO STONE FEED DC FAN |  | _FN8213_SSA | P_DIn | Sts_PV | 1 | Stone_Feed_TaskB | Task_B | _FN8213_SSA | Stone Feed
370 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 02 | 1756-IA16 | 2 | 3 | 02 | FN8213_AUX | I:027/2 | FN | FN 8213 AUX FDBK STONE FEED DC FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | FN8213_AUX_IO | MCR2_R02:3:I.Data.02 | FN8213_AUX_IO:= MCR2_R02:3:I.Data.02; //FN 8213 AUX FDBK STONE FEED DC FAN |  | _FN8213_M01 | P_Motor | Sts_Running | 1 | Stone_Feed_TaskC | Task_C | _FN8213_M01 | Stone Feed
371 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 03 | 1756-IA16 | 2 | 3 | 03 | BC8302_AUX | I:027/3 | BC | BC 8302 AUX FDBK STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BC8302_AUX_IO | MCR2_R02:3:I.Data.03 | BC8302_AUX_IO:= MCR2_R02:3:I.Data.03; //BC 8302 AUX FDBK STONE FEED BELT CONVEYOR |  | _BC8302_M01 | P_Motor | Sts_Running | 1 | Stone_Feed_TaskC | Task_C | _BC8302_M01 | Stone Feed
372 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 04 | 1756-IA16 | 2 | 3 | 04 | BC8302_MS | I:027/4 | BC | BC 8302 MOTION SWITCH STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BC8302_MS_IO | MCR2_R02:3:I.Data.04 | BC8302_MS_IO:= MCR2_R02:3:I.Data.04; //BC 8302 MOTION SWITCH STONE FEED BELT CONVEYOR |  | _BC8302_MS | P_DIn | Sts_PV | 1 | Stone_Feed_TaskB | Task_B | _BC8302_MS | Stone Feed
373 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 05 | 1756-IA16 | 2 | 3 | 05 | VS8328_AUX | I:027/5 | VS | VS 8328 AUX FDBK STONE FEED VIBRATING SCREEN | [10 empty] | MCR2_R02 | I.Data | INPUT | VS8328_AUX_IO | MCR2_R02:3:I.Data.05 | VS8328_AUX_IO:= MCR2_R02:3:I.Data.05; //VS 8328 AUX FDBK STONE FEED VIBRATING SCREEN |  | _VS8328_M01 | P_Motor | Sts_Running | 1 | Stone_Feed_TaskC | Task_C | _VS8328_M01 | Stone Feed
374 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 06 | 1756-IA16 | 2 | 3 | 06 | BC8329_AUX | I:027/6 | BC | BC 8329 AUX FDBK STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BC8329_AUX_IO | MCR2_R02:3:I.Data.06 | BC8329_AUX_IO:= MCR2_R02:3:I.Data.06; //BC 8329 AUX FDBK STONE FEED BELT CONVEYOR |  | _BC8329_M01 | P_Motor | Sts_Running | 1 | Stone_Feed_TaskC | Task_C | _BC8329_M01 | Stone Feed
375 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 07 | 1756-IA16 | 2 | 3 | 07 | BC8329_MS | I:027/7 | BC | BC 8329 MOTION SWITCH STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BC8329_MS_IO | MCR2_R02:3:I.Data.07 | BC8329_MS_IO:= MCR2_R02:3:I.Data.07; //BC 8329 MOTION SWITCH STONE FEED BELT CONVEYOR |  | _BC8329_MS | P_DIn | Sts_PV | 1 | Stone_Feed_TaskB | Task_B | _BC8329_MS | Stone Feed
376 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 10 | 1756-IA16 | 2 | 3 | 08 |  | I:027/10 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:3:I.Data.08 | // MCR2_R02:3:I.Data.08 SPARE
377 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 11 | 1756-IA16 | 2 | 3 | 09 |  | I:027/11 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:3:I.Data.09 | // MCR2_R02:3:I.Data.09 SPARE
378 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 12 | 1756-IA16 | 2 | 3 | 10 | KL1FN_AUX | I:027/12 | FN | FDBK KILN 1 O2 COOLING H2O FAN | [10 empty] | MCR2_R02 | I.Data | INPUT | KL1FN_AUX_IO | MCR2_R02:3:I.Data.10 | KL1FN_AUX_IO:= MCR2_R02:3:I.Data.10; //FDBK KILN 1 O2 COOLING H2O FAN |  | _KL1FN_M01 | P_DIn | Sts_PV | bar: Notes to EU
379 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 13 | 1756-IA16 | 2 | 3 | 11 |  | I:027/13 |  | SPARE | [10 empty] | MCR2_R02 | I.Data | INPUT |  | MCR2_R02:3:I.Data.11 | // MCR2_R02:3:I.Data.11 SPARE | bar: Notes to EU
380 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 14 | 1756-IA16 | 2 | 3 | 12 | MCR2_ALM | I:027/14 | MCR2 | ALARM FIRE IN MCR #2 | [10 empty] | MCR2_R02 | I.Data | INPUT | MCR2_ALM_IO | MCR2_R02:3:I.Data.12 | MCR2_ALM_IO:= MCR2_R02:3:I.Data.12; //ALARM FIRE IN MCR #2 |  | _MCR2_ALM | P_DIn | Sts_PV
381 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 15 | 1756-IA16 | 2 | 3 | 13 | BC8302_PCD | I:027/15 | BC | BC 8302 PLUGGED CHUTE ALARM STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | BC8302_PCD_IO | MCR2_R02:3:I.Data.13 | BC8302_PCD_IO:= MCR2_R02:3:I.Data.13; //BC 8302 PLUGGED CHUTE ALARM STONE FEED BELT CONVEYOR |  | _BC8302_PCD | P_DIn | Sts_PV | 1 | Stone_Feed_TaskB | Task_B | _BC8302_PCD | Stone Feed
382 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 16 | 1756-IA16 | 2 | 3 | 14 | SC1316_MS | I:027/16 | SC | SC1316 ZERO SPEED KILN1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | SC1316_MS_IO | MCR2_R02:3:I.Data.14 | SC1316_MS_IO:= MCR2_R02:3:I.Data.14; //SC1316 ZERO SPEED KILN1 DUST SCREW CONVEYOR |  | _SC1316_MS | P_DIn | Sts_PV
383 | MCR2 R2G7M0 | 1771-IAD | 2 | 14 | 17 | 1756-IA16 | 2 | 3 | 15 | SC1318_MS | I:027/17 | SC | SC1318 ZERO SPEED KILN1 DUST SCREW CONVEYOR | [10 empty] | MCR2_R02 | I.Data | INPUT | SC1318_MS_IO | MCR2_R02:3:I.Data.15 | SC1318_MS_IO:= MCR2_R02:3:I.Data.15; //SC1318 ZERO SPEED KILN1 DUST SCREW CONVEYOR |  | _SC1318_MS | P_DIn | Sts_PV
384 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-0 | 1756-OA16I | 2 | 6 | 0 |  | O:027/0 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.0 | // MCR2_R02:6:O.Data.0 SPARE
385 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-1 | 1756-OA16I | 2 | 6 | 1 |  | O:027/1 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.1 | // MCR2_R02:6:O.Data.1 SPARE
386 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-2 | 1756-OA16I | 2 | 6 | 2 | FN8213_COIL | O:027/2 | FN | FN 8213 RUN STONE FEED DC FAN | [10 empty] | MCR2_R02 | O.Data | OUTPUT | FN8213_COIL_IO | MCR2_R02:6:O.Data.2 | MCR2_R02:6:O.Data.2:=FN8213_COIL_IO; //FN 8213 RUN STONE FEED DC FAN |  | _FN8213_M01 | P_Motor | PCmd_Start | 1 | Stone_Feed_TaskC | Task_C | _FN8213_M01 | Stone Feed
387 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-3 | 1756-OA16I | 2 | 6 | 3 | BC8302_COIL | O:027/3 | BC | BC 8302 RUN STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BC8302_COIL_IO | MCR2_R02:6:O.Data.3 | MCR2_R02:6:O.Data.3:=BC8302_COIL_IO; //BC 8302 RUN STONE FEED BELT CONVEYOR |  | _BC8302_M01 | P_Motor | PCmd_Start | 1 | Stone_Feed_TaskC | Task_C | _BC8302_M01 | Stone Feed
388 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-4 | 1756-OA16I | 2 | 6 | 4 | VS8328_COIL | O:027/4 | VS | VS 8328 RUN STONE FEED VIBRATING SCREEN | [10 empty] | MCR2_R02 | O.Data | OUTPUT | VS8328_COIL_IO | MCR2_R02:6:O.Data.4 | MCR2_R02:6:O.Data.4:=VS8328_COIL_IO; //VS 8328 RUN STONE FEED VIBRATING SCREEN |  | _VS8328_M01 | P_Motor | PCmd_Start | 1 | Stone_Feed_TaskC | Task_C | _VS8328_M01 | Stone Feed
389 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-5 | 1756-OA16I | 2 | 6 | 5 | BC8329_COIL | O:027/5 | BC | BC 8329 RUN STONE FEED BELT CONVEYOR | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BC8329_COIL_IO | MCR2_R02:6:O.Data.5 | MCR2_R02:6:O.Data.5:=BC8329_COIL_IO; //BC 8329 RUN STONE FEED BELT CONVEYOR |  | _BC8329_M01 | P_Motor | PCmd_Start | 1 | Stone_Feed_TaskC | Task_C | _BC8329_M01 | Stone Feed
390 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-6 | 1756-OA16I | 2 | 6 | 6 |  | O:027/6 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.6 | // MCR2_R02:6:O.Data.6 SPARE
391 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-7 | 1756-OA16I | 2 | 6 | 7 |  | O:027/7 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.7 | // MCR2_R02:6:O.Data.7 SPARE
392 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-10 | 1756-OA16I | 2 | 6 | 8 | BC302TUN_YAY | O:027/10 | SIREN | WARNING HORN STONE FEED BC 302 TUNNEL | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BC302TUN_YAY_IO | MCR2_R02:6:O.Data.8 | MCR2_R02:6:O.Data.8:=BC302TUN_YAY_IO; //WARNING HORN STONE FEED BC 302 TUNNEL |  | _BC302TUN_YAY | P_Dout | PCmd_On | 1 | Stone_Feed_TaskB | Task_B | _BC302TUN_YAY | Stone Feed
393 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-11 | 1756-OA16I | 2 | 6 | 9 |  | O:027/11 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.9 | // MCR2_R02:6:O.Data.9 SPARE | [8 empty] | `
394 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-12 | 1756-OA16I | 2 | 6 | 10 | BC302HP_YAY | O:027/12 | SIREN | WARNING HORN STONE FEED BC 302 HEAD PULLEY | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BC302HP_YAY_IO | MCR2_R02:6:O.Data.10 | MCR2_R02:6:O.Data.10:=BC302HP_YAY_IO; //WARNING HORN STONE FEED BC 302 HEAD PULLEY |  | _BC302HP_YAY | P_Dout | PCmd_On | 1 | Stone_Feed_TaskB | Task_B | _BC302HP_YAY | Stone Feed
395 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-13 | 1756-OA16I | 2 | 6 | 11 | BC329_YAY | O:027/13 | SIREN | WARNING HORN STONE FEED BC 329 | [10 empty] | MCR2_R02 | O.Data | OUTPUT | BC329_YAY_IO | MCR2_R02:6:O.Data.11 | MCR2_R02:6:O.Data.11:=BC329_YAY_IO; //WARNING HORN STONE FEED BC 329 |  | _BC329_YAY | P_Dout | PCmd_On | 1 | Stone_Feed_TaskB | Task_B | _BC329_YAY | Stone Feed
396 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-14 | 1756-OA16I | 2 | 6 | 12 |  | O:027/14 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.12 | // MCR2_R02:6:O.Data.12 SPARE
397 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-15 | 1756-OA16I | 2 | 6 | 13 |  | O:027/15 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.13 | // MCR2_R02:6:O.Data.13 SPARE
398 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-16 | 1756-OA16I | 2 | 6 | 14 |  | O:027/16 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.14 | // MCR2_R02:6:O.Data.14 SPARE
399 | MCR2 R2G7M1 | 1771-ODD | 2 | 15 | L1-17 | 1756-OA16I | 2 | 6 | 15 |  | O:027/17 |  | SPARE | [10 empty] | MCR2_R02 | O.Data | OUTPUT |  | MCR2_R02:6:O.Data.15 | // MCR2_R02:6:O.Data.15 SPARE
400 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH1 | 1756-IF16 | 3 | 8 | 0 | FV1312_ZT | N37:0 | FV | FV 1312 DAMPER POSITION KILN 1 COOLER |  | EU: % Position; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | FV1312_ZT_IO | SampleRoom_R03:8:I.Ch0Data | FV1312_ZT_IO:= SampleRoom_R03:8:I.Ch0Data; //FV 1312 DAMPER POSITION KILN 1 COOLER |  | _FV1312_ZT | P_AIn | Val
401 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH2 | 1756-IF16 | 3 | 8 | 1 | FV1607A_ZT | N37:1 | FV | FV 1607-A DAMPER POSITION KILN 1 AIR FUEL |  | EU: % Position; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | FV1607A_ZT_IO | SampleRoom_R03:8:I.Ch1Data | FV1607A_ZT_IO:= SampleRoom_R03:8:I.Ch1Data; //FV 1607-A DAMPER POSITION KILN 1 AIR FUEL |  | _FV1607A_ZT | P_AIn | Val
402 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH3 | 1756-IF16 | 3 | 8 | 2 | FV1607B_ZT | N37:2 | FV | FV 1607-B DAMPER POSITION KILN 1 TEMPERING |  | EU: % Position; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | FV1607B_ZT_IO | SampleRoom_R03:8:I.Ch2Data | FV1607B_ZT_IO:= SampleRoom_R03:8:I.Ch2Data; //FV 1607-B DAMPER POSITION KILN 1 TEMPERING |  | _FV1607B_ZT | P_AIn | Val |  | Kiln1_Solid_Fuel_System_TaskD | Task_D | _FV1607B_ZT
403 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH4 | 1756-IF16 | 3 | 8 | 3 | PM4610KL2_1_FT | N37:3 | FT | PM 4610 FLOW RATE KILN 2 DIESEL PUMP (3.5 - 35 GPM) | FLEXIM | EU: GPM; V.MIN: 3.5; V.MAX: 35 | SampleRoom_R03 | I.Ch | INPUT | PM4610KL2_1_FT_IO | SampleRoom_R03:8:I.Ch3Data | PM4610KL2_1_FT_IO:= SampleRoom_R03:8:I.Ch3Data; //PM 4610 FLOW RATE KILN 2 DIESEL PUMP (3.5 - 35 GPM) |  | _PM4610KL2_1_FT | P_AIn | Val
404 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH5 | 1756-IF16 | 3 | 8 | 4 | FV1340_ZT | N37:4 | FV | FV 1340 DAMPER POSITION KILN 1 COOLER |  | EU: % Position; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | FV1340_ZT_IO | SampleRoom_R03:8:I.Ch4Data | FV1340_ZT_IO:= SampleRoom_R03:8:I.Ch4Data; //FV 1340 DAMPER POSITION KILN 1 COOLER |  | _FV1340_ZT | P_AIn | Val
405 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH6 | 1756-IF16 | 3 | 8 | 5 | PM4610KL1_FT | N37:5 | FT | PM 4610 FLOW RATE KILN 1 DIESEL PUMP (3.5 - 35 GPM) |  | EU: GPM; V.MIN: 3.5; V.MAX: 35 | SampleRoom_R03 | I.Ch | INPUT | PM4610KL1_FT_IO | SampleRoom_R03:8:I.Ch5Data | PM4610KL1_FT_IO:= SampleRoom_R03:8:I.Ch5Data; //PM 4610 FLOW RATE KILN 1 DIESEL PUMP (3.5 - 35 GPM) |  | _PM4610KL1_FT | P_AIn | Val
406 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH7 | 1756-IF16 | 3 | 8 | 6 |  | N37:6 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:8:I.Ch6Data | // SampleRoom_R03:8:I.Ch6Data SPARE
407 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH8 | 1756-IF16 | 3 | 8 | 7 | FIREDP_PT | N37:7 |  | FIRE DECK PLANT AIR 0-200PSI |  | EU: PSI; V.MIN: 0; V.MAX: 200 | SampleRoom_R03 | I.Ch | INPUT | FIREDP_PT_IO | SampleRoom_R03:8:I.Ch7Data | FIREDP_PT_IO:= SampleRoom_R03:8:I.Ch7Data; //FIRE DECK PLANT AIR 0-200PSI |  | _FIREDP_PT | P_AIn | Val
408 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH9 | 1756-IF16 | 3 | 8 | 8 |  | N37:8 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:8:I.Ch8Data | // SampleRoom_R03:8:I.Ch8Data SPARE | bar: EU to HH
409 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH10 | 1756-IF16 | 3 | 8 | 9 |  | N37:9 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:8:I.Ch9Data | // SampleRoom_R03:8:I.Ch9Data SPARE
410 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH11 | 1756-IF16 | 3 | 8 | 10 |  | N37:10 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:8:I.Ch10Data | // SampleRoom_R03:8:I.Ch10Data SPARE | bar: EU to HH
411 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH12 | 1756-IF16 | 3 | 8 | 11 |  | N37:11 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:8:I.Ch11Data | // SampleRoom_R03:8:I.Ch11Data SPARE
412 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH13 | 1756-IF16 | 3 | 8 | 12 | BM1602_1_IT | N37:12 | BM | BM 1602 AMPS KILN 1 COAL BALL MILL | SIGNAL CONDITIONER | EU: Ampers; V.MIN: 0; V.MAX: 110 | SampleRoom_R03 | I.Ch | INPUT | BM1602_1_IT_IO | SampleRoom_R03:8:I.Ch12Data | BM1602_1_IT_IO:= SampleRoom_R03:8:I.Ch12Data; //BM 1602 AMPS KILN 1 COAL BALL MILL |  | _BM1602_1_IT | P_AIn | Val | 1 |  |  |  | Kiln 1
413 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH14 | 1756-IF16 | 3 | 8 | 13 | FN1312_IT | N37:13 | FN | FN 1312 AMPS KILN 1 COOLER FAN |  | EU: Ampers; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | FN1312_IT_IO | SampleRoom_R03:8:I.Ch13Data | FN1312_IT_IO:= SampleRoom_R03:8:I.Ch13Data; //FN 1312 AMPS KILN 1 COOLER FAN |  | _FN1312_IT | P_AIn | Val |  | Kiln1_Main_TaskD | Task_D | _FN1312_IT
414 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH15 | 1756-IF16 | 3 | 8 | 14 |  | N37:14 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:8:I.Ch14Data | // SampleRoom_R03:8:I.Ch14Data SPARE
415 | SAMPLE R3G0M0 | 1771-IFE | 3 | 0 | CH16 | 1756-IF16 | 3 | 8 | 15 | PM4610KL2_2_FT | N37:15 | FT | PM 4610 KILN 2 DIESEL FLOW RATE 0-20GPM | Verify and Check | EU: GPM; V.MIN: 0; V.MAX: 20 | SampleRoom_R03 | I.Ch | INPUT | PM4610KL2_2_FT_IO | SampleRoom_R03:8:I.Ch15Data | PM4610KL2_2_FT_IO:= SampleRoom_R03:8:I.Ch15Data; //PM 4610 KILN 2 DIESEL FLOW RATE 0-20GPM |  | _PM4610KL2_2_FT | P_AIn | Val
416 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH1 | 1756-IF16 | 3 | 9 | 0 |  | N38:0 |  | SPARE | MOVED TO RACK 11 N31:32 | [9 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch0Data | // SampleRoom_R03:9:I.Ch0Data SPARE
417 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH2 | 1756-IF16 | 3 | 9 | 1 |  | N38:1 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch1Data | // SampleRoom_R03:9:I.Ch1Data SPARE
418 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH3 | 1756-IF16 | 3 | 9 | 2 |  | N38:2 | [12 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch2Data | // SampleRoom_R03:9:I.Ch2Data
419 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH4 | 1756-IF16 | 3 | 9 | 3 |  | N38:3 |  | SPARE | MOVED TO RACK 11 N31:31 | [9 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch3Data | // SampleRoom_R03:9:I.Ch3Data SPARE
420 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH5 | 1756-IF16 | 3 | 9 | 4 | FN1312_1_FT | N38:4 | FT | FN 1312 AIR FLOW KILN 1 COOLER FAN | ROSEMOUNT ANUBAR | EU: % Flow; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | FN1312_1_FT_IO | SampleRoom_R03:9:I.Ch4Data | FN1312_1_FT_IO:= SampleRoom_R03:9:I.Ch4Data; //FN 1312 AIR FLOW KILN 1 COOLER FAN |  | _FN1312_1_FT | P_AIn | Val
421 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH6 | 1756-IF16 | 3 | 9 | 5 |  | N38:5 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch5Data | // SampleRoom_R03:9:I.Ch5Data SPARE
422 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH7 | 1756-IF16 | 3 | 9 | 6 |  | N38:6 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch6Data | // SampleRoom_R03:9:I.Ch6Data SPARE
423 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH8 | 1756-IF16 | 3 | 9 | 7 |  | N38:7 |  | SPARE | MOVED TO RACK 5 N41:04 | [9 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch7Data | // SampleRoom_R03:9:I.Ch7Data SPARE
424 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH9 | 1756-IF16 | 3 | 9 | 8 |  | N38:8 |  | SPARE | MOVED TO RACK 5 N41:05 | [9 empty] | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch8Data | // SampleRoom_R03:9:I.Ch8Data SPARE
425 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH10 | 1756-IF16 | 3 | 9 | 9 | BM1602_2_LT | N38:9 | LT | BM 1602 LEVEL KILN 1 COAL BALL MILL |  | EU: % Level; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | BM1602_2_LT_IO | SampleRoom_R03:9:I.Ch9Data | BM1602_2_LT_IO:= SampleRoom_R03:9:I.Ch9Data; //BM 1602 LEVEL KILN 1 COAL BALL MILL |  | _BM1602_2_LT | P_AIn | Val | 1 |  |  |  | Kiln 1
426 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH11 | 1756-IF16 | 3 | 9 | 10 | OV1310_LT | N38:10 | LT | OV 1310 COOLER LEVEL KILN 1 OHMART/VEGA |  | EU: Feet; V.MIN: 0; V.MAX: 10 | SampleRoom_R03 | I.Ch | INPUT | OV1310_LT_IO | SampleRoom_R03:9:I.Ch10Data | OV1310_LT_IO:= SampleRoom_R03:9:I.Ch10Data; //OV 1310 COOLER LEVEL KILN 1 OHMART/VEGA |  | _OV1310_LT | P_AIn | Val |  | Kiln1_Main_TaskD | Task_D | _OV1310_LT
427 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH12 | 1756-IF16 | 3 | 9 | 11 | OV2310_LT | N38:11 | LT | OV 2310 COOLER LEVEL KILN 2 OHMART/VEGA |  | EU: Feet; V.MIN: 0; V.MAX: 10 | SampleRoom_R03 | I.Ch | INPUT | OV2310_LT_IO | SampleRoom_R03:9:I.Ch11Data | OV2310_LT_IO:= SampleRoom_R03:9:I.Ch11Data; //OV 2310 COOLER LEVEL KILN 2 OHMART/VEGA |  | _OV2310_LT | P_AIn | Val |  | Kiln2_Main_TaskD | Task_D | _OV2310_LT
428 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH13 | 1756-IF16 | 3 | 9 | 12 | OHV1310_LT | N38:12 | LT | OHMART VEGA 1-310 LEVEL 0-100% |  | EU: % Level; V.MIN: 0; V.MAX: 100 | SampleRoom_R03 | I.Ch | INPUT | OHV1310_LT_IO | SampleRoom_R03:9:I.Ch12Data | OHV1310_LT_IO:= SampleRoom_R03:9:I.Ch12Data; //OHMART VEGA 1-310 LEVEL 0-100% |  | _OHV1310_LT | P_AIn | Val
429 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH14 | 1756-IF16 | 3 | 9 | 13 | FN1312_2_FT | N38:13 | FT | AIR FLOW COOLER FAN 0-5 IWC |  | EU: "WC; V.MIN: 0; V.MAX: 5 | SampleRoom_R03 | I.Ch | INPUT | FN1312_2_FT_IO | SampleRoom_R03:9:I.Ch13Data | FN1312_2_FT_IO:= SampleRoom_R03:9:I.Ch13Data; //AIR FLOW COOLER FAN 0-5 IWC |  | _FN1312_2_FT | P_AIn | Val
430 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH15 | 1756-IF16 | 3 | 9 | 14 |  | N38:14 | TBD | SPARE | PYROMETER ON K1. NOT IN SERVICE | Notes: TBD | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch14Data | // SampleRoom_R03:9:I.Ch14Data SPARE
431 | SAMPLE R3G0M1 | 1771-IFE | 3 | 1 | CH16 | 1756-IF16 | 3 | 9 | 15 |  | N38:15 | TBD | SPARE | PYROMETER ON K1. NOT IN SERVICE | Notes: TBD | SampleRoom_R03 | I.Ch | INPUT |  | SampleRoom_R03:9:I.Ch15Data | // SampleRoom_R03:9:I.Ch15Data SPARE
432 | SAMPLE R3G1M0 | 1771-OFE | 3 | 2 | CH1+ | 1756-OF8I | 3 | 10 | 0 |  | N34:0 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[0].Data | // SampleRoom_R03:10:O.Ch[0].Data SPARE
433 | SAMPLE R3G1M0 | 1771-OFE | 3 | 2 | CH2+ | 1756-OF8I | 3 | 10 | 1 |  | N34:1 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[1].Data | // SampleRoom_R03:10:O.Ch[1].Data SPARE
434 | SAMPLE R3G1M0 | 1771-OFE | 3 | 2 | CH3+ | 1756-OF8I | 3 | 10 | 2 |  | N34:2 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[2].Data | // SampleRoom_R03:10:O.Ch[2].Data SPARE
435 | SAMPLE R3G1M0 | 1771-OFE | 3 | 2 | CH4+ | 1756-OF8I | 3 | 10 | 3 |  | N34:3 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[3].Data | // SampleRoom_R03:10:O.Ch[3].Data SPARE
436 | [5 empty] | 1756-OF8I | 3 | 10 | 4 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[4].Data | // SampleRoom_R03:10:O.Ch[4].Data SPARE
437 | [5 empty] | 1756-OF8I | 3 | 10 | 5 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[5].Data | // SampleRoom_R03:10:O.Ch[5].Data SPARE
438 | [5 empty] | 1756-OF8I | 3 | 10 | 6 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[6].Data | // SampleRoom_R03:10:O.Ch[6].Data SPARE
439 | [5 empty] | 1756-OF8I | 3 | 10 | 7 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:10:O.Ch[7].Data | // SampleRoom_R03:10:O.Ch[7].Data SPARE
440 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH1+ | 1756-IRT8I | 3 | 12 | 0 | BM1602_INLET_TE | N39:0 | TE | BM 1602 TEMPERATURE KILN 1 BALL MILL INLET | TC Type K | EU: °F; V.MIN: 0; V.MAX: 1000 | SampleRoom_R03 | I.Ch[ | INPUT | BM1602_INLET_TE_IO | SampleRoom_R03:12:I.Ch[0].Data | BM1602_INLET_TE_IO:= SampleRoom_R03:12:I.Ch[0].Data; //BM 1602 TEMPERATURE KILN 1 BALL MILL INLET |  | _BM1602_INLET_TE | P_AIn | Val | 0
441 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH2+ | 1756-IRT8I | 3 | 12 | 1 | BM1602_OUTLET_TE | N39:1 | TE | BM 1602 TEMPERATURE KILN 1 BALL MILL OUTLET | TC Type K | EU: °F; V.MIN: 0; V.MAX: 1000 | SampleRoom_R03 | I.Ch[ | INPUT | BM1602_OUTLET_TE_IO | SampleRoom_R03:12:I.Ch[1].Data | BM1602_OUTLET_TE_IO:= SampleRoom_R03:12:I.Ch[1].Data; //BM 1602 TEMPERATURE KILN 1 BALL MILL OUTLET |  | _BM1602_OUTLET_TE | P_AIn | Val | 1 | Kiln1_Solid_Fuel_System_TaskD | Task_D | _BM1602_OUTLET_TE | Kiln 1
442 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH3+ | 1756-IRT8I | 3 | 12 | 2 | KN1_SA_TE | N39:2 | TE | KILN 1 TEMPERATURE KILN 1 SECONDARY AIR | TC Type K | EU: °F; V.MIN: 0; V.MAX: 3000 | SampleRoom_R03 | I.Ch[ | INPUT | KN1_SA_TE_IO | SampleRoom_R03:12:I.Ch[2].Data | KN1_SA_TE_IO:= SampleRoom_R03:12:I.Ch[2].Data; //KILN 1 TEMPERATURE KILN 1 SECONDARY AIR |  | _KN1_SA_TE | P_AIn | Val
443 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH4+ | 1756-IRT8I | 3 | 12 | 3 | FN1605_INLET_TE | N39:3 | TE | FN 1-605 INLET TEMPERATURE KILN 1 MILL EXHAUST FAN | TC Type K | EU: °F; V.MIN: 0; V.MAX: 250 | SampleRoom_R03 | I.Ch[ | INPUT | FN1605_INLET_TE_IO | SampleRoom_R03:12:I.Ch[3].Data | FN1605_INLET_TE_IO:= SampleRoom_R03:12:I.Ch[3].Data; //FN 1-605 INLET TEMPERATURE KILN 1 MILL EXHAUST FAN |  | _FN1605_INLET_TE | P_AIn | Val | 1 | Kiln1_Main_TaskD | Task_D | _FN1605_INLET_TE | Kiil 1
444 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH5+ | 1756-IRT8I | 3 | 12 | 4 | VF1340A_TE | N39:4 | VF | VF 1340-A TEMPERATURE KILN 1 VIBRATING FEEDER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2000 | SampleRoom_R03 | I.Ch[ | INPUT | VF1340A_TE_IO | SampleRoom_R03:12:I.Ch[4].Data | VF1340A_TE_IO:= SampleRoom_R03:12:I.Ch[4].Data; //VF 1340-A TEMPERATURE KILN 1 VIBRATING FEEDER |  | _VF1340A_TE | P_AIn | Val |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340A_TE
445 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH6+ | 1756-IRT8I | 3 | 12 | 5 | VF1340B_TE | N39:5 | VF | VF 1340-B TEMPERATURE KILN 1 VIBRATING FEEDER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2000 | SampleRoom_R03 | I.Ch[ | INPUT | VF1340B_TE_IO | SampleRoom_R03:12:I.Ch[5].Data | VF1340B_TE_IO:= SampleRoom_R03:12:I.Ch[5].Data; //VF 1340-B TEMPERATURE KILN 1 VIBRATING FEEDER |  | _VF1340B_TE | P_AIn | Val |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340B_TE
446 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH7+ | 1756-IRT8I | 3 | 12 | 6 | VF1340C_TE | N39:6 | VF | VF 1340-C TEMPERATURE KILN 1 VIBRATING FEEDER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2000 | SampleRoom_R03 | I.Ch[ | INPUT | VF1340C_TE_IO | SampleRoom_R03:12:I.Ch[6].Data | VF1340C_TE_IO:= SampleRoom_R03:12:I.Ch[6].Data; //VF 1340-C TEMPERATURE KILN 1 VIBRATING FEEDER |  | _VF1340C_TE | P_AIn | Val |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340C_TE
447 | SAMPLE R3G1M1 | 1771-IXE | 3 | 3 | CH8+ | 1756-IRT8I | 3 | 12 | 7 | VF1340D_TE | N39:7 | VF | VF 1340-D TEMPERATURE KILN 1 VIBRATING FEEDER | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2000 | SampleRoom_R03 | I.Ch[ | INPUT | VF1340D_TE_IO | SampleRoom_R03:12:I.Ch[7].Data | VF1340D_TE_IO:= SampleRoom_R03:12:I.Ch[7].Data; //VF 1340-D TEMPERATURE KILN 1 VIBRATING FEEDER |  | _VF1340D_TE | P_AIn | Val |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340D_TE
448 | SAMPLE R3G2M0 | 1771-OFE | 3 | 4 | CH1+ | 1756-OF8I | 3 | 11 | 0 | VF1340A_SPT | N35:0 | VF | VF 1340-A SPEED KILN 1 VIBRATING FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 4095 | SampleRoom_R03 | O.Ch[ | OUTPUT | VF1340A_SPT_IO | SampleRoom_R03:11:O.Ch[0].Data | SampleRoom_R03:11:O.Ch[0].Data:=VF1340A_SPT_IO; //VF 1340-A SPEED KILN 1 VIBRATING FEEDER |  | _VF1340A_SPT | P_VSD | Out_SpeedRef |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340A_SPT
449 | SAMPLE R3G2M0 | 1771-OFE | 3 | 4 | CH2+ | 1756-OF8I | 3 | 11 | 1 | VF1340B_SPT | N35:1 | VF | VF 1340-B SPEED KILN 1 VIBRATING FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 4095 | SampleRoom_R03 | O.Ch[ | OUTPUT | VF1340B_SPT_IO | SampleRoom_R03:11:O.Ch[1].Data | SampleRoom_R03:11:O.Ch[1].Data:=VF1340B_SPT_IO; //VF 1340-B SPEED KILN 1 VIBRATING FEEDER |  | _VF1340B_SPT | P_VSD | Out_SpeedRef |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340B_SPT
450 | SAMPLE R3G2M0 | 1771-OFE | 3 | 4 | CH3+ | 1756-OF8I | 3 | 11 | 2 | VF1340C_SPT | N35:2 | VF | VF 1340-C SPEED KILN 1 VIBRATING FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 4095 | SampleRoom_R03 | O.Ch[ | OUTPUT | VF1340C_SPT_IO | SampleRoom_R03:11:O.Ch[2].Data | SampleRoom_R03:11:O.Ch[2].Data:=VF1340C_SPT_IO; //VF 1340-C SPEED KILN 1 VIBRATING FEEDER |  | _VF1340C_SPT | P_VSD | Out_SpeedRef |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340C_SPT
451 | SAMPLE R3G2M0 | 1771-OFE | 3 | 4 | CH4+ | 1756-OF8I | 3 | 11 | 3 | VF1340D_SPT | N35:3 | VF | VF 1340-D SPEED KILN 1 VIBRATING FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 4095 | SampleRoom_R03 | O.Ch[ | OUTPUT | VF1340D_SPT_IO | SampleRoom_R03:11:O.Ch[3].Data | SampleRoom_R03:11:O.Ch[3].Data:=VF1340D_SPT_IO; //VF 1340-D SPEED KILN 1 VIBRATING FEEDER |  | _VF1340D_SPT | P_VSD | Out_SpeedRef |  | Kiln1_Discharge_Cooler_TaskD | Task_D | _VF1340D_SPT
452 | [5 empty] | 1756-OF8I | 3 | 11 | 4 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:11:O.Ch[4].Data | // SampleRoom_R03:11:O.Ch[4].Data SPARE
453 | [5 empty] | 1756-OF8I | 3 | 11 | 5 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:11:O.Ch[5].Data | // SampleRoom_R03:11:O.Ch[5].Data SPARE
454 | [5 empty] | 1756-OF8I | 3 | 11 | 6 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:11:O.Ch[6].Data | // SampleRoom_R03:11:O.Ch[6].Data SPARE
455 | [5 empty] | 1756-OF8I | 3 | 11 | 7 |  |  |  | SPARE | [10 empty] | SampleRoom_R03 | O.Ch[ | OUTPUT |  | SampleRoom_R03:11:O.Ch[7].Data | // SampleRoom_R03:11:O.Ch[7].Data SPARE
456 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 00 | 1756-IA16 | 3 | 0 | 00 |  | I:034/0 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.00 | // SampleRoom_R03:0:I.Data.00 SPARE
457 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 01 | 1756-IA16 | 3 | 0 | 01 |  | I:034/1 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.01 | // SampleRoom_R03:0:I.Data.01 SPARE
458 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 02 | 1756-IA16 | 3 | 0 | 02 |  | I:034/2 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.02 | // SampleRoom_R03:0:I.Data.02 SPARE
459 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 03 | 1756-IA16 | 3 | 0 | 03 |  | I:034/3 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.03 | // SampleRoom_R03:0:I.Data.03 SPARE
460 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 04 | 1756-IA16 | 3 | 0 | 04 |  | I:034/4 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.04 | // SampleRoom_R03:0:I.Data.04 SPARE
461 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 05 | 1756-IA16 | 3 | 0 | 05 |  | I:034/5 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.05 | // SampleRoom_R03:0:I.Data.05 SPARE
462 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 06 | 1756-IA16 | 3 | 0 | 06 |  | I:034/6 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.06 | // SampleRoom_R03:0:I.Data.06 SPARE
463 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 07 | 1756-IA16 | 3 | 0 | 07 |  | I:034/7 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.07 | // SampleRoom_R03:0:I.Data.07 SPARE
464 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 10 | 1756-IA16 | 3 | 0 | 08 |  | I:034/10 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.08 | // SampleRoom_R03:0:I.Data.08 SPARE
465 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 11 | 1756-IA16 | 3 | 0 | 09 |  | I:034/11 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.09 | // SampleRoom_R03:0:I.Data.09 SPARE
466 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 12 | 1756-IA16 | 3 | 0 | 10 |  | I:034/12 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.10 | // SampleRoom_R03:0:I.Data.10 SPARE
467 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 13 | 1756-IA16 | 3 | 0 | 11 |  | I:034/13 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.11 | // SampleRoom_R03:0:I.Data.11 SPARE
468 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 14 | 1756-IA16 | 3 | 0 | 12 |  | I:034/14 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.12 | // SampleRoom_R03:0:I.Data.12 SPARE
469 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 15 | 1756-IA16 | 3 | 0 | 13 |  | I:034/15 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.13 | // SampleRoom_R03:0:I.Data.13 SPARE
470 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 16 | 1756-IA16 | 3 | 0 | 14 |  | I:034/16 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.14 | // SampleRoom_R03:0:I.Data.14 SPARE
471 | SAMPLE R3G4M0 | 1771-IAD | 3 | 8 | 17 | 1756-IA16 | 3 | 0 | 15 |  | I:034/17 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:0:I.Data.15 | // SampleRoom_R03:0:I.Data.15 SPARE
472 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-0 | 1756-OA16I | 3 | 4 | 0 | VF1340A_COIL | O:034/0 | VF | VF 1340-A RUN KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | VF1340A_COIL_IO | SampleRoom_R03:4:O.Data.0 | SampleRoom_R03:4:O.Data.0:=VF1340A_COIL_IO; //VF 1340-A RUN KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340A_M01 | P_VSD | PCmd_StartFwd |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340A_M01
473 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-1 | 1756-OA16I | 3 | 4 | 1 | VF1340B_COIL | O:034/1 | VF | VF 1340-B RUN KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | VF1340B_COIL_IO | SampleRoom_R03:4:O.Data.1 | SampleRoom_R03:4:O.Data.1:=VF1340B_COIL_IO; //VF 1340-B RUN KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340B_M01 | P_VSD | PCmd_StartFwd |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340B_M01
474 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-2 | 1756-OA16I | 3 | 4 | 2 | VF1340C_COIL | O:034/2 | VF | VF 1340-C RUN KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | VF1340C_COIL_IO | SampleRoom_R03:4:O.Data.2 | SampleRoom_R03:4:O.Data.2:=VF1340C_COIL_IO; //VF 1340-C RUN KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340C_M01 | P_VSD | PCmd_StartFwd |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340C_M01
475 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-3 | 1756-OA16I | 3 | 4 | 3 | VF1340D_COIL | O:034/3 | VF | VF 1340-D RUN KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | VF1340D_COIL_IO | SampleRoom_R03:4:O.Data.3 | SampleRoom_R03:4:O.Data.3:=VF1340D_COIL_IO; //VF 1340-D RUN KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340D_M01 | P_VSD | PCmd_StartFwd |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340D_M01
476 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-4 | 1756-OA16I | 3 | 4 | 4 |  | O:034/4 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.4 | // SampleRoom_R03:4:O.Data.4 SPARE
477 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-5 | 1756-OA16I | 3 | 4 | 5 |  | O:034/5 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.5 | // SampleRoom_R03:4:O.Data.5 SPARE
478 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-6 | 1756-OA16I | 3 | 4 | 6 |  | O:034/6 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.6 | // SampleRoom_R03:4:O.Data.6 SPARE
479 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-7 | 1756-OA16I | 3 | 4 | 7 |  | O:034/7 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.7 | // SampleRoom_R03:4:O.Data.7 SPARE
480 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-10 | 1756-OA16I | 3 | 4 | 8 |  | O:034/10 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.8 | // SampleRoom_R03:4:O.Data.8 SPARE
481 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-11 | 1756-OA16I | 3 | 4 | 9 |  | O:034/11 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.9 | // SampleRoom_R03:4:O.Data.9 SPARE
482 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-12 | 1756-OA16I | 3 | 4 | 10 |  | O:034/12 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.10 | // SampleRoom_R03:4:O.Data.10 SPARE
483 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-13 | 1756-OA16I | 3 | 4 | 11 |  | O:034/13 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.11 | // SampleRoom_R03:4:O.Data.11 SPARE
484 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-14 | 1756-OA16I | 3 | 4 | 12 |  | O:034/14 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.12 | // SampleRoom_R03:4:O.Data.12 SPARE
485 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-15 | 1756-OA16I | 3 | 4 | 13 |  | O:034/15 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.13 | // SampleRoom_R03:4:O.Data.13 SPARE
486 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-16 | 1756-OA16I | 3 | 4 | 14 |  | O:034/16 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.14 | // SampleRoom_R03:4:O.Data.14 SPARE
487 | SAMPLE R3G4M1 | 1771-ODD | 3 | 9 | L1-17 | 1756-OA16I | 3 | 4 | 15 |  | O:034/17 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:4:O.Data.15 | // SampleRoom_R03:4:O.Data.15 SPARE
488 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 00 | 1756-IA16 | 3 | 1 | 00 |  | I:035/0 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.00 | // SampleRoom_R03:1:I.Data.00 SPARE
489 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 01 | 1756-IA16 | 3 | 1 | 01 |  | I:035/1 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.01 | // SampleRoom_R03:1:I.Data.01 SPARE
490 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 02 | 1756-IA16 | 3 | 1 | 02 |  | I:035/2 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.02 | // SampleRoom_R03:1:I.Data.02 SPARE
491 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 03 | 1756-IA16 | 3 | 1 | 03 |  | I:035/3 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.03 | // SampleRoom_R03:1:I.Data.03 SPARE
492 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 04 | 1756-IA16 | 3 | 1 | 04 | MCR4_ALM | I:035/4 | ALARM | ALARM FIRE IN MCR #4 | [10 empty] | SampleRoom_R03 | I.Data | INPUT | MCR4_ALM_IO | SampleRoom_R03:1:I.Data.04 | MCR4_ALM_IO:= SampleRoom_R03:1:I.Data.04; //ALARM FIRE IN MCR #4 |  | _MCR4_ALM | P_DIn | Sts_PV
493 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 05 | 1756-IA16 | 3 | 1 | 05 |  | I:035/5 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.05 | // SampleRoom_R03:1:I.Data.05 SPARE
494 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 06 | 1756-IA16 | 3 | 1 | 06 | MCR6_ALM | I:035/6 | ALARM | ALARM FIRE IN MCR #6 | [10 empty] | SampleRoom_R03 | I.Data | INPUT | MCR6_ALM_IO | SampleRoom_R03:1:I.Data.06 | MCR6_ALM_IO:= SampleRoom_R03:1:I.Data.06; //ALARM FIRE IN MCR #6 |  | _MCR6_ALM | P_DIn | Sts_PV
495 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 07 | 1756-IA16 | 3 | 1 | 07 |  | I:035/7 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.07 | // SampleRoom_R03:1:I.Data.07 SPARE
496 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 10 | 1756-IA16 | 3 | 1 | 08 |  | I:035/10 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.08 | // SampleRoom_R03:1:I.Data.08 SPARE
497 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 11 | 1756-IA16 | 3 | 1 | 09 |  | I:035/11 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.09 | // SampleRoom_R03:1:I.Data.09 SPARE | bar: Notes to EU
498 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 12 | 1756-IA16 | 3 | 1 | 10 |  | I:035/12 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.10 | // SampleRoom_R03:1:I.Data.10 SPARE | bar: Notes to EU
499 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 13 | 1756-IA16 | 3 | 1 | 11 |  | I:035/13 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.11 | // SampleRoom_R03:1:I.Data.11 SPARE | bar: Notes to EU
500 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 14 | 1756-IA16 | 3 | 1 | 12 |  | I:035/14 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.12 | // SampleRoom_R03:1:I.Data.12 SPARE | bar: Notes to EU
501 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 15 | 1756-IA16 | 3 | 1 | 13 |  | I:035/15 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.13 | // SampleRoom_R03:1:I.Data.13 SPARE | bar: Notes to EU
502 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 16 | 1756-IA16 | 3 | 1 | 14 |  | I:035/16 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.14 | // SampleRoom_R03:1:I.Data.14 SPARE | bar: Notes to EU
503 | SAMPLE R3G5M0 | 1771-IAD | 3 | 10 | 17 | 1756-IA16 | 3 | 1 | 15 |  | I:035/17 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:1:I.Data.15 | // SampleRoom_R03:1:I.Data.15 SPARE | bar: Notes to EU
504 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-0 | 1756-OA16I | 3 | 5 | 0 |  | O:035/0 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.0 | // SampleRoom_R03:5:O.Data.0 SPARE
505 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-1 | 1756-OA16I | 3 | 5 | 1 |  | O:035/1 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.1 | // SampleRoom_R03:5:O.Data.1 SPARE
506 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-2 | 1756-OA16I | 3 | 5 | 2 |  | O:035/2 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.2 | // SampleRoom_R03:5:O.Data.2 SPARE
507 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-3 | 1756-OA16I | 3 | 5 | 3 |  | O:035/3 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.3 | // SampleRoom_R03:5:O.Data.3 SPARE
508 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-4 | 1756-OA16I | 3 | 5 | 4 |  | O:035/4 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.4 | // SampleRoom_R03:5:O.Data.4 SPARE
509 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-5 | 1756-OA16I | 3 | 5 | 5 |  | O:035/5 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.5 | // SampleRoom_R03:5:O.Data.5 SPARE
510 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-6 | 1756-OA16I | 3 | 5 | 6 |  | O:035/6 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.6 | // SampleRoom_R03:5:O.Data.6 SPARE
511 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-7 | 1756-OA16I | 3 | 5 | 7 |  | O:035/7 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.7 | // SampleRoom_R03:5:O.Data.7 SPARE
512 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-10 | 1756-OA16I | 3 | 5 | 8 |  | O:035/10 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.8 | // SampleRoom_R03:5:O.Data.8 SPARE
513 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-11 | 1756-OA16I | 3 | 5 | 9 |  | O:035/11 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.9 | // SampleRoom_R03:5:O.Data.9 SPARE
514 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-12 | 1756-OA16I | 3 | 5 | 10 |  | O:035/12 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.10 | // SampleRoom_R03:5:O.Data.10 SPARE
515 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-13 | 1756-OA16I | 3 | 5 | 11 |  | O:035/13 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.11 | // SampleRoom_R03:5:O.Data.11 SPARE
516 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-14 | 1756-OA16I | 3 | 5 | 12 |  | O:035/14 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.12 | // SampleRoom_R03:5:O.Data.12 SPARE
517 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-15 | 1756-OA16I | 3 | 5 | 13 |  | O:035/15 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.13 | // SampleRoom_R03:5:O.Data.13 SPARE
518 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-16 | 1756-OA16I | 3 | 5 | 14 |  | O:035/16 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.14 | // SampleRoom_R03:5:O.Data.14 SPARE
519 | SAMPLE R3G5M1 | 1771-ODD | 3 | 11 | L1-17 | 1756-OA16I | 3 | 5 | 15 |  | O:035/17 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:5:O.Data.15 | // SampleRoom_R03:5:O.Data.15 SPARE
520 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 00 | 1756-IA16 | 3 | 2 | 00 |  | I:036/0 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.00 | // SampleRoom_R03:2:I.Data.00 SPARE
521 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 01 | 1756-IA16 | 3 | 2 | 01 |  | I:036/1 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.01 | // SampleRoom_R03:2:I.Data.01 SPARE
522 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 02 | 1756-IA16 | 3 | 2 | 02 |  | I:036/2 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.02 | // SampleRoom_R03:2:I.Data.02 SPARE
523 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 03 | 1756-IA16 | 3 | 2 | 03 |  | I:036/3 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.03 | // SampleRoom_R03:2:I.Data.03 SPARE
524 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 04 | 1756-IA16 | 3 | 2 | 04 |  | I:036/4 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.04 | // SampleRoom_R03:2:I.Data.04 SPARE
525 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 05 | 1756-IA16 | 3 | 2 | 05 |  | I:036/5 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.05 | // SampleRoom_R03:2:I.Data.05 SPARE
526 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 06 | 1756-IA16 | 3 | 2 | 06 |  | I:036/6 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.06 | // SampleRoom_R03:2:I.Data.06 SPARE
527 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 07 | 1756-IA16 | 3 | 2 | 07 |  | I:036/7 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.07 | // SampleRoom_R03:2:I.Data.07 SPARE
528 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 10 | 1756-IA16 | 3 | 2 | 08 |  | I:036/10 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.08 | // SampleRoom_R03:2:I.Data.08 SPARE
529 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 11 | 1756-IA16 | 3 | 2 | 09 |  | I:036/11 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.09 | // SampleRoom_R03:2:I.Data.09 SPARE | bar: Notes to EU
530 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 12 | 1756-IA16 | 3 | 2 | 10 |  | I:036/12 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.10 | // SampleRoom_R03:2:I.Data.10 SPARE | bar: Notes to EU
531 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 13 | 1756-IA16 | 3 | 2 | 11 |  | I:036/13 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.11 | // SampleRoom_R03:2:I.Data.11 SPARE | bar: Notes to EU
532 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 14 | 1756-IA16 | 3 | 2 | 12 |  | I:036/14 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.12 | // SampleRoom_R03:2:I.Data.12 SPARE | bar: Notes to EU
533 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 15 | 1756-IA16 | 3 | 2 | 13 |  | I:036/15 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.13 | // SampleRoom_R03:2:I.Data.13 SPARE | bar: Notes to EU
534 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 16 | 1756-IA16 | 3 | 2 | 14 |  | I:036/16 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.14 | // SampleRoom_R03:2:I.Data.14 SPARE | bar: Notes to EU
535 | SAMPLE R3G6MO | 1771-IAD | 3 | 12 | 17 | 1756-IA16 | 3 | 2 | 15 |  | I:036/17 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:2:I.Data.15 | // SampleRoom_R03:2:I.Data.15 SPARE | bar: Notes to EU
536 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-0 | 1756-OA16I | 3 | 6 | 0 | IV1607_ZVO | O:036/0 | IV | IV 1607 OPEN KILN 1 ISOLATION VALVE #1 | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | IV1607_ZVO_IO | SampleRoom_R03:6:O.Data.0 | SampleRoom_R03:6:O.Data.0:=IV1607_ZVO_IO; //IV 1607 OPEN KILN 1 ISOLATION VALVE #1 |  | _IV1607_ZVO | NA | NA
537 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-1 | 1756-OA16I | 3 | 6 | 1 |  | O:036/1 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.1 | // SampleRoom_R03:6:O.Data.1 SPARE
538 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-2 | 1756-OA16I | 3 | 6 | 2 |  | O:036/2 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.2 | // SampleRoom_R03:6:O.Data.2 SPARE
539 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-3 | 1756-OA16I | 3 | 6 | 3 |  | O:036/3 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.3 | // SampleRoom_R03:6:O.Data.3 SPARE
540 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-4 | 1756-OA16I | 3 | 6 | 4 | KN1_DS_SV | O:036/4 | SV | K1 Diesel Torch Solenoid | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | KN1_DS_SV_IO | SampleRoom_R03:6:O.Data.4 | SampleRoom_R03:6:O.Data.4:=KN1_DS_SV_IO; //K1 Diesel Torch Solenoid |  | NA | NA | NA
541 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-5 | 1756-OA16I | 3 | 6 | 5 | KN2_DS_SV | O:036/5 | SV | K2 Diesel Torch Solenoid | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | KN2_DS_SV_IO | SampleRoom_R03:6:O.Data.5 | SampleRoom_R03:6:O.Data.5:=KN2_DS_SV_IO; //K2 Diesel Torch Solenoid |  | NA | NA | NA
542 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-6 | 1756-OA16I | 3 | 6 | 6 |  | O:036/6 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.6 | // SampleRoom_R03:6:O.Data.6 SPARE
543 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-7 | 1756-OA16I | 3 | 6 | 7 |  | O:036/7 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.7 | // SampleRoom_R03:6:O.Data.7 SPARE
544 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-10 | 1756-OA16I | 3 | 6 | 8 |  | O:036/10 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.8 | // SampleRoom_R03:6:O.Data.8 SPARE
545 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-11 | 1756-OA16I | 3 | 6 | 9 |  | O:036/11 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.9 | // SampleRoom_R03:6:O.Data.9 SPARE
546 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-12 | 1756-OA16I | 3 | 6 | 10 |  | O:036/12 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.10 | // SampleRoom_R03:6:O.Data.10 SPARE
547 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-13 | 1756-OA16I | 3 | 6 | 11 |  | O:036/13 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.11 | // SampleRoom_R03:6:O.Data.11 SPARE
548 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-14 | 1756-OA16I | 3 | 6 | 12 |  | O:036/14 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.12 | // SampleRoom_R03:6:O.Data.12 SPARE
549 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-15 | 1756-OA16I | 3 | 6 | 13 |  | O:036/15 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.13 | // SampleRoom_R03:6:O.Data.13 SPARE
550 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-16 | 1756-OA16I | 3 | 6 | 14 |  | O:036/16 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.14 | // SampleRoom_R03:6:O.Data.14 SPARE
551 | SAMPLE R3G6M1 | 1771-ODD | 3 | 13 | L1-17 | 1756-OA16I | 3 | 6 | 15 |  | O:036/17 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:6:O.Data.15 | // SampleRoom_R03:6:O.Data.15 SPARE
552 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 00 | 1756-IA16 | 3 | 3 | 00 | VF1340A_AUX | I:037/0 | VF | VF 1340-A AUX FDBK KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | I.Data | INPUT | VF1340A_AUX_IO | SampleRoom_R03:3:I.Data.00 | VF1340A_AUX_IO:= SampleRoom_R03:3:I.Data.00; //VF 1340-A AUX FDBK KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340A_M01 | P_VSD | Sts_Running |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340A_M01
553 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 01 | 1756-IA16 | 3 | 3 | 01 | VF1340B_AUX | I:037/1 | VF | VF 1340-B AUX FDBK KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | I.Data | INPUT | VF1340B_AUX_IO | SampleRoom_R03:3:I.Data.01 | VF1340B_AUX_IO:= SampleRoom_R03:3:I.Data.01; //VF 1340-B AUX FDBK KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340B_M01 | P_VSD | Sts_Running |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340B_M01
554 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 02 | 1756-IA16 | 3 | 3 | 02 | VF1340C_AUX | I:037/2 | VF | VF 1340-C AUX FDBK KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | I.Data | INPUT | VF1340C_AUX_IO | SampleRoom_R03:3:I.Data.02 | VF1340C_AUX_IO:= SampleRoom_R03:3:I.Data.02; //VF 1340-C AUX FDBK KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340C_M01 | P_VSD | Sts_Running |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340C_M01
555 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 03 | 1756-IA16 | 3 | 3 | 03 | VF1340D_AUX | I:037/3 | VF | VF 1340-D AUX FDBK KILN 1 COOLER VIBRATORY FEEDER | [10 empty] | SampleRoom_R03 | I.Data | INPUT | VF1340D_AUX_IO | SampleRoom_R03:3:I.Data.03 | VF1340D_AUX_IO:= SampleRoom_R03:3:I.Data.03; //VF 1340-D AUX FDBK KILN 1 COOLER VIBRATORY FEEDER |  | _VF1340D_M01 | P_VSD | Sts_Running |  | Kiln1_Discharge_Cooler_TaskC | Task_C | _VF1340D_M01
556 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 04 | 1756-IA16 | 3 | 3 | 04 | IV1215_ZVC | I:037/4 | IV | IV 1215 LIMIT SWITCH KILN 1 ISOLATION VALVE CLOSED | [10 empty] | SampleRoom_R03 | I.Data | INPUT | IV1215_ZVC_IO | SampleRoom_R03:3:I.Data.04 | IV1215_ZVC_IO:= SampleRoom_R03:3:I.Data.04; //IV 1215 LIMIT SWITCH KILN 1 ISOLATION VALVE CLOSED |  | _IV1215_ZVC | NA | NA
557 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 05 | 1756-IA16 | 3 | 3 | 05 | IV1211_ZVC | I:037/5 | IV | IV 1211 LIMIT SWITCH KILN 1 ISOLATION VALVE CLOSED | [10 empty] | SampleRoom_R03 | I.Data | INPUT | IV1211_ZVC_IO | SampleRoom_R03:3:I.Data.05 | IV1211_ZVC_IO:= SampleRoom_R03:3:I.Data.05; //IV 1211 LIMIT SWITCH KILN 1 ISOLATION VALVE CLOSED |  | _IV1211_ZVC | NA | NA
558 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 06 | 1756-IA16 | 3 | 3 | 06 |  | I:037/6 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:3:I.Data.06 | // SampleRoom_R03:3:I.Data.06 SPARE
559 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 07 | 1756-IA16 | 3 | 3 | 07 |  | I:037/7 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:3:I.Data.07 | // SampleRoom_R03:3:I.Data.07 SPARE
560 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 10 | 1756-IA16 | 3 | 3 | 08 | IV1215_ZVO | I:037/10 | IV | IV 1215 LIMIT SWITCH KILN 1 ISOLATION VALVE OPEN | [10 empty] | SampleRoom_R03 | I.Data | INPUT | IV1215_ZVO_IO | SampleRoom_R03:3:I.Data.08 | IV1215_ZVO_IO:= SampleRoom_R03:3:I.Data.08; //IV 1215 LIMIT SWITCH KILN 1 ISOLATION VALVE OPEN |  | _IV1215_ZVO | NA | NA
561 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 11 | 1756-IA16 | 3 | 3 | 09 | IV1211_ZVO | I:037/11 | IV | IV 1211 LIMIT SWITCH KILN 1 ISOLATION VALVE OPEN | [10 empty] | SampleRoom_R03 | I.Data | INPUT | IV1211_ZVO_IO | SampleRoom_R03:3:I.Data.09 | IV1211_ZVO_IO:= SampleRoom_R03:3:I.Data.09; //IV 1211 LIMIT SWITCH KILN 1 ISOLATION VALVE OPEN |  | _IV1211_ZVO | NA | NA
562 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 12 | 1756-IA16 | 3 | 3 | 10 |  | I:037/12 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:3:I.Data.10 | // SampleRoom_R03:3:I.Data.10 SPARE
563 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 13 | 1756-IA16 | 3 | 3 | 11 | WF1601_AUX | I:037/13 | WF | WF 1601 AUX FDBK KILN 1 COAL WEIGH FEEDER | [10 empty] | SampleRoom_R03 | I.Data | INPUT | WF1601_AUX_IO | SampleRoom_R03:3:I.Data.11 | WF1601_AUX_IO:= SampleRoom_R03:3:I.Data.11; //WF 1601 AUX FDBK KILN 1 COAL WEIGH FEEDER |  | _WF1601_M01 | P_Motor | Sts_Running |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _WF1601_M01
564 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 14 | 1756-IA16 | 3 | 3 | 12 |  | I:037/14 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:3:I.Data.12 | // SampleRoom_R03:3:I.Data.12 SPARE
565 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 15 | 1756-IA16 | 3 | 3 | 13 |  | I:037/15 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:3:I.Data.13 | // SampleRoom_R03:3:I.Data.13 SPARE
566 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 16 | 1756-IA16 | 3 | 3 | 14 |  | I:037/16 |  | SPARE | [10 empty] | SampleRoom_R03 | I.Data | INPUT |  | SampleRoom_R03:3:I.Data.14 | // SampleRoom_R03:3:I.Data.14 SPARE
567 | SAMPLE R3G7M0 | 1771-IAD | 3 | 14 | 17 | 1756-IA16 | 3 | 3 | 15 | CL1310_LAH | I:037/17 |  | C 1310 ALARM KILN 1 COOLER FULL A2D2 | [10 empty] | SampleRoom_R03 | I.Data | INPUT | CL1310_LAH_IO | SampleRoom_R03:3:I.Data.15 | CL1310_LAH_IO:= SampleRoom_R03:3:I.Data.15; //C 1310 ALARM KILN 1 COOLER FULL A2D2 |  | _CL1310_LAH | P_DIn | Sts_PV | 0
568 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-0 | 1756-OA16I | 3 | 7 | 0 |  | O:037/0 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.0 | // SampleRoom_R03:7:O.Data.0 SPARE | bar: Notes
569 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-1 | 1756-OA16I | 3 | 7 | 1 |  | O:037/1 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.1 | // SampleRoom_R03:7:O.Data.1 SPARE | bar: Notes
570 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-2 | 1756-OA16I | 3 | 7 | 2 |  | O:037/2 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.2 | // SampleRoom_R03:7:O.Data.2 SPARE
571 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-3 | 1756-OA16I | 3 | 7 | 3 |  | O:037/3 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.3 | // SampleRoom_R03:7:O.Data.3 SPARE
572 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-4 | 1756-OA16I | 3 | 7 | 4 | FV1607B_XY_A | O:037/4 | FV | FV 1607-B OPEN KILN 1 BM TEMPERING TEE DAMPER | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | FV1607B_XY_A_IO | SampleRoom_R03:7:O.Data.4 | SampleRoom_R03:7:O.Data.4:=FV1607B_XY_A_IO; //FV 1607-B OPEN KILN 1 BM TEMPERING TEE DAMPER |  | NA | NA | NA | bar: Notes
573 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-5 | 1756-OA16I | 3 | 7 | 5 | FV1607B_XY_B | O:037/5 | FV | FV 1607-B CLOSE KILN 1 BM TEMPERING TEE DAMPER | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT | FV1607B_XY_B_IO | SampleRoom_R03:7:O.Data.5 | SampleRoom_R03:7:O.Data.5:=FV1607B_XY_B_IO; //FV 1607-B CLOSE KILN 1 BM TEMPERING TEE DAMPER |  | NA | NA | NA | bar: Notes
574 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-6 | 1756-OA16I | 3 | 7 | 6 |  | O:037/6 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.6 | // SampleRoom_R03:7:O.Data.6 SPARE
575 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-7 | 1756-OA16I | 3 | 7 | 7 |  | O:037/7 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.7 | // SampleRoom_R03:7:O.Data.7 SPARE
576 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-10 | 1756-OA16I | 3 | 7 | 8 |  | O:037/10 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.8 | // SampleRoom_R03:7:O.Data.8 SPARE
577 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-11 | 1756-OA16I | 3 | 7 | 9 |  | O:037/11 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.9 | // SampleRoom_R03:7:O.Data.9 SPARE
578 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-12 | 1756-OA16I | 3 | 7 | 10 |  | O:037/12 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.10 | // SampleRoom_R03:7:O.Data.10 SPARE
579 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-13 | 1756-OA16I | 3 | 7 | 11 |  | O:037/13 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.11 | // SampleRoom_R03:7:O.Data.11 SPARE
580 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-14 | 1756-OA16I | 3 | 7 | 12 |  | O:037/14 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.12 | // SampleRoom_R03:7:O.Data.12 SPARE
581 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-15 | 1756-OA16I | 3 | 7 | 13 |  | O:037/15 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.13 | // SampleRoom_R03:7:O.Data.13 SPARE
582 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-16 | 1756-OA16I | 3 | 7 | 14 |  | O:037/16 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.14 | // SampleRoom_R03:7:O.Data.14 SPARE
583 | SAMPLE R3G7M1 | 1771-ODD | 3 | 15 | L1-17 | 1756-OA16I | 3 | 7 | 15 |  | O:037/17 |  | SPARE | [10 empty] | SampleRoom_R03 | O.Data | OUTPUT |  | SampleRoom_R03:7:O.Data.15 | // SampleRoom_R03:7:O.Data.15 SPARE
584 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH1+ | 1756-IF16 | 4 | 8 | 0 | PM23051_PT | N40:0 | PM | PM 2305-1 PRESSURE KILN 2 PH HYDRAULIC PUMP #1 |  | EU: PSIG; V.MIN: 0; V.MAX: 3000 | K2_Preheater_R04 | I.Ch | INPUT | PM23051_PT_IO | K2_Preheater_R04:8:I.Ch0Data | PM23051_PT_IO:= K2_Preheater_R04:8:I.Ch0Data; //PM 2305-1 PRESSURE KILN 2 PH HYDRAULIC PUMP #1 |  | _PM23051_PT | P_AIn | Val |  | Kiln2_Preheater_TaskD | Task_D | _PM23051_PT
585 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH1- | 1756-IF16 | 4 | 8 | 2 |  | N40:2 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch2Data | // K2_Preheater_R04:8:I.Ch2Data SPARE
586 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH2+ | 1756-IF16 | 4 | 8 | 1 | PM23052_PT | N40:1 | PM | PM 2305-2 PRESSURE KILN 2 PH HYDRAULIC PUMP #2 |  | EU: PSIG; V.MIN: 0; V.MAX: 3000 | K2_Preheater_R04 | I.Ch | INPUT | PM23052_PT_IO | K2_Preheater_R04:8:I.Ch1Data | PM23052_PT_IO:= K2_Preheater_R04:8:I.Ch1Data; //PM 2305-2 PRESSURE KILN 2 PH HYDRAULIC PUMP #2 |  | _PM23052_PT | P_DIn | Sts_PV |  | Kiln2_Preheater_TaskD | Task_D | _PM23052_PT
587 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH2- | 1756-IF16 | 4 | 8 | 3 |  | N40:3 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch3Data | // K2_Preheater_R04:8:I.Ch3Data SPARE
588 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH3+ | 1756-IF16 | 4 | 8 | 4 |  | N40:4 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch4Data | // K2_Preheater_R04:8:I.Ch4Data SPARE
589 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH3- | 1756-IF16 | 4 | 8 | 5 |  | N40:5 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch5Data | // K2_Preheater_R04:8:I.Ch5Data SPARE
590 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH4+ | 1756-IF16 | 4 | 8 | 6 |  | N40:6 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch6Data | // K2_Preheater_R04:8:I.Ch6Data SPARE
591 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH4- | 1756-IF16 | 4 | 8 | 7 |  | N40:7 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch7Data | // K2_Preheater_R04:8:I.Ch7Data SPARE
592 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH5+ | 1756-IF16 | 4 | 8 | 8 |  | N40:8 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch8Data | // K2_Preheater_R04:8:I.Ch8Data SPARE | bar: Notes to HH
593 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH5- | 1756-IF16 | 4 | 8 | 9 |  | N40:9 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch9Data | // K2_Preheater_R04:8:I.Ch9Data SPARE | bar: Notes to HH
594 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH6+ | 1756-IF16 | 4 | 8 | 10 |  | N40:10 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch10Data | // K2_Preheater_R04:8:I.Ch10Data SPARE
595 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH6- | 1756-IF16 | 4 | 8 | 11 |  | N40:11 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch11Data | // K2_Preheater_R04:8:I.Ch11Data SPARE
596 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH7+ | 1756-IF16 | 4 | 8 | 12 |  | N40:12 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch12Data | // K2_Preheater_R04:8:I.Ch12Data SPARE
597 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH7- | 1756-IF16 | 4 | 8 | 13 |  | N40:13 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch13Data | // K2_Preheater_R04:8:I.Ch13Data SPARE
598 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH8+ | 1756-IF16 | 4 | 8 | 14 |  | N40:14 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch14Data | // K2_Preheater_R04:8:I.Ch14Data SPARE | bar: Notes to HH
599 | PH2 R4G0M0 | 1771-IFE | 4 | 0 | CH8- | 1756-IF16 | 4 | 8 | 15 |  | N40:15 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch | INPUT |  | K2_Preheater_R04:8:I.Ch15Data | // K2_Preheater_R04:8:I.Ch15Data SPARE | bar: Notes to HH
600 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH1+ | 1756-IRT8I | 4 | 9 | 0 | PH1306_IN_TE | N59:1 |  | TEMPERATURE KILN 1 PH INLET |  | Notes: From 4_PH2_NEW | K2_Preheater_R04 | I.Ch[ | INPUT | PH1306_IN_TE_IO | K2_Preheater_R04:9:I.Ch[0].Data | PH1306_IN_TE_IO:= K2_Preheater_R04:9:I.Ch[0].Data; //TEMPERATURE KILN 1 PH INLET |  | _PH1306_IN_TE | P_AIn | Val
601 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH2+ | 1756-IRT8I | 4 | 9 | 1 | PH1306_OUT_TE | N59:2 |  | TEMPERATURE KILN 1 PH OUTLET |  | Notes: From 4_PH2_NEW | K2_Preheater_R04 | I.Ch[ | INPUT | PH1306_OUT_TE_IO | K2_Preheater_R04:9:I.Ch[1].Data | PH1306_OUT_TE_IO:= K2_Preheater_R04:9:I.Ch[1].Data; //TEMPERATURE KILN 1 PH OUTLET |  | _PH1306_OUT_TE | P_AIn | Val
602 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH3+ | 1756-IRT8I | 4 | REMOVE | 2 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[2].Data | // K2_Preheater_R04:REMOVE:I.Ch[2].Data SPARE
603 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH4+ | 1756-IRT8I | 4 | REMOVE | 3 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[3].Data | // K2_Preheater_R04:REMOVE:I.Ch[3].Data SPARE
604 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH5+ | 1756-IRT8I | 4 | 9 | 2 | DC2319_EXIT_TE | N59:4 |  | DC 2319 EXIT TEMPERATURE KILN 2 MULTICLONE | TC Type K | EU: °F; V.MIN: 0; V.MAX: 1000 | K2_Preheater_R04 | I.Ch[ | INPUT | DC2319_EXIT_TE_IO | K2_Preheater_R04:9:I.Ch[2].Data | DC2319_EXIT_TE_IO:= K2_Preheater_R04:9:I.Ch[2].Data; //DC 2319 EXIT TEMPERATURE KILN 2 MULTICLONE |  | _DC2319_EXIT_TE | P_AIn | Val | 0
605 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH6+ | 1756-IRT8I | 4 | 9 | 3 | KL2PH01_INLET_ET | N59:5 |  | TEMPERATURE KILN 2 PH INLET | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2400 | K2_Preheater_R04 | I.Ch[ | INPUT | KL2PH01_INLET_ET_IO | K2_Preheater_R04:9:I.Ch[3].Data | KL2PH01_INLET_ET_IO:= K2_Preheater_R04:9:I.Ch[3].Data; //TEMPERATURE KILN 2 PH INLET |  | _KL2PH01_INLET_ET | P_AIn | Val
606 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH7+ | 1756-IRT8I | 4 | 9 | 4 | KL2PH01_OUTLET_TE | N59:6 |  | TEMPERATURE KILN 2 PH OUTLET | TC Type K | EU: °F; V.MIN: 0; V.MAX: 800 | K2_Preheater_R04 | I.Ch[ | INPUT | KL2PH01_OUTLET_TE_IO | K2_Preheater_R04:9:I.Ch[4].Data | KL2PH01_OUTLET_TE_IO:= K2_Preheater_R04:9:I.Ch[4].Data; //TEMPERATURE KILN 2 PH OUTLET |  | _KL2PH01_OUTLET_TE | P_AIn | Val |  | Kiln2_Preheater_TaskD | Task_D | _KL2PH01_OUTLET_TE
607 | PH2 R4G0M1 | 1771-IXE/D | 4 | 1 | CH8+ | 1756-IRT8I | 4 | 9 | 5 | KN2_EXIT_TE | N59:7 |  | TEMPERATURE KILN 2 EXIT | TC Type K | EU: °F; V.MIN: 0; V.MAX: 3000 | K2_Preheater_R04 | I.Ch[ | INPUT | KN2_EXIT_TE_IO | K2_Preheater_R04:9:I.Ch[5].Data | KN2_EXIT_TE_IO:= K2_Preheater_R04:9:I.Ch[5].Data; //TEMPERATURE KILN 2 EXIT |  | NA | NA | NA
608 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH1+ | 1756-IRT8I | 4 | 9 | 6 | PH2RAM1_TE | N49:0 | PH | PH 2305 RAM 1 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM1_TE_IO | K2_Preheater_R04:9:I.Ch[6].Data | PH2RAM1_TE_IO:= K2_Preheater_R04:9:I.Ch[6].Data; //PH 2305 RAM 1 TEMPERATURE KILN 2 |  | _PH2RAM1_TE | P_AIn | Val
609 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH2+ | 1756-IRT8I | 4 | 9 | 7 | PH2RAM3_TE | N49:1 | PH | PH 2305 RAM 3 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM3_TE_IO | K2_Preheater_R04:9:I.Ch[7].Data | PH2RAM3_TE_IO:= K2_Preheater_R04:9:I.Ch[7].Data; //PH 2305 RAM 3 TEMPERATURE KILN 2 |  | _PH2RAM3_TE | P_AIn | Val
610 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH3+ | 1756-IRT8I | 4 | 10 | 0 | PH2RAM5_TE | N49:2 | PH | PH 2305 RAM 5 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM5_TE_IO | K2_Preheater_R04:10:I.Ch[0].Data | PH2RAM5_TE_IO:= K2_Preheater_R04:10:I.Ch[0].Data; //PH 2305 RAM 5 TEMPERATURE KILN 2 |  | _PH2RAM5_TE | P_AIn | Val
611 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH4+ | 1756-IRT8I | 4 | 10 | 1 | PH2RAM7_TE | N49:3 | PH | PH 2305 RAM 7 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM7_TE_IO | K2_Preheater_R04:10:I.Ch[1].Data | PH2RAM7_TE_IO:= K2_Preheater_R04:10:I.Ch[1].Data; //PH 2305 RAM 7 TEMPERATURE KILN 2 |  | _PH2RAM7_TE | P_AIn | Val
612 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH5+ | 1756-IRT8I | 4 | 10 | 2 | PH2RAM9_TE | N49:4 | PH | PH 2305 RAM 9 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM9_TE_IO | K2_Preheater_R04:10:I.Ch[2].Data | PH2RAM9_TE_IO:= K2_Preheater_R04:10:I.Ch[2].Data; //PH 2305 RAM 9 TEMPERATURE KILN 2 |  | _PH2RAM9_TE | P_AIn | Val
613 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH6+ | 1756-IRT8I | 4 | 10 | 3 | PH2RAM11_TE | N49:5 | PH | PH 2305 RAM 11 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM11_TE_IO | K2_Preheater_R04:10:I.Ch[3].Data | PH2RAM11_TE_IO:= K2_Preheater_R04:10:I.Ch[3].Data; //PH 2305 RAM 11 TEMPERATURE KILN 2 |  | _PH2RAM11_TE | P_AIn | Val
614 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH7+ | 1756-IRT8I | 4 | 10 | 4 | PH2RAM13_TE | N49:6 | PH | PH 2305 RAM 13 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM13_TE_IO | K2_Preheater_R04:10:I.Ch[4].Data | PH2RAM13_TE_IO:= K2_Preheater_R04:10:I.Ch[4].Data; //PH 2305 RAM 13 TEMPERATURE KILN 2 |  | _PH2RAM13_TE | P_AIn | Val
615 | PH2 R4G1M0 | 1771-IXE | 4 | 2 | CH8+ | 1756-IRT8I | 4 | 10 | 5 | PH2RAM15_TE | N49:7 | PH | PH 2305 RAM 15 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM15_TE_IO | K2_Preheater_R04:10:I.Ch[5].Data | PH2RAM15_TE_IO:= K2_Preheater_R04:10:I.Ch[5].Data; //PH 2305 RAM 15 TEMPERATURE KILN 2 |  | _PH2RAM15_TE | P_AIn | Val
616 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH1+ | 1756-IRT8I | 4 | 10 | 6 | PH2RAM17_TE | N60:0 | PH | PH 2305 RAM 17 TEMPERATURE KILN 2 | TC Type K | EU: °F; V.MIN: 0; V.MAX: 2516 | K2_Preheater_R04 | I.Ch[ | INPUT | PH2RAM17_TE_IO | K2_Preheater_R04:10:I.Ch[6].Data | PH2RAM17_TE_IO:= K2_Preheater_R04:10:I.Ch[6].Data; //PH 2305 RAM 17 TEMPERATURE KILN 2 |  | _PH2RAM17_TE | P_AIn | Val
617 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH2+ | 1756-IRT8I | 4 | 10 | 7 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:10:I.Ch[7].Data | // K2_Preheater_R04:10:I.Ch[7].Data SPARE
618 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH3+ | 1756-IRT8I | 4 | REMOVE | 2 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[2].Data | // K2_Preheater_R04:REMOVE:I.Ch[2].Data SPARE
619 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH4+ | 1756-IRT8I | 4 | REMOVE | 3 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[3].Data | // K2_Preheater_R04:REMOVE:I.Ch[3].Data SPARE
620 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH5+ | 1756-IRT8I | 4 | REMOVE | 4 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[4].Data | // K2_Preheater_R04:REMOVE:I.Ch[4].Data SPARE
621 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH6+ | 1756-IRT8I | 4 | REMOVE | 5 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[5].Data | // K2_Preheater_R04:REMOVE:I.Ch[5].Data SPARE
622 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH7+ | 1756-IRT8I | 4 | REMOVE | 6 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[6].Data | // K2_Preheater_R04:REMOVE:I.Ch[6].Data SPARE
623 | PH2 R4G1M1 | 1771-IXE | 4 | 3 | CH8+ | 1756-IRT8I | 4 | REMOVE | 7 |  |  |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Ch[ | INPUT |  | K2_Preheater_R04:REMOVE:I.Ch[7].Data | // K2_Preheater_R04:REMOVE:I.Ch[7].Data SPARE
624 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 00 | 1756-IA16 | 4 | REMOVE | 00 |  | I:042/0 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.00 | // K2_Preheater_R04:REMOVE:I.Data.00 SPARE
625 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 01 | 1756-IA16 | 4 | REMOVE | 01 |  | I:042/1 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.01 | // K2_Preheater_R04:REMOVE:I.Data.01 SPARE
626 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 02 | 1756-IA16 | 4 | 1 | 02 | PH2RAM1_LS_B | I:042/2 |  | PH 2305 RAM 1 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM1_LS_B_IO | K2_Preheater_R04:1:I.Data.02 | PH2RAM1_LS_B_IO:= K2_Preheater_R04:1:I.Data.02; //PH 2305 RAM 1 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
627 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 03 | 1756-IA16 | 4 | 1 | 03 | PH2RAM2_LS_B | I:042/3 |  | PH 2305 RAM 2 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM2_LS_B_IO | K2_Preheater_R04:1:I.Data.03 | PH2RAM2_LS_B_IO:= K2_Preheater_R04:1:I.Data.03; //PH 2305 RAM 2 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
628 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 04 | 1756-IA16 | 4 | 1 | 04 | PH2RAM3_LS_B | I:042/4 |  | PH 2305 RAM 3 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM3_LS_B_IO | K2_Preheater_R04:1:I.Data.04 | PH2RAM3_LS_B_IO:= K2_Preheater_R04:1:I.Data.04; //PH 2305 RAM 3 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
629 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 05 | 1756-IA16 | 4 | 1 | 05 | PH2RAM4_LS_B | I:042/5 |  | PH 2305 RAM 4 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM4_LS_B_IO | K2_Preheater_R04:1:I.Data.05 | PH2RAM4_LS_B_IO:= K2_Preheater_R04:1:I.Data.05; //PH 2305 RAM 4 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
630 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 06 | 1756-IA16 | 4 | 1 | 06 | PH2RAM5_LS_B | I:042/6 |  | PH 2305 RAM 5 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM5_LS_B_IO | K2_Preheater_R04:1:I.Data.06 | PH2RAM5_LS_B_IO:= K2_Preheater_R04:1:I.Data.06; //PH 2305 RAM 5 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
631 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 07 | 1756-IA16 | 4 | 1 | 07 | PH2RAM6_LS_B | I:042/7 |  | PH 2305 RAM 6 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM6_LS_B_IO | K2_Preheater_R04:1:I.Data.07 | PH2RAM6_LS_B_IO:= K2_Preheater_R04:1:I.Data.07; //PH 2305 RAM 6 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
632 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 10 | 1756-IA16 | 4 | 1 | 08 | PH2RAM7_LS_B | I:042/10 |  | PH 2305 RAM 7 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM7_LS_B_IO | K2_Preheater_R04:1:I.Data.08 | PH2RAM7_LS_B_IO:= K2_Preheater_R04:1:I.Data.08; //PH 2305 RAM 7 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
633 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 11 | 1756-IA16 | 4 | 1 | 09 | PH2RAM8_LS_B | I:042/11 |  | PH 2305 RAM 8 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM8_LS_B_IO | K2_Preheater_R04:1:I.Data.09 | PH2RAM8_LS_B_IO:= K2_Preheater_R04:1:I.Data.09; //PH 2305 RAM 8 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
634 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 12 | 1756-IA16 | 4 | 1 | 10 | PH2RAM9_LS_B | I:042/12 |  | PH 2305 RAM 9 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM9_LS_B_IO | K2_Preheater_R04:1:I.Data.10 | PH2RAM9_LS_B_IO:= K2_Preheater_R04:1:I.Data.10; //PH 2305 RAM 9 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
635 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 13 | 1756-IA16 | 4 | 1 | 11 | PH2RAM10_LS_B | I:042/13 |  | PH 2305 RAM 10 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM10_LS_B_IO | K2_Preheater_R04:1:I.Data.11 | PH2RAM10_LS_B_IO:= K2_Preheater_R04:1:I.Data.11; //PH 2305 RAM 10 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
636 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 14 | 1756-IA16 | 4 | 1 | 12 | PH2RAM11_LS_B | I:042/14 |  | PH 2305 RAM 11 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM11_LS_B_IO | K2_Preheater_R04:1:I.Data.12 | PH2RAM11_LS_B_IO:= K2_Preheater_R04:1:I.Data.12; //PH 2305 RAM 11 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
637 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 15 | 1756-IA16 | 4 | 1 | 13 | PH2RAM12_LS_B | I:042/15 |  | PH 2305 RAM 12 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM12_LS_B_IO | K2_Preheater_R04:1:I.Data.13 | PH2RAM12_LS_B_IO:= K2_Preheater_R04:1:I.Data.13; //PH 2305 RAM 12 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
638 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 16 | 1756-IA16 | 4 | 1 | 14 | PH2RAM13_LS_B | I:042/16 |  | PH 2305 RAM 13 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM13_LS_B_IO | K2_Preheater_R04:1:I.Data.14 | PH2RAM13_LS_B_IO:= K2_Preheater_R04:1:I.Data.14; //PH 2305 RAM 13 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
639 | PH2 R4G2M0 | 1771-IAD | 4 | 4 | 17 | 1756-IA16 | 4 | 1 | 15 | PH2RAM14_LS_B | I:042/17 |  | PH 2305 RAM 14 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM14_LS_B_IO | K2_Preheater_R04:1:I.Data.15 | PH2RAM14_LS_B_IO:= K2_Preheater_R04:1:I.Data.15; //PH 2305 RAM 14 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
640 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 00 | 1756-OA16 | 4 | 5 | 00 | KN2_CAN1_SV | O:042/0 |  | AIR CANNONS CANNON 1 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN1_SV_IO | K2_Preheater_R04:5:O.Data.00 | K2_Preheater_R04:5:O.Data.00:=KN2_CAN1_SV_IO; //AIR CANNONS CANNON 1 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
641 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 01 | 1756-OA16 | 4 | 5 | 01 | KN2_CAN2_SV | O:042/1 |  | AIR CANNONS CANNON 2 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN2_SV_IO | K2_Preheater_R04:5:O.Data.01 | K2_Preheater_R04:5:O.Data.01:=KN2_CAN2_SV_IO; //AIR CANNONS CANNON 2 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
642 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 02 | 1756-OA16 | 4 | 5 | 02 | KN2_CAN3_SV | O:042/2 |  | AIR CANNONS CANNON 3 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN3_SV_IO | K2_Preheater_R04:5:O.Data.02 | K2_Preheater_R04:5:O.Data.02:=KN2_CAN3_SV_IO; //AIR CANNONS CANNON 3 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
643 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 03 | 1756-OA16 | 4 | 5 | 03 | KN2_CAN4_SV | O:042/3 |  | AIR CANNONS CANNON 4 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN4_SV_IO | K2_Preheater_R04:5:O.Data.03 | K2_Preheater_R04:5:O.Data.03:=KN2_CAN4_SV_IO; //AIR CANNONS CANNON 4 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
644 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 04 | 1756-OA16 | 4 | 5 | 04 | KN2_CAN5_SV | O:042/4 |  | AIR CANNONS CANNON 5 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN5_SV_IO | K2_Preheater_R04:5:O.Data.04 | K2_Preheater_R04:5:O.Data.04:=KN2_CAN5_SV_IO; //AIR CANNONS CANNON 5 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
645 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 05 | 1756-OA16 | 4 | 5 | 05 | KN2_CAN6_SV | O:042/5 |  | AIR CANNONS CANNON 6 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN6_SV_IO | K2_Preheater_R04:5:O.Data.05 | K2_Preheater_R04:5:O.Data.05:=KN2_CAN6_SV_IO; //AIR CANNONS CANNON 6 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
646 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 06 | 1756-OA16 | 4 | 5 | 06 | KN2_CAN7_SV | O:042/6 |  | AIR CANNONS CANNON 7 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN7_SV_IO | K2_Preheater_R04:5:O.Data.06 | K2_Preheater_R04:5:O.Data.06:=KN2_CAN7_SV_IO; //AIR CANNONS CANNON 7 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
647 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 07 | 1756-OA16 | 4 | 5 | 07 | KN2_CAN8_SV | O:042/7 |  | AIR CANNONS CANNON 8 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN8_SV_IO | K2_Preheater_R04:5:O.Data.07 | K2_Preheater_R04:5:O.Data.07:=KN2_CAN8_SV_IO; //AIR CANNONS CANNON 8 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
648 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 10 | 1756-OA16 | 4 | 5 | 08 | KN2_CAN9_SV | O:042/10 |  | AIR CANNONS CANNON 9 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN9_SV_IO | K2_Preheater_R04:5:O.Data.08 | K2_Preheater_R04:5:O.Data.08:=KN2_CAN9_SV_IO; //AIR CANNONS CANNON 9 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
649 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 11 | 1756-OA16 | 4 | 5 | 09 | KN2_CAN10_SV | O:042/11 |  | AIR CANNONS CANNON 10 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN10_SV_IO | K2_Preheater_R04:5:O.Data.09 | K2_Preheater_R04:5:O.Data.09:=KN2_CAN10_SV_IO; //AIR CANNONS CANNON 10 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
650 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 12 | 1756-OA16 | 4 | 5 | 10 | KN2_CAN11_SV | O:042/12 |  | AIR CANNONS CANNON 11 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN11_SV_IO | K2_Preheater_R04:5:O.Data.10 | K2_Preheater_R04:5:O.Data.10:=KN2_CAN11_SV_IO; //AIR CANNONS CANNON 11 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
651 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 13 | 1756-OA16 | 4 | 5 | 11 | KN2_CAN12_SV | O:042/13 |  | AIR CANNONS CANNON 12 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN12_SV_IO | K2_Preheater_R04:5:O.Data.11 | K2_Preheater_R04:5:O.Data.11:=KN2_CAN12_SV_IO; //AIR CANNONS CANNON 12 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
652 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 14 | 1756-OA16 | 4 | 5 | 12 | KN2_CAN13_SV | O:042/14 |  | AIR CANNONS CANNON 13 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN13_SV_IO | K2_Preheater_R04:5:O.Data.12 | K2_Preheater_R04:5:O.Data.12:=KN2_CAN13_SV_IO; //AIR CANNONS CANNON 13 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
653 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 15 | 1756-OA16 | 4 | 5 | 13 | KN2_CAN14_SV | O:042/15 |  | AIR CANNONS CANNON 14 KILN 2 SOLENIOD OUTPUT | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | KN2_CAN14_SV_IO | K2_Preheater_R04:5:O.Data.13 | K2_Preheater_R04:5:O.Data.13:=KN2_CAN14_SV_IO; //AIR CANNONS CANNON 14 KILN 2 SOLENIOD OUTPUT |  | NA | NA | NA
654 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 16 | 1756-OA16 | 4 | 5 | 14 | SPARE | O:042/16 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | SPARE_IO | K2_Preheater_R04:5:O.Data.14 | K2_Preheater_R04:5:O.Data.14:=SPARE_IO; //SPARE |  | _SPARE
655 | PH2 R4G2M1 | 1771-OAD | 4 | 5 | 17 | 1756-OA16 | 4 | 5 | 15 | SPARE | O:042/17 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | SPARE_IO | K2_Preheater_R04:5:O.Data.15 | K2_Preheater_R04:5:O.Data.15:=SPARE_IO; //SPARE |  | _SPARE
656 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 00 | 1756-IA16 | 4 | REMOVE | 00 |  | I:043/0 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.00 | // K2_Preheater_R04:REMOVE:I.Data.00 SPARE
657 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 01 | 1756-IA16 | 4 | REMOVE | 01 |  | I:043/1 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.01 | // K2_Preheater_R04:REMOVE:I.Data.01 SPARE
658 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 02 | 1756-IA16 | 4 | REMOVE | 02 |  | I:043/2 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.02 | // K2_Preheater_R04:REMOVE:I.Data.02 SPARE
659 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 03 | 1756-IA16 | 4 | REMOVE | 03 |  | I:043/3 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.03 | // K2_Preheater_R04:REMOVE:I.Data.03 SPARE
660 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 04 | 1756-IA16 | 4 | 4 | 04 |  | I:043/4 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.04 | // K2_Preheater_R04:4:I.Data.04 SPARE
661 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 05 | 1756-IA16 | 4 | 4 | 05 |  | I:043/5 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.05 | // K2_Preheater_R04:4:I.Data.05 SPARE
662 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 06 | 1756-IA16 | 4 | 4 | 06 |  | I:043/6 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.06 | // K2_Preheater_R04:4:I.Data.06 SPARE
663 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 07 | 1756-IA16 | 4 | 4 | 07 |  | I:043/7 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.07 | // K2_Preheater_R04:4:I.Data.07 SPARE
664 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 10 | 1756-IA16 | 4 | 4 | 08 |  | I:043/10 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.08 | // K2_Preheater_R04:4:I.Data.08 SPARE
665 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 11 | 1756-IA16 | 4 | 4 | 09 |  | I:043/11 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.09 | // K2_Preheater_R04:4:I.Data.09 SPARE
666 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 12 | 1756-IA16 | 4 | 4 | 10 |  | I:043/12 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.10 | // K2_Preheater_R04:4:I.Data.10 SPARE
667 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 13 | 1756-IA16 | 4 | 4 | 11 |  | I:043/13 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.11 | // K2_Preheater_R04:4:I.Data.11 SPARE
668 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 14 | 1756-IA16 | 4 | 4 | 12 |  | I:043/14 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.12 | // K2_Preheater_R04:4:I.Data.12 SPARE
669 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 15 | 1756-IA16 | 4 | 4 | 13 |  | I:043/15 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.13 | // K2_Preheater_R04:4:I.Data.13 SPARE
670 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 16 | 1756-IA16 | 4 | 4 | 14 |  | I:043/16 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.14 | // K2_Preheater_R04:4:I.Data.14 SPARE
671 | PH2 R4G3M0 | 1771-IAD | 4 | 6 | 17 | 1756-IA16 | 4 | 4 | 15 |  | I:043/17 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:4:I.Data.15 | // K2_Preheater_R04:4:I.Data.15 SPARE
672 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 00 | 1756-OA16 | 4 | REMOVE | 0 |  | O:043/0 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.0 | // K2_Preheater_R04:REMOVE:O.Data.0 SPARE
673 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 01 | 1756-OA16 | 4 | REMOVE | 1 |  | O:043/1 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.1 | // K2_Preheater_R04:REMOVE:O.Data.1 SPARE
674 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 02 | 1756-OA16 | 4 | REMOVE | 2 |  | O:043/2 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.2 | // K2_Preheater_R04:REMOVE:O.Data.2 SPARE
675 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 03 | 1756-OA16 | 4 | REMOVE | 3 |  | O:043/3 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.3 | // K2_Preheater_R04:REMOVE:O.Data.3 SPARE
676 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 04 | 1756-OA16 | 4 | REMOVE | 4 |  | O:043/4 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.4 | // K2_Preheater_R04:REMOVE:O.Data.4 SPARE
677 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 05 | 1756-OA16 | 4 | REMOVE | 5 |  | O:043/5 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.5 | // K2_Preheater_R04:REMOVE:O.Data.5 SPARE
678 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 06 | 1756-OA16 | 4 | REMOVE | 6 |  | O:043/6 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.6 | // K2_Preheater_R04:REMOVE:O.Data.6 SPARE
679 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 07 | 1756-OA16 | 4 | REMOVE | 7 |  | O:043/7 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.7 | // K2_Preheater_R04:REMOVE:O.Data.7 SPARE
680 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 10 | 1756-OA16 | 4 | REMOVE | 8 |  | O:043/10 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.8 | // K2_Preheater_R04:REMOVE:O.Data.8 SPARE
681 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 11 | 1756-OA16 | 4 | 7 | 9 | K1AIRCANNON_SV | O:043/11 |  | SOLENOID KILN 1 TRANSFER CHUTE AIR CANNON |  | Notes: From 4_PH2_NEW | K2_Preheater_R04 | O.Data | OUTPUT | K1AIRCANNON_SV_IO | K2_Preheater_R04:7:O.Data.9 | K2_Preheater_R04:7:O.Data.9:=K1AIRCANNON_SV_IO; //SOLENOID KILN 1 TRANSFER CHUTE AIR CANNON |  | _K1AIRCANNON_SV | NA | NA
682 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 12 | 1756-OA16 | 4 | 7 | 10 | K2AIRCANNON_SV | O:043/12 |  | SOLENOID KILN 2 TRANSFER CHUTE AIR CANNON |  | Notes: From 4_PH2_NEW | K2_Preheater_R04 | O.Data | OUTPUT | K2AIRCANNON_SV_IO | K2_Preheater_R04:7:O.Data.10 | K2_Preheater_R04:7:O.Data.10:=K2AIRCANNON_SV_IO; //SOLENOID KILN 2 TRANSFER CHUTE AIR CANNON |  | _K2AIRCANNON_SV | NA | NA
683 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 13 | 1756-OA16 | 4 | 7 | 11 | KD308K1K2_YAY | O:043/13 |  | KD 1-308 & 2-308 RUN STRATUP HORN KILN1 & 2 |  | Notes: From 4_PH2_NEW | K2_Preheater_R04 | O.Data | OUTPUT | KD308K1K2_YAY_IO | K2_Preheater_R04:7:O.Data.11 | K2_Preheater_R04:7:O.Data.11:=KD308K1K2_YAY_IO; //KD 1-308 & 2-308 RUN STRATUP HORN KILN1 & 2 |  | _KD308K1K2_YAY | P_Dout | PCmd_On |  | Kiln1_Main_TaskB | Task_B | _KD308K1K2_YAY
684 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 14 | 1756-OA16 | 4 | REMOVE | 12 |  | O:043/14 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.12 | // K2_Preheater_R04:REMOVE:O.Data.12 SPARE
685 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 15 | 1756-OA16 | 4 | REMOVE | 13 |  | O:043/15 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.13 | // K2_Preheater_R04:REMOVE:O.Data.13 SPARE
686 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 16 | 1756-OA16 | 4 | REMOVE | 14 |  | O:043/16 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.14 | // K2_Preheater_R04:REMOVE:O.Data.14 SPARE
687 | PH 2 R4G3M1 | 1771-OAD | 4 | 7 | 17 | 1756-OA16 | 4 | REMOVE | 15 |  | O:043/17 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.15 | // K2_Preheater_R04:REMOVE:O.Data.15 SPARE
688 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 00 | 1756-IA16 | 4 | 2 | 00 | PH2RAM15_LS_B | I:044/0 |  | PH 2305 RAM 15 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM15_LS_B_IO | K2_Preheater_R04:2:I.Data.00 | PH2RAM15_LS_B_IO:= K2_Preheater_R04:2:I.Data.00; //PH 2305 RAM 15 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
689 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 01 | 1756-IA16 | 4 | 2 | 01 | PH2RAM16_LS_B | I:044/1 |  | PH 2305 RAM 16 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM16_LS_B_IO | K2_Preheater_R04:2:I.Data.01 | PH2RAM16_LS_B_IO:= K2_Preheater_R04:2:I.Data.01; //PH 2305 RAM 16 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
690 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 02 | 1756-IA16 | 4 | 2 | 02 | PH2RAM17_LS_B | I:044/2 |  | PH 2305 RAM 17 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM17_LS_B_IO | K2_Preheater_R04:2:I.Data.02 | PH2RAM17_LS_B_IO:= K2_Preheater_R04:2:I.Data.02; //PH 2305 RAM 17 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
691 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 03 | 1756-IA16 | 4 | 2 | 03 | PH2RAM18_LS_B | I:044/3 |  | PH 2305 RAM 18 LIMIT SWITCH KILN 2 PH RETRACTED |  | Notes: NEW | K2_Preheater_R04 | I.Data | INPUT | PH2RAM18_LS_B_IO | K2_Preheater_R04:2:I.Data.03 | PH2RAM18_LS_B_IO:= K2_Preheater_R04:2:I.Data.03; //PH 2305 RAM 18 LIMIT SWITCH KILN 2 PH RETRACTED |  | NA | NA | NA
692 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 04 | 1756-IA16 | 4 | 2 | 04 |  | I:044/4 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:2:I.Data.04 | // K2_Preheater_R04:2:I.Data.04 SPARE
693 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 05 | 1756-IA16 | 4 | REMOVE | 05 |  | I:044/5 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.05 | // K2_Preheater_R04:REMOVE:I.Data.05 SPARE
694 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 06 | 1756-IA16 | 4 | REMOVE | 06 |  | I:044/6 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.06 | // K2_Preheater_R04:REMOVE:I.Data.06 SPARE
695 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 07 | 1756-IA16 | 4 | 3 | 07 | K202_PV | I:044/7 |  | KILN 2 O2 PURGING 1=PURGING |  | Notes: From 4_PH2_NEW | K2_Preheater_R04 | I.Data | INPUT | K202_PV_IO | K2_Preheater_R04:3:I.Data.07 | K202_PV_IO:= K2_Preheater_R04:3:I.Data.07; //KILN 2 O2 PURGING 1=PURGING |  | _K202_PV | P_DIn | Sts_PV
696 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 10 | 1756-IA16 | 4 | 3 | 08 | KL1O2_FS | I:044/10 | TK_02 | FLOW SWITCH KILN 1 O2 PROBE WATER |  | Notes: USED IN HMI ONLY | K2_Preheater_R04 | I.Data | INPUT | KL1O2_FS_IO | K2_Preheater_R04:3:I.Data.08 | KL1O2_FS_IO:= K2_Preheater_R04:3:I.Data.08; //FLOW SWITCH KILN 1 O2 PROBE WATER |  | _KL1O2_FS | P_DIn | Sts_PV
697 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 11 | 1756-IA16 | 4 | 3 | 09 | KL2OS_FS | I:044/11 | TK_02 | FLOW SWITCH KILN 2 O2 PROBE WATER |  | Notes: USED IN HMI ONLY | K2_Preheater_R04 | I.Data | INPUT | KL2OS_FS_IO | K2_Preheater_R04:3:I.Data.09 | KL2OS_FS_IO:= K2_Preheater_R04:3:I.Data.09; //FLOW SWITCH KILN 2 O2 PROBE WATER |  | _KL2OS_FS | P_DIn | Sts_PV
698 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 12 | 1756-IA16 | 4 | REMOVE | 10 |  | I:044/12 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.10 | // K2_Preheater_R04:REMOVE:I.Data.10 SPARE
699 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 13 | 1756-IA16 | 4 | 3 | 10 | SB2304_LIL | I:044/13 |  | SB 2304 LOW LEVEL KILN 2 STONE BIN | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | SB2304_LIL_IO | K2_Preheater_R04:3:I.Data.10 | SB2304_LIL_IO:= K2_Preheater_R04:3:I.Data.10; //SB 2304 LOW LEVEL KILN 2 STONE BIN |  | _SB2304_LIL | P_DIn | Sts_PV
700 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 14 | 1756-IA16 | 4 | 3 | 11 | SB2304_LIH | I:044/14 |  | SB 2304 HIGH LEVEL KILN 2 STONE BIN | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | SB2304_LIH_IO | K2_Preheater_R04:3:I.Data.11 | SB2304_LIH_IO:= K2_Preheater_R04:3:I.Data.11; //SB 2304 HIGH LEVEL KILN 2 STONE BIN |  | _SB2304_LIH | P_DIn | Sts_PV |  | Kiln2_Main_TaskB | Task_B | _SB2304_LIH
701 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 15 | 1756-IA16 | 4 | REMOVE | 13 |  | I:044/15 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.13 | // K2_Preheater_R04:REMOVE:I.Data.13 SPARE
702 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 16 | 1756-IA16 | 4 | REMOVE | 14 |  | I:044/16 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.14 | // K2_Preheater_R04:REMOVE:I.Data.14 SPARE
703 | PH2 R4G4M0 | 1771-IAD | 4 | 8 | 17 | 1756-IA16 | 4 | REMOVE | 15 |  | I:044/17 |  | SPARE | [10 empty] | K2_Preheater_R04 | I.Data | INPUT |  | K2_Preheater_R04:REMOVE:I.Data.15 | // K2_Preheater_R04:REMOVE:I.Data.15 SPARE | bar: Notes to EU
704 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 00 | 1756-OA16 | 4 | REMOVE | 0 |  | O:044/0 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.0 | // K2_Preheater_R04:REMOVE:O.Data.0 SPARE (NO SPARE, SI TIENE DESCRIPCION)
705 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 01 | 1756-OA16 | 4 | REMOVE | 1 |  | O:044/1 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.1 | // K2_Preheater_R04:REMOVE:O.Data.1 SPARE (NO SPARE, SI TIENE DESCRIPCION)
706 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 02 | 1756-OA16 | 4 | REMOVE | 2 |  | O:044/2 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.2 | // K2_Preheater_R04:REMOVE:O.Data.2 SPARE (NO SPARE, SI TIENE DESCRIPCION)
707 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 03 | 1756-OA16 | 4 | REMOVE | 3 |  | O:044/3 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.3 | // K2_Preheater_R04:REMOVE:O.Data.3 SPARE (NO SPARE, SI TIENE DESCRIPCION)
708 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 04 | 1756-OA16 | 4 | REMOVE | 4 |  | O:044/4 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.4 | // K2_Preheater_R04:REMOVE:O.Data.4 SPARE (NO SPARE, SI TIENE DESCRIPCION)
709 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 05 | 1756-OA16 | 4 | REMOVE | 5 |  | O:044/5 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.5 | // K2_Preheater_R04:REMOVE:O.Data.5 SPARE (NO SPARE, SI TIENE DESCRIPCION)
710 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 06 | 1756-OA16 | 4 | REMOVE | 6 |  | O:044/6 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.6 | // K2_Preheater_R04:REMOVE:O.Data.6 SPARE (NO SPARE, SI TIENE DESCRIPCION)
711 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 07 | 1756-OA16 | 4 | REMOVE | 7 |  | O:044/7 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.7 | // K2_Preheater_R04:REMOVE:O.Data.7 SPARE (NO SPARE, SI TIENE DESCRIPCION)
712 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 10 | 1756-OA16 | 4 | REMOVE | 8 |  | O:044/10 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.8 | // K2_Preheater_R04:REMOVE:O.Data.8 SPARE (NO SPARE, SI TIENE DESCRIPCION)
713 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 11 | 1756-OA16 | 4 | REMOVE | 9 |  | O:044/11 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.9 | // K2_Preheater_R04:REMOVE:O.Data.9 SPARE (NO SPARE, SI TIENE DESCRIPCION)
714 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 12 | 1756-OA16 | 4 | REMOVE | 10 |  | O:044/12 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.10 | // K2_Preheater_R04:REMOVE:O.Data.10 SPARE (NO SPARE, SI TIENE DESCRIPCION)
715 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 13 | 1756-OA16 | 4 | REMOVE | 11 |  | O:044/13 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.11 | // K2_Preheater_R04:REMOVE:O.Data.11 SPARE (NO SPARE, SI TIENE DESCRIPCION)
716 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 14 | 1756-OA16 | 4 | REMOVE | 12 |  | O:044/14 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.12 | // K2_Preheater_R04:REMOVE:O.Data.12 SPARE (NO SPARE, SI TIENE DESCRIPCION)
717 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 15 | 1756-OA16 | 4 | REMOVE | 13 |  | O:044/15 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.13 | // K2_Preheater_R04:REMOVE:O.Data.13 SPARE (NO SPARE, SI TIENE DESCRIPCION)
718 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 16 | 1756-OA16 | 4 | REMOVE | 14 |  | O:044/16 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.14 | // K2_Preheater_R04:REMOVE:O.Data.14 SPARE (NO SPARE, SI TIENE DESCRIPCION)
719 | PH 2 R4G4M1 | 1771-OAD | 4 | 9 | 17 | 1756-OA16 | 4 | REMOVE | 15 |  | O:044/17 |  | SPARE (NO SPARE, SI TIENE DESCRIPCION) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.15 | // K2_Preheater_R04:REMOVE:O.Data.15 SPARE (NO SPARE, SI TIENE DESCRIPCION)
720 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 00 | 1756-IA16 | 4 | 0 | 00 | PH2RAM1_LS_A | I:045/0 |  | PH 2305 RAM 1 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM1_LS_A_IO | K2_Preheater_R04:0:I.Data.00 | PH2RAM1_LS_A_IO:= K2_Preheater_R04:0:I.Data.00; //PH 2305 RAM 1 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
721 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 01 | 1756-IA16 | 4 | 0 | 01 | PH2RAM2_LS_A | I:045/1 |  | PH 2305 RAM 2 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM2_LS_A_IO | K2_Preheater_R04:0:I.Data.01 | PH2RAM2_LS_A_IO:= K2_Preheater_R04:0:I.Data.01; //PH 2305 RAM 2 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
722 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 02 | 1756-IA16 | 4 | 0 | 02 | PH2RAM3_LS_A | I:045/2 |  | PH 2305 RAM 3 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM3_LS_A_IO | K2_Preheater_R04:0:I.Data.02 | PH2RAM3_LS_A_IO:= K2_Preheater_R04:0:I.Data.02; //PH 2305 RAM 3 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
723 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 03 | 1756-IA16 | 4 | 0 | 03 | PH2RAM4_LS_A | I:045/3 |  | PH 2305 RAM 4 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM4_LS_A_IO | K2_Preheater_R04:0:I.Data.03 | PH2RAM4_LS_A_IO:= K2_Preheater_R04:0:I.Data.03; //PH 2305 RAM 4 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
724 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 04 | 1756-IA16 | 4 | 0 | 04 | PH2RAM5_LS_A | I:045/4 |  | PH 2305 RAM 5 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM5_LS_A_IO | K2_Preheater_R04:0:I.Data.04 | PH2RAM5_LS_A_IO:= K2_Preheater_R04:0:I.Data.04; //PH 2305 RAM 5 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
725 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 05 | 1756-IA16 | 4 | 0 | 05 | PH2RAM6_LS_A | I:045/5 |  | PH 2305 RAM 6 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM6_LS_A_IO | K2_Preheater_R04:0:I.Data.05 | PH2RAM6_LS_A_IO:= K2_Preheater_R04:0:I.Data.05; //PH 2305 RAM 6 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
726 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 06 | 1756-IA16 | 4 | 0 | 06 | PH2RAM7_LS_A | I:045/6 |  | PH 2305 RAM 7 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM7_LS_A_IO | K2_Preheater_R04:0:I.Data.06 | PH2RAM7_LS_A_IO:= K2_Preheater_R04:0:I.Data.06; //PH 2305 RAM 7 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
727 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 07 | 1756-IA16 | 4 | 0 | 07 | PH2RAM8_LS_A | I:045/7 |  | PH 2305 RAM 8 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM8_LS_A_IO | K2_Preheater_R04:0:I.Data.07 | PH2RAM8_LS_A_IO:= K2_Preheater_R04:0:I.Data.07; //PH 2305 RAM 8 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
728 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 10 | 1756-IA16 | 4 | 0 | 08 | PH2RAM9_LS_A | I:045/10 |  | PH 2305 RAM 9 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM9_LS_A_IO | K2_Preheater_R04:0:I.Data.08 | PH2RAM9_LS_A_IO:= K2_Preheater_R04:0:I.Data.08; //PH 2305 RAM 9 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
729 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 11 | 1756-IA16 | 4 | 0 | 09 | PH2RAM10_LS_A | I:045/11 |  | PH 2305 RAM 10 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM10_LS_A_IO | K2_Preheater_R04:0:I.Data.09 | PH2RAM10_LS_A_IO:= K2_Preheater_R04:0:I.Data.09; //PH 2305 RAM 10 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
730 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 12 | 1756-IA16 | 4 | 0 | 10 | PH2RAM11_LS_A | I:045/12 |  | PH 2305 RAM 11 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM11_LS_A_IO | K2_Preheater_R04:0:I.Data.10 | PH2RAM11_LS_A_IO:= K2_Preheater_R04:0:I.Data.10; //PH 2305 RAM 11 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
731 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 13 | 1756-IA16 | 4 | 0 | 11 | PH2RAM12_LS_A | I:045/13 |  | PH 2305 RAM 12 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM12_LS_A_IO | K2_Preheater_R04:0:I.Data.11 | PH2RAM12_LS_A_IO:= K2_Preheater_R04:0:I.Data.11; //PH 2305 RAM 12 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
732 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 14 | 1756-IA16 | 4 | 0 | 12 | PH2RAM13_LS_A | I:045/14 |  | PH 2305 RAM 13 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM13_LS_A_IO | K2_Preheater_R04:0:I.Data.12 | PH2RAM13_LS_A_IO:= K2_Preheater_R04:0:I.Data.12; //PH 2305 RAM 13 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
733 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 15 | 1756-IA16 | 4 | 0 | 13 | PH2RAM14_LS_A | I:045/15 |  | PH 2305 RAM 14 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM14_LS_A_IO | K2_Preheater_R04:0:I.Data.13 | PH2RAM14_LS_A_IO:= K2_Preheater_R04:0:I.Data.13; //PH 2305 RAM 14 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
734 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 16 | 1756-IA16 | 4 | 0 | 14 | PH2RAM15_LS_A | I:045/16 |  | PH 2305 RAM 15 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM15_LS_A_IO | K2_Preheater_R04:0:I.Data.14 | PH2RAM15_LS_A_IO:= K2_Preheater_R04:0:I.Data.14; //PH 2305 RAM 15 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
735 | PH 2 R4G5M0 | 1771-IAD | 4 | 10 | 17 | 1756-IA16 | 4 | 0 | 15 | PH2RAM16_LS_A | I:045/17 |  | PH 2305 RAM 16 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM16_LS_A_IO | K2_Preheater_R04:0:I.Data.15 | PH2RAM16_LS_A_IO:= K2_Preheater_R04:0:I.Data.15; //PH 2305 RAM 16 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
736 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 00 | 1756-OA16 | 4 | REMOVE | 0 |  | O:045/0 |  | PH 2305 RAM 1 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.0 | // K2_Preheater_R04:REMOVE:O.Data.0 PH 2305 RAM 1 MIMIC LIGHT KILN 2 PH
737 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 01 | 1756-OA16 | 4 | REMOVE | 1 |  | O:045/1 |  | PH 2305 RAM 2 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.1 | // K2_Preheater_R04:REMOVE:O.Data.1 PH 2305 RAM 2 MIMIC LIGHT KILN 2 PH | [9 empty] | Sts_AtSpeed
738 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 02 | 1756-OA16 | 4 | REMOVE | 2 |  | O:045/2 |  | PH 2305 RAM 3 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.2 | // K2_Preheater_R04:REMOVE:O.Data.2 PH 2305 RAM 3 MIMIC LIGHT KILN 2 PH | [9 empty] | Sts_Running
739 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 03 | 1756-OA16 | 4 | REMOVE | 3 |  | O:045/3 |  | PH 2305 RAM 4 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.3 | // K2_Preheater_R04:REMOVE:O.Data.3 PH 2305 RAM 4 MIMIC LIGHT KILN 2 PH | [9 empty] | Sts_DriveFault
740 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 04 | 1756-OA16 | 4 | REMOVE | 4 |  | O:045/4 |  | PH 2305 RAM 5 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.4 | // K2_Preheater_R04:REMOVE:O.Data.4 PH 2305 RAM 5 MIMIC LIGHT KILN 2 PH | [9 empty] | Out_SpeedRef
741 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 05 | 1756-OA16 | 4 | REMOVE | 5 |  | O:045/5 |  | PH 2305 RAM 6 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.5 | // K2_Preheater_R04:REMOVE:O.Data.5 PH 2305 RAM 6 MIMIC LIGHT KILN 2 PH
742 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 06 | 1756-OA16 | 4 | REMOVE | 6 |  | O:045/6 |  | PH 2305 RAM 7 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.6 | // K2_Preheater_R04:REMOVE:O.Data.6 PH 2305 RAM 7 MIMIC LIGHT KILN 2 PH
743 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 07 | 1756-OA16 | 4 | REMOVE | 7 |  | O:045/7 |  | PH 2305 RAM 8 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.7 | // K2_Preheater_R04:REMOVE:O.Data.7 PH 2305 RAM 8 MIMIC LIGHT KILN 2 PH
744 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 10 | 1756-OA16 | 4 | REMOVE | 8 |  | O:045/10 |  | PH 2305 RAM 9 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.8 | // K2_Preheater_R04:REMOVE:O.Data.8 PH 2305 RAM 9 MIMIC LIGHT KILN 2 PH
745 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 11 | 1756-OA16 | 4 | REMOVE | 9 |  | O:045/11 |  | PH 2305 RAM 10 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.9 | // K2_Preheater_R04:REMOVE:O.Data.9 PH 2305 RAM 10 MIMIC LIGHT KILN 2 PH
746 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 12 | 1756-OA16 | 4 | REMOVE | 10 |  | O:045/12 |  | PH 2305 RAM 11 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.10 | // K2_Preheater_R04:REMOVE:O.Data.10 PH 2305 RAM 11 MIMIC LIGHT KILN 2 PH
747 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 13 | 1756-OA16 | 4 | REMOVE | 11 |  | O:045/13 |  | PH 2305 RAM 12 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.11 | // K2_Preheater_R04:REMOVE:O.Data.11 PH 2305 RAM 12 MIMIC LIGHT KILN 2 PH
748 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 14 | 1756-OA16 | 4 | REMOVE | 12 |  | O:045/14 |  | PH 2305 RAM 13 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.12 | // K2_Preheater_R04:REMOVE:O.Data.12 PH 2305 RAM 13 MIMIC LIGHT KILN 2 PH
749 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 15 | 1756-OA16 | 4 | REMOVE | 13 |  | O:045/15 |  | PH 2305 RAM 14 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.13 | // K2_Preheater_R04:REMOVE:O.Data.13 PH 2305 RAM 14 MIMIC LIGHT KILN 2 PH
750 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 16 | 1756-OA16 | 4 | REMOVE | 14 |  | O:045/16 |  | PH 2305 RAM 15 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.14 | // K2_Preheater_R04:REMOVE:O.Data.14 PH 2305 RAM 15 MIMIC LIGHT KILN 2 PH
751 | PH 2 R4G5M1 | 1771-OAD | 4 | 11 | 17 | 1756-OA16 | 4 | REMOVE | 15 |  | O:045/17 |  | PH 2305 RAM 16 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.15 | // K2_Preheater_R04:REMOVE:O.Data.15 PH 2305 RAM 16 MIMIC LIGHT KILN 2 PH
752 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 00 | 1756-IA16 | 4 | 1 | 0 | PH2RAM17_LS_A | I:046/0 |  | PH 2305 RAM 17 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM17_LS_A_IO | K2_Preheater_R04:1:I.Data.0 | PH2RAM17_LS_A_IO:= K2_Preheater_R04:1:I.Data.0; //PH 2305 RAM 17 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
753 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 01 | 1756-IA16 | 4 | 1 | 1 | PH2RAM18_LS_A | I:046/1 |  | PH 2305 RAM 18 LIMIT SWITCH KILN 2 PH INSERTED | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM18_LS_A_IO | K2_Preheater_R04:1:I.Data.1 | PH2RAM18_LS_A_IO:= K2_Preheater_R04:1:I.Data.1; //PH 2305 RAM 18 LIMIT SWITCH KILN 2 PH INSERTED |  | NA | NA | NA
754 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 02 | 1756-IA16 | 4 | 2 | 5 | PH2RAM1_SS | I:046/2 |  | PH 2305 RAM 1 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM1_SS_IO | K2_Preheater_R04:2:I.Data.5 | PH2RAM1_SS_IO:= K2_Preheater_R04:2:I.Data.5; //PH 2305 RAM 1 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
755 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 03 | 1756-IA16 | 4 | 2 | 6 | PH2RAM2_SS | I:046/3 |  | PH 2305 RAM 2 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM2_SS_IO | K2_Preheater_R04:2:I.Data.6 | PH2RAM2_SS_IO:= K2_Preheater_R04:2:I.Data.6; //PH 2305 RAM 2 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
756 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 04 | 1756-IA16 | 4 | 2 | 7 | PH2RAM3_SS | I:046/4 |  | PH 2305 RAM 3 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM3_SS_IO | K2_Preheater_R04:2:I.Data.7 | PH2RAM3_SS_IO:= K2_Preheater_R04:2:I.Data.7; //PH 2305 RAM 3 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
757 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 05 | 1756-IA16 | 4 | 2 | 8 | PH2RAM4_SS | I:046/5 |  | PH 2305 RAM 4 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM4_SS_IO | K2_Preheater_R04:2:I.Data.8 | PH2RAM4_SS_IO:= K2_Preheater_R04:2:I.Data.8; //PH 2305 RAM 4 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
758 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 06 | 1756-IA16 | 4 | 2 | 9 | PH2RAM5_SS | I:046/6 |  | PH 2305 RAM 5 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM5_SS_IO | K2_Preheater_R04:2:I.Data.9 | PH2RAM5_SS_IO:= K2_Preheater_R04:2:I.Data.9; //PH 2305 RAM 5 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
759 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 07 | 1756-IA16 | 4 | 2 | 10 | PH2RAM6_SS | I:046/7 |  | PH 2305 RAM 6 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM6_SS_IO | K2_Preheater_R04:2:I.Data.10 | PH2RAM6_SS_IO:= K2_Preheater_R04:2:I.Data.10; //PH 2305 RAM 6 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
760 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 10 | 1756-IA16 | 4 | 2 | 11 | PH2RAM7_SS | I:046/10 |  | PH 2305 RAM 7 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM7_SS_IO | K2_Preheater_R04:2:I.Data.11 | PH2RAM7_SS_IO:= K2_Preheater_R04:2:I.Data.11; //PH 2305 RAM 7 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
761 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 11 | 1756-IA16 | 4 | 2 | 12 | PH2RAM8_SS | I:046/11 |  | PH 2305 RAM 8 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM8_SS_IO | K2_Preheater_R04:2:I.Data.12 | PH2RAM8_SS_IO:= K2_Preheater_R04:2:I.Data.12; //PH 2305 RAM 8 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
762 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 12 | 1756-IA16 | 4 | 2 | 13 | PH2RAM9_SS | I:046/12 |  | PH 2305 RAM 9 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM9_SS_IO | K2_Preheater_R04:2:I.Data.13 | PH2RAM9_SS_IO:= K2_Preheater_R04:2:I.Data.13; //PH 2305 RAM 9 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
763 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 13 | 1756-IA16 | 4 | 2 | 14 | PH2RAM10_SS | I:046/13 |  | PH 2305 RAM 10 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM10_SS_IO | K2_Preheater_R04:2:I.Data.14 | PH2RAM10_SS_IO:= K2_Preheater_R04:2:I.Data.14; //PH 2305 RAM 10 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
764 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 14 | 1756-IA16 | 4 | 2 | 15 | PH2RAM11_SS | I:046/14 |  | PH 2305 RAM 11 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM11_SS_IO | K2_Preheater_R04:2:I.Data.15 | PH2RAM11_SS_IO:= K2_Preheater_R04:2:I.Data.15; //PH 2305 RAM 11 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
765 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 15 | 1756-IA16 | 4 | 3 | 0 | PH2RAM12_SS | I:046/15 |  | PH 2305 RAM 12 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM12_SS_IO | K2_Preheater_R04:3:I.Data.0 | PH2RAM12_SS_IO:= K2_Preheater_R04:3:I.Data.0; //PH 2305 RAM 12 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
766 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 16 | 1756-IA16 | 4 | 3 | 1 | PH2RAM13_SS | I:046/16 |  | PH 2305 RAM 13 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM13_SS_IO | K2_Preheater_R04:3:I.Data.1 | PH2RAM13_SS_IO:= K2_Preheater_R04:3:I.Data.1; //PH 2305 RAM 13 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
767 | PH 2 R4G6M0 | 1771-IAD | 4 | 12 | 17 | 1756-IA16 | 4 | 3 | 2 | PH2RAM14_SS | I:046/17 |  | PH 2305 RAM 14 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM14_SS_IO | K2_Preheater_R04:3:I.Data.2 | PH2RAM14_SS_IO:= K2_Preheater_R04:3:I.Data.2; //PH 2305 RAM 14 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
768 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 00 | 1756-OA16 | 4 | REMOVE | 0 |  | O:046/0 |  | PH 2305 RAM 17 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.0 | // K2_Preheater_R04:REMOVE:O.Data.0 PH 2305 RAM 17 MIMIC LIGHT KILN 2 PH
769 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 01 | 1756-OA16 | 4 | REMOVE | 1 |  | O:046/1 |  | PH 2305 RAM 18 MIMIC LIGHT KILN 2 PH |  | Notes: Mimic light outputs will be removed on new panel | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:REMOVE:O.Data.1 | // K2_Preheater_R04:REMOVE:O.Data.1 PH 2305 RAM 18 MIMIC LIGHT KILN 2 PH
770 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 02 | 1756-OA16 | 4 | 6 | 0 | PH2RAM1_SV | O:046/2 | PH | PH 2305 RAM 1 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM1_SV_IO | K2_Preheater_R04:6:O.Data.0 | K2_Preheater_R04:6:O.Data.0:=PH2RAM1_SV_IO; //PH 2305 RAM 1 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
771 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 03 | 1756-OA16 | 4 | 6 | 1 | PH2RAM2_SV | O:046/3 | PH | PH 2305 RAM 2 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM2_SV_IO | K2_Preheater_R04:6:O.Data.1 | K2_Preheater_R04:6:O.Data.1:=PH2RAM2_SV_IO; //PH 2305 RAM 2 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
772 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 04 | 1756-OA16 | 4 | 6 | 2 | PH2RAM3_SV | O:046/4 | PH | PH 2305 RAM 3 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM3_SV_IO | K2_Preheater_R04:6:O.Data.2 | K2_Preheater_R04:6:O.Data.2:=PH2RAM3_SV_IO; //PH 2305 RAM 3 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
773 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 05 | 1756-OA16 | 4 | 6 | 3 | PH2RAM4_SV | O:046/5 | PH | PH 2305 RAM 4 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM4_SV_IO | K2_Preheater_R04:6:O.Data.3 | K2_Preheater_R04:6:O.Data.3:=PH2RAM4_SV_IO; //PH 2305 RAM 4 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
774 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 06 | 1756-OA16 | 4 | 6 | 4 | PH2RAM5_SV | O:046/6 | PH | PH 2305 RAM 5 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM5_SV_IO | K2_Preheater_R04:6:O.Data.4 | K2_Preheater_R04:6:O.Data.4:=PH2RAM5_SV_IO; //PH 2305 RAM 5 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
775 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 07 | 1756-OA16 | 4 | 6 | 5 | PH2RAM6_SV | O:046/7 | PH | PH 2305 RAM 6 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM6_SV_IO | K2_Preheater_R04:6:O.Data.5 | K2_Preheater_R04:6:O.Data.5:=PH2RAM6_SV_IO; //PH 2305 RAM 6 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
776 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 10 | 1756-OA16 | 4 | 6 | 6 | PH2RAM7_SV | O:046/10 | PH | PH 2305 RAM 7 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM7_SV_IO | K2_Preheater_R04:6:O.Data.6 | K2_Preheater_R04:6:O.Data.6:=PH2RAM7_SV_IO; //PH 2305 RAM 7 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
777 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 11 | 1756-OA16 | 4 | 6 | 7 | PH2RAM8_SV | O:046/11 | PH | PH 2305 RAM 8 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM8_SV_IO | K2_Preheater_R04:6:O.Data.7 | K2_Preheater_R04:6:O.Data.7:=PH2RAM8_SV_IO; //PH 2305 RAM 8 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
778 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 12 | 1756-OA16 | 4 | 6 | 8 | PH2RAM9_SV | O:046/12 | PH | PH 2305 RAM 9 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM9_SV_IO | K2_Preheater_R04:6:O.Data.8 | K2_Preheater_R04:6:O.Data.8:=PH2RAM9_SV_IO; //PH 2305 RAM 9 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
779 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 13 | 1756-OA16 | 4 | 6 | 9 | PH2RAM10_SV | O:046/13 | PH | PH 2305 RAM 10 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM10_SV_IO | K2_Preheater_R04:6:O.Data.9 | K2_Preheater_R04:6:O.Data.9:=PH2RAM10_SV_IO; //PH 2305 RAM 10 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
780 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 14 | 1756-OA16 | 4 | 6 | 10 | PH2RAM11_SV | O:046/14 | PH | PH 2305 RAM 11 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM11_SV_IO | K2_Preheater_R04:6:O.Data.10 | K2_Preheater_R04:6:O.Data.10:=PH2RAM11_SV_IO; //PH 2305 RAM 11 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
781 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 15 | 1756-OA16 | 4 | 6 | 11 | PH2RAM12_SV | O:046/15 | PH | PH 2305 RAM 12 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM12_SV_IO | K2_Preheater_R04:6:O.Data.11 | K2_Preheater_R04:6:O.Data.11:=PH2RAM12_SV_IO; //PH 2305 RAM 12 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
782 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 16 | 1756-OA16 | 4 | 6 | 12 | PH2RAM13_SV | O:046/16 | PH | PH 2305 RAM 13 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM13_SV_IO | K2_Preheater_R04:6:O.Data.12 | K2_Preheater_R04:6:O.Data.12:=PH2RAM13_SV_IO; //PH 2305 RAM 13 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
783 | PH 2 R4G6M1 | 1771-OAD | 4 | 13 | 17 | 1756-OA16 | 4 | 6 | 13 | PH2RAM14_SV | O:046/17 | PH | PH 2305 RAM 14 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM14_SV_IO | K2_Preheater_R04:6:O.Data.13 | K2_Preheater_R04:6:O.Data.13:=PH2RAM14_SV_IO; //PH 2305 RAM 14 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
784 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 00 | 1756-IA16 | 4 | 3 | 3 | PH2RAM15_SS | I:047/0 |  | PH 2305 RAM 15 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM15_SS_IO | K2_Preheater_R04:3:I.Data.3 | PH2RAM15_SS_IO:= K2_Preheater_R04:3:I.Data.3; //PH 2305 RAM 15 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
785 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 01 | 1756-IA16 | 4 | 3 | 4 | PH2RAM16_SS | I:047/1 |  | PH 2305 RAM 16 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM16_SS_IO | K2_Preheater_R04:3:I.Data.4 | PH2RAM16_SS_IO:= K2_Preheater_R04:3:I.Data.4; //PH 2305 RAM 16 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
786 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 02 | 1756-IA16 | 4 | 3 | 5 | PH2RAM17_SS | I:047/2 |  | PH 2305 RAM 17 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM17_SS_IO | K2_Preheater_R04:3:I.Data.5 | PH2RAM17_SS_IO:= K2_Preheater_R04:3:I.Data.5; //PH 2305 RAM 17 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
787 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 03 | 1756-IA16 | 4 | 3 | 6 | PH2RAM18_SS | I:047/3 |  | PH 2305 RAM 18 SELECTOR SWITCH KILN 2 PH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2RAM18_SS_IO | K2_Preheater_R04:3:I.Data.6 | PH2RAM18_SS_IO:= K2_Preheater_R04:3:I.Data.6; //PH 2305 RAM 18 SELECTOR SWITCH KILN 2 PH |  | NA | NA | NA
788 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 04 | 1756-IA16 | 4 | 3 | 12 | PM23051_SS | I:047/4 |  | PM 2305-1 ENABLED KILN 2 PH HYDRAULIC PUMP #1 SELECTOR SWITCH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PM23051_SS_IO | K2_Preheater_R04:3:I.Data.12 | PM23051_SS_IO:= K2_Preheater_R04:3:I.Data.12; //PM 2305-1 ENABLED KILN 2 PH HYDRAULIC PUMP #1 SELECTOR SWITCH |  | _PM23051_SS | P_DIn | Sts_PV
789 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 05 | 1756-IA16 | 4 | 3 | 13 | PM23052_SS | I:047/5 |  | PM 2305-2 ENABLED KILN 2 PH HYDRAULIC PUMP #2 SELECTOR SWITCH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PM23052_SS_IO | K2_Preheater_R04:3:I.Data.13 | PM23052_SS_IO:= K2_Preheater_R04:3:I.Data.13; //PM 2305-2 ENABLED KILN 2 PH HYDRAULIC PUMP #2 SELECTOR SWITCH |  | _PM23052_SS | P_DIn | Sts_PV
790 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 06 | 1756-IA16 | 4 | 4 | 06 | PH2305_LAMPTST | I:047/6 |  | PH 2305 LAMP TEST PUSHBUTTON KILN 2 PH |  | Notes: Lamp Test Light Input will be removed on New Panel | K2_Preheater_R04 | I.Data | INPUT | PH2305_LAMPTST_IO | K2_Preheater_R04:4:I.Data.06 | PH2305_LAMPTST_IO:= K2_Preheater_R04:4:I.Data.06; //PH 2305 LAMP TEST PUSHBUTTON KILN 2 PH |  | _PH2305_LAMPTST | P_DIn | Sts_PV
791 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 07 | 1756-IA16 | 4 | 4 | 07 | PH2305_1_ZSO | I:047/7 |  | PH 2305 LIMIT SWITCH KILN 2 PH SOUTH RAMS OPEN |  | Notes: South Rams Open Input will be removed on New Panel | K2_Preheater_R04 | I.Data | INPUT | PH2305_1_ZSO_IO | K2_Preheater_R04:4:I.Data.07 | PH2305_1_ZSO_IO:= K2_Preheater_R04:4:I.Data.07; //PH 2305 LIMIT SWITCH KILN 2 PH SOUTH RAMS OPEN |  | NA | NA | NA
792 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 10 | 1756-IA16 | 4 | 4 | 08 | PH2305_2_ZSO | I:047/10 |  | PH 2305 LIMIT SWITCH KILN 2 PH NORTH RAMS OPEN |  | Notes: North Rams Open Input will be removed on New Panel | K2_Preheater_R04 | I.Data | INPUT | PH2305_2_ZSO_IO | K2_Preheater_R04:4:I.Data.08 | PH2305_2_ZSO_IO:= K2_Preheater_R04:4:I.Data.08; //PH 2305 LIMIT SWITCH KILN 2 PH NORTH RAMS OPEN |  | NA | NA | NA
793 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 11 | 1756-IA16 | 4 | 4 | 09 | PS_UY | I:047/11 |  | RESET PUSHBUTTON | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PS_UY_IO | K2_Preheater_R04:4:I.Data.09 | PS_UY_IO:= K2_Preheater_R04:4:I.Data.09; //RESET PUSHBUTTON |  | _PS_UY | P_DIn | Sts_PV
794 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 12 | 1756-IA16 | 4 | 3 | 14 | PH2_HYD_LLL | I:047/12 |  | ALARM KILN 2 PH OIL LO LO | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2_HYD_LLL_IO | K2_Preheater_R04:3:I.Data.14 | PH2_HYD_LLL_IO:= K2_Preheater_R04:3:I.Data.14; //ALARM KILN 2 PH OIL LO LO |  | _PH2_HYD_LLL | P_DIn | Sts_PV
795 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 13 | 1756-IA16 | 4 | 3 | 15 | PH2_HYD_LL | I:047/13 |  | ALARM KILN 2 PH OIL LO | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2_HYD_LL_IO | K2_Preheater_R04:3:I.Data.15 | PH2_HYD_LL_IO:= K2_Preheater_R04:3:I.Data.15; //ALARM KILN 2 PH OIL LO |  | _PH2_HYD_LL | P_DIn | Sts_PV
796 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 14 | 1756-IA16 | 4 | 4 | 0 | PH2_FILTER_PH | I:047/14 |  | ALARM KILN 2 PH FILTER PRESSURE HIGH | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2_FILTER_PH_IO | K2_Preheater_R04:4:I.Data.0 | PH2_FILTER_PH_IO:= K2_Preheater_R04:4:I.Data.0; //ALARM KILN 2 PH FILTER PRESSURE HIGH |  | _PH2_FILTER_PH | P_DIn | Sts_PV
797 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 15 | 1756-IA16 | 4 | 4 | 1 | PH2_HYD_OIL_TL | I:047/15 |  | ALARM KILN 2 PH OIL TEMPERATURE LOW | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PH2_HYD_OIL_TL_IO | K2_Preheater_R04:4:I.Data.1 | PH2_HYD_OIL_TL_IO:= K2_Preheater_R04:4:I.Data.1; //ALARM KILN 2 PH OIL TEMPERATURE LOW |  | _PH2_HYD_OIL_TL | P_DIn | Sts_PV
798 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 16 | 1756-IA16 | 4 | 4 | 2 | PM23051_AUX | I:047/16 | PM | PM 2305-1 AUX FDBK KILN 2 PH HYDRAULIC PUMP #1 | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PM23051_AUX_IO | K2_Preheater_R04:4:I.Data.2 | PM23051_AUX_IO:= K2_Preheater_R04:4:I.Data.2; //PM 2305-1 AUX FDBK KILN 2 PH HYDRAULIC PUMP #1 |  | _PM23051_M01 | P_Motor | Sts_Running |  | Kiln2_Preheater_TaskC | Task_C | _PM23051_M01
799 | PH 2 R4G7M0 | 1771-IAD | 4 | 14 | 17 | 1756-IA16 | 4 | 4 | 3 | PM23052_AUX | I:047/17 | PM | PM 2305-2 AUX FDBK KILN 2 PH HYDRAULIC PUMP #2 | [10 empty] | K2_Preheater_R04 | I.Data | INPUT | PM23052_AUX_IO | K2_Preheater_R04:4:I.Data.3 | PM23052_AUX_IO:= K2_Preheater_R04:4:I.Data.3; //PM 2305-2 AUX FDBK KILN 2 PH HYDRAULIC PUMP #2 |  | _PM23052_M01 | P_Motor | Sts_Running |  | Kiln2_Preheater_TaskC | Task_C | _PM23052_M01
800 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 00 | 1756-OA16 | 4 | 6 | 14 | PH2RAM15_SV | O:047/0 | PH | PH 2305 RAM 15 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM15_SV_IO | K2_Preheater_R04:6:O.Data.14 | K2_Preheater_R04:6:O.Data.14:=PH2RAM15_SV_IO; //PH 2305 RAM 15 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
801 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 01 | 1756-OA16 | 4 | 6 | 15 | PH2RAM16_SV | O:047/1 | PH | PH 2305 RAM 16 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM16_SV_IO | K2_Preheater_R04:6:O.Data.15 | K2_Preheater_R04:6:O.Data.15:=PH2RAM16_SV_IO; //PH 2305 RAM 16 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
802 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 02 | 1756-OA16 | 4 | 7 | 0 | PH2RAM17_SV | O:047/2 | PH | PH 2305 RAM 17 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM17_SV_IO | K2_Preheater_R04:7:O.Data.0 | K2_Preheater_R04:7:O.Data.0:=PH2RAM17_SV_IO; //PH 2305 RAM 17 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
803 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 03 | 1756-OA16 | 4 | 7 | 1 | PH2RAM18_SV | O:047/3 | PH | PH 2305 RAM 18 RUN KILN 2 PH HYDRAULIC SOLENOID | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2RAM18_SV_IO | K2_Preheater_R04:7:O.Data.1 | K2_Preheater_R04:7:O.Data.1:=PH2RAM18_SV_IO; //PH 2305 RAM 18 RUN KILN 2 PH HYDRAULIC SOLENOID |  | NA | NA | NA
804 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 04 | 1756-OA16 | 4 | 7 | 2 | PM23051_COIL | O:047/4 | PH | PM 2305-1 RUN KILN 2 PH HYDRAULIC PUMP #1 | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PM23051_COIL_IO | K2_Preheater_R04:7:O.Data.2 | K2_Preheater_R04:7:O.Data.2:=PM23051_COIL_IO; //PM 2305-1 RUN KILN 2 PH HYDRAULIC PUMP #1 |  | _PM23051_M01 | P_Motor | PCmd_Start |  | Kiln2_Preheater_TaskC | Task_C | _PM23051_M01
805 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 05 | 1756-OA16 | 4 | 7 | 3 | PM23052_COIL | O:047/5 | PH | PM 2305-2 RUN KILN 2 PH HYDRAULIC PUMP #2 | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PM23052_COIL_IO | K2_Preheater_R04:7:O.Data.3 | K2_Preheater_R04:7:O.Data.3:=PM23052_COIL_IO; //PM 2305-2 RUN KILN 2 PH HYDRAULIC PUMP #2 |  | _PM23052_M01 | P_Motor | PCmd_Start |  | Kiln2_Preheater_TaskC | Task_C | _PM23052_M01
806 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 06 | 1756-OA16 | 4 | 7 | 4 | PH2_HYD_SDUMP_SV | O:047/6 |  | PH 2305 RELEASE KILN 2 PH SOUTH RAMS SOLENOIDS | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2_HYD_SDUMP_SV_IO | K2_Preheater_R04:7:O.Data.4 | K2_Preheater_R04:7:O.Data.4:=PH2_HYD_SDUMP_SV_IO; //PH 2305 RELEASE KILN 2 PH SOUTH RAMS SOLENOIDS |  | NA | NA | NA
807 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 07 | 1756-OA16 | 4 | 7 | 5 | PH2_HYD_NDUMP_SV | O:047/7 |  | PH 2305 RELEASE KILN 2 PH NORTH RAMS SOLENOIDS | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | PH2_HYD_NDUMP_SV_IO | K2_Preheater_R04:7:O.Data.5 | K2_Preheater_R04:7:O.Data.5:=PH2_HYD_NDUMP_SV_IO; //PH 2305 RELEASE KILN 2 PH NORTH RAMS SOLENOIDS |  | NA | NA | NA
808 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 10 | 1756-OA16 | 4 | 7 | 6 | O2AN_FRO_SV | O:047/10 |  | OPEN AIR FLOW LINE TO O2 ANALYZERS | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | O2AN_FRO_SV_IO | K2_Preheater_R04:7:O.Data.6 | K2_Preheater_R04:7:O.Data.6:=O2AN_FRO_SV_IO; //OPEN AIR FLOW LINE TO O2 ANALYZERS |  | NA | NA | NA
809 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 11 | 1756-OA16 | 4 | 7 | 9 | SPARE | O:047/11 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | SPARE_IO | K2_Preheater_R04:7:O.Data.9 | K2_Preheater_R04:7:O.Data.9:=SPARE_IO; //SPARE |  | _SPARE
810 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 12 | 1756-OA16 | 4 | 7 | 7 | O2AN_BLD_SV | O:047/12 |  | AIR BLEED LINE AFTER PURGE OFF | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | O2AN_BLD_SV_IO | K2_Preheater_R04:7:O.Data.7 | K2_Preheater_R04:7:O.Data.7:=O2AN_BLD_SV_IO; //AIR BLEED LINE AFTER PURGE OFF |  | NA | NA | NA
811 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 13 | 1756-OA16 | 4 | 7 | 8 | O2AN_PGE_SV | O:047/13 |  | AIR PURGE FOR BLOWBACK OF O2 TUBING LINES (SUBSTITUTE O:47/11) | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT | O2AN_PGE_SV_IO | K2_Preheater_R04:7:O.Data.8 | K2_Preheater_R04:7:O.Data.8:=O2AN_PGE_SV_IO; //AIR PURGE FOR BLOWBACK OF O2 TUBING LINES (SUBSTITUTE O:47/11) |  | NA | NA | NA
812 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 14 | 1756-OA16 | 4 | 7 | 12 |  | O:047/14 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:7:O.Data.12 | // K2_Preheater_R04:7:O.Data.12 SPARE
813 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 15 | 1756-OA16 | 4 | 7 | 13 |  | O:047/15 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:7:O.Data.13 | // K2_Preheater_R04:7:O.Data.13 SPARE
814 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 16 | 1756-OA16 | 4 | 7 | 14 |  | O:047/16 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:7:O.Data.14 | // K2_Preheater_R04:7:O.Data.14 SPARE
815 | PH 2 R4G7M1 | 1771-OAD | 4 | 15 | 17 | 1756-OA16 | 4 | 7 | 15 |  | O:047/17 |  | SPARE | [10 empty] | K2_Preheater_R04 | O.Data | OUTPUT |  | K2_Preheater_R04:7:O.Data.15 | // K2_Preheater_R04:7:O.Data.15 SPARE
816 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH1 | 1756-IF16 | 5 | 8 | 0 | FN4460_IT | N41:0 | FN | FN 4460 AMPS DUST BLENDING BLOWER |  | EU: Ampers; V.MIN: 0; V.MAX: 100 | MCR5_R05 | I.Ch | INPUT | FN4460_IT_IO | MCR5_R05:8:I.Ch0Data | FN4460_IT_IO:= MCR5_R05:8:I.Ch0Data; //FN 4460 AMPS DUST BLENDING BLOWER |  | _FN4460_IT | P_AIn | Val |  | Dust_Blending_TaskD | Task_D | _FN4460_IT
817 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH2 | 1756-IF16 | 5 | 8 | 1 | PM4461_IT | N41:1 | PM | PM 4461 AMPS DUST BLENDING PUMP |  | EU: Ampers; V.MIN: 0; V.MAX: 25 | MCR5_R05 | I.Ch | INPUT | PM4461_IT_IO | MCR5_R05:8:I.Ch1Data | PM4461_IT_IO:= MCR5_R05:8:I.Ch1Data; //PM 4461 AMPS DUST BLENDING PUMP |  | _PM4461_IT | P_AIn | Val |  | Dust_Blending_TaskD | Task_D | _PM4461_IT
818 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH3 | 1756-IF16 | 5 | 8 | 2 | DC1313_DPT | N41:2 |  | K1 1313 BAGHOUSE DIFFERENTIAL 0-10"WC |  | EU: "WC; V.MIN: 0; V.MAX: 10 | MCR5_R05 | I.Ch | INPUT | DC1313_DPT_IO | MCR5_R05:8:I.Ch2Data | DC1313_DPT_IO:= MCR5_R05:8:I.Ch2Data; //K1 1313 BAGHOUSE DIFFERENTIAL 0-10"WC |  | _DC1313_DPT | P_AIn | Val | 0
819 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH4 | 1756-IF16 | 5 | 8 | 3 | FN4460_PT_DISCHARGE | N41:3 | FN | FN 4460 PRESSURE DUST BLENDING BLOWER DISCHARGE |  | EU: Pressure; V.MIN: 0; V.MAX: 50 | MCR5_R05 | I.Ch | INPUT | FN4460_PT_DISCHARGE_IO | MCR5_R05:8:I.Ch3Data | FN4460_PT_DISCHARGE_IO:= MCR5_R05:8:I.Ch3Data; //FN 4460 PRESSURE DUST BLENDING BLOWER DISCHARGE |  | _FN4460_PT_DISCHARGE | P_AIn | Val |  | Dust_Blending_TaskD | Task_D | _FN4460_PT_DISCHARGE
820 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH5 | 1756-IF16 | 5 | 8 | 4 | DC2319_PT | N41:4 |  | DC 2319 STATIC PRESSURE 0-50" WC |  | EU: "WC; V.MIN: 0; V.MAX: 50 | MCR5_R05 | I.Ch | INPUT | DC2319_PT_IO | MCR5_R05:8:I.Ch4Data | DC2319_PT_IO:= MCR5_R05:8:I.Ch4Data; //DC 2319 STATIC PRESSURE 0-50" WC |  | _DC2319_PT | P_AIn | Val | 1 | Kiln2_Dust_Collection_TaskD | Task_D | _DC2319_PT | Kill 2 Dust Collection
821 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH6 | 1756-IF16 | 5 | 8 | 5 | PH2_PT_OUTLET | N41:5 |  | K2 PREHEATER OUTLET DRAFT 0-50"WC |  | EU: "WC; V.MIN: 0; V.MAX: 50 | MCR5_R05 | I.Ch | INPUT | PH2_PT_OUTLET_IO | MCR5_R05:8:I.Ch5Data | PH2_PT_OUTLET_IO:= MCR5_R05:8:I.Ch5Data; //K2 PREHEATER OUTLET DRAFT 0-50"WC |  | _PH2_PT_OUTLET | P_AIn | Val
822 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH7 | 1756-IF16 | 5 | 8 | 6 | KN2_PT_FEEDEND | N41:6 |  | K2 FEED END DRAFT 0-10" WC |  | EU: "WC; V.MIN: 0; V.MAX: 10 | MCR5_R05 | I.Ch | INPUT | KN2_PT_FEEDEND_IO | MCR5_R05:8:I.Ch6Data | KN2_PT_FEEDEND_IO:= MCR5_R05:8:I.Ch6Data; //K2 FEED END DRAFT 0-10" WC |  | NA | NA | NA
823 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH8 | 1756-IF16 | 5 | 8 | 7 | DC22313_DPT | N41:7 |  | K2 2313 BAGHOUSE DIFFERENTIAL 0-15"WC |  | EU: "WC; V.MIN: 0; V.MAX: 15 | MCR5_R05 | I.Ch | INPUT | DC22313_DPT_IO | MCR5_R05:8:I.Ch7Data | DC22313_DPT_IO:= MCR5_R05:8:I.Ch7Data; //K2 2313 BAGHOUSE DIFFERENTIAL 0-15"WC |  | _DC22313_DPT | P_AIn | Val | 0
824 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH9 | 1756-IF16 | 5 | 8 | 8 | FN2314_IT | N41:8 | FN | FN 2314 AMPS KILN 2 ID FAN |  | EU: Ampers; V.MIN: 0; V.MAX: 350 | MCR5_R05 | I.Ch | INPUT | FN2314_IT_IO | MCR5_R05:8:I.Ch8Data | FN2314_IT_IO:= MCR5_R05:8:I.Ch8Data; //FN 2314 AMPS KILN 2 ID FAN |  | _FN2314_IT | P_AIn | Val |  | Kiln2_Main_TaskD | Task_D | _FN2314_IT
825 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH10 | 1756-IF16 | 5 | 8 | 9 |  | N41:9 |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:8:I.Ch9Data | // MCR5_R05:8:I.Ch9Data SPARE
826 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH11 | 1756-IF16 | 5 | 8 | 10 |  | N41:10 |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:8:I.Ch10Data | // MCR5_R05:8:I.Ch10Data SPARE
827 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH12 | 1756-IF16 | 5 | 8 | 11 |  | N41:11 |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:8:I.Ch11Data | // MCR5_R05:8:I.Ch11Data SPARE
828 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH13 | 1756-IF16 | 5 | 8 | 12 | BN2318_LT | N41:12 |  | BN2318 DUST BIN LEVEL TRANSMITTER |  | EU: % Level; V.MIN: 0; V.MAX: 100 | MCR5_R05 | I.Ch | INPUT | BN2318_LT_IO | MCR5_R05:8:I.Ch12Data | BN2318_LT_IO:= MCR5_R05:8:I.Ch12Data; //BN2318 DUST BIN LEVEL TRANSMITTER |  | _BN2318_LT | P_AIn | Val | 0
829 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH14 | 1756-IF16 | 5 | 8 | 13 | FN2314_PT_INLET | N41:13 |  | K2 ID FAN INLET 0-50" WC |  | EU: "WC; V.MIN: 0; V.MAX: 50 | MCR5_R05 | I.Ch | INPUT | FN2314_PT_INLET_IO | MCR5_R05:8:I.Ch13Data | FN2314_PT_INLET_IO:= MCR5_R05:8:I.Ch13Data; //K2 ID FAN INLET 0-50" WC |  | _FN2314_PT_INLET | P_AIn | Val
830 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH15 | 1756-IF16 | 5 | 8 | 14 | FN1314_PT_INLET | N41:14 |  | K1 ID FAN INLET PRESSURE 0-50"WC |  | EU: "WC; V.MIN: 0; V.MAX: 50 | MCR5_R05 | I.Ch | INPUT | FN1314_PT_INLET_IO | MCR5_R05:8:I.Ch14Data | FN1314_PT_INLET_IO:= MCR5_R05:8:I.Ch14Data; //K1 ID FAN INLET PRESSURE 0-50"WC |  | _FN1314_PT_INLET | P_AIn | Val
831 | MCR5 R5G0M0 | 1771-IFE | 5 | 0 | CH16 | 1756-IF16 | 5 | 8 | 15 | PH1_PT_OUTLET | N41:15 |  | K1 PREHEATER OUTLET PRESSURE 0-50" WC |  | EU: "WC; V.MIN: 0; V.MAX: 50 | MCR5_R05 | I.Ch | INPUT | PH1_PT_OUTLET_IO | MCR5_R05:8:I.Ch15Data | PH1_PT_OUTLET_IO:= MCR5_R05:8:I.Ch15Data; //K1 PREHEATER OUTLET PRESSURE 0-50" WC |  | _PH1_PT_OUTLET | P_AIn | Val
832 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH1 | 1756-IF16 | 5 | 9 | 0 | WS8329_WIT | N82:13 | WS | WS 8329 FEED RATE STONE FEED WEIGH SCALE TONS/HR | RAMSEY SCALE | EU: Tons per Hours; V.MIN: 0; V.MAX: 300 | MCR5_R05 | I.Ch | INPUT | WS8329_WIT_IO | MCR5_R05:9:I.Ch0Data | WS8329_WIT_IO:= MCR5_R05:9:I.Ch0Data; //WS 8329 FEED RATE STONE FEED WEIGH SCALE TONS/HR |  | _WS8329_WIT | P_AIn | Val
833 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH2 | 1756-IF16 | 5 | 9 | 1 | WS8303A_WIT | N82:5 | WS | WS 8303-A FEED RATE STONE FEED WEIGH SCALE TONS/HR | RAMSEY SCALE | EU: Tons per Hours; V.MIN: 0; V.MAX: 300 | MCR5_R05 | I.Ch | INPUT | WS8303A_WIT_IO | MCR5_R05:9:I.Ch1Data | WS8303A_WIT_IO:= MCR5_R05:9:I.Ch1Data; //WS 8303-A FEED RATE STONE FEED WEIGH SCALE TONS/HR |  | _WS8303A_WIT | P_AIn | Val
834 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH3 | 1756-IF16 | 5 | 9 | 2 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch2Data | // MCR5_R05:9:I.Ch2Data SPARE
835 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH4 | 1756-IF16 | 5 | 9 | 3 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch3Data | // MCR5_R05:9:I.Ch3Data SPARE
836 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH5 | 1756-IF16 | 5 | 9 | 4 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch4Data | // MCR5_R05:9:I.Ch4Data SPARE
837 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH6 | 1756-IF16 | 5 | 9 | 5 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch5Data | // MCR5_R05:9:I.Ch5Data SPARE
838 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH7 | 1756-IF16 | 5 | 9 | 6 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch6Data | // MCR5_R05:9:I.Ch6Data SPARE
839 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH8 | 1756-IF16 | 5 | 9 | 7 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch7Data | // MCR5_R05:9:I.Ch7Data SPARE
840 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH9 | 1756-IF16 | 5 | 9 | 8 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch8Data | // MCR5_R05:9:I.Ch8Data SPARE
841 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH10 | 1756-IF16 | 5 | 9 | 9 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch9Data | // MCR5_R05:9:I.Ch9Data SPARE
842 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH11 | 1756-IF16 | 5 | 9 | 10 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch10Data | // MCR5_R05:9:I.Ch10Data SPARE
843 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH12 | 1756-IF16 | 5 | 9 | 11 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch11Data | // MCR5_R05:9:I.Ch11Data SPARE
844 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH13 | 1756-IF16 | 5 | 9 | 12 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch12Data | // MCR5_R05:9:I.Ch12Data SPARE
845 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH14 | 1756-IF16 | 5 | 9 | 13 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch13Data | // MCR5_R05:9:I.Ch13Data SPARE
846 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH15 | 1756-IF16 | 5 | 9 | 14 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch14Data | // MCR5_R05:9:I.Ch14Data SPARE
847 | MCR5 R5G0M1 | 1771-IFE | 5 | 1 | CH16 | 1756-IF16 | 5 | 9 | 15 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Ch | INPUT |  | MCR5_R05:9:I.Ch15Data | // MCR5_R05:9:I.Ch15Data SPARE
848 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 0 | 1756-IB16 | 5 | 4 | 0 |  | I:051/0 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.0 | // MCR5_R05:4:I.Data.0 SPARE
849 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 1 | 1756-IB16 | 5 | 4 | 1 |  | I:051/1 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.1 | // MCR5_R05:4:I.Data.1 SPARE
850 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 2 | 1756-IB16 | 5 | 4 | 2 |  | I:051/2 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.2 | // MCR5_R05:4:I.Data.2 SPARE
851 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 3 | 1756-IB16 | 5 | 4 | 3 |  | I:051/3 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.3 | // MCR5_R05:4:I.Data.3 SPARE
852 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 4 | 1756-IB16 | 5 | 4 | 4 |  | I:051/4 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.4 | // MCR5_R05:4:I.Data.4 SPARE
853 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 5 | 1756-IB16 | 5 | 4 | 5 |  | I:051/5 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.5 | // MCR5_R05:4:I.Data.5 SPARE
854 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 6 | 1756-IB16 | 5 | 4 | 6 |  | I:051/6 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.6 | // MCR5_R05:4:I.Data.6 SPARE
855 | MCR5 R5G1M0 | 1771-IT | 5 | 2 | 7 | 1756-IB16 | 5 | 4 | 7 |  | I:051/7 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.7 | // MCR5_R05:4:I.Data.7 SPARE
856 | [5 empty] | 1756-IB16 | 5 | 4 | 8 |  | I:051/10 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.8 | // MCR5_R05:4:I.Data.8 SPARE
857 | [5 empty] | 1756-IB16 | 5 | 4 | 9 |  | I:051/11 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.9 | // MCR5_R05:4:I.Data.9 SPARE
858 | [5 empty] | 1756-IB16 | 5 | 4 | 10 |  | I:051/12 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.10 | // MCR5_R05:4:I.Data.10 SPARE
859 | [5 empty] | 1756-IB16 | 5 | 4 | 11 |  | I:051/13 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.11 | // MCR5_R05:4:I.Data.11 SPARE
860 | [5 empty] | 1756-IB16 | 5 | 4 | 12 |  | I:051/14 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.12 | // MCR5_R05:4:I.Data.12 SPARE
861 | [5 empty] | 1756-IB16 | 5 | 4 | 13 |  | I:051/15 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.13 | // MCR5_R05:4:I.Data.13 SPARE
862 | [5 empty] | 1756-IB16 | 5 | 4 | 14 |  | I:051/16 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.14 | // MCR5_R05:4:I.Data.14 SPARE
863 | [5 empty] | 1756-IB16 | 5 | 4 | 15 |  | I:051/17 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:4:I.Data.15 | // MCR5_R05:4:I.Data.15 SPARE
864 | MCR5 R5G2M0 | 1771-IR | 5 | 4 | CH1 | 1756-IRT8I | 5 | 12 | 0 | FN2314N_1_TE | N68:46 | FN | FN 2314 N FAN BEARING TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN2314N_1_TE_IO | MCR5_R05:12:I.Ch[0].Data | FN2314N_1_TE_IO:= MCR5_R05:12:I.Ch[0].Data; //FN 2314 N FAN BEARING TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN2314N_1_TE | P_AIn | Val
865 | MCR5 R5G2M0 | 1771-IR | 5 | 4 | CH2 | 1756-IRT8I | 5 | 12 | 1 | FN2314S_1_TE | N68:47 | FN | FN 2314 S FAN BEARING TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN2314S_1_TE_IO | MCR5_R05:12:I.Ch[1].Data | FN2314S_1_TE_IO:= MCR5_R05:12:I.Ch[1].Data; //FN 2314 S FAN BEARING TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN2314S_1_TE | P_AIn | Val
866 | MCR5 R5G2M0 | 1771-IR | 5 | 4 | CH3 | 1756-IRT8I | 5 | 12 | 2 | FN2314S_2_TE | N68:48 | FN | FN 2314 S MOTOR BEARING TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN2314S_2_TE_IO | MCR5_R05:12:I.Ch[2].Data | FN2314S_2_TE_IO:= MCR5_R05:12:I.Ch[2].Data; //FN 2314 S MOTOR BEARING TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN2314S_2_TE | P_AIn | Val
867 | MCR5 R5G2M0 | 1771-IR | 5 | 4 | CH4 | 1756-IRT8I | 5 | 12 | 3 | FN2314N_2_TE | N68:49 | FN | FN 2314 N MOTOR BEARING TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN2314N_2_TE_IO | MCR5_R05:12:I.Ch[3].Data | FN2314N_2_TE_IO:= MCR5_R05:12:I.Ch[3].Data; //FN 2314 N MOTOR BEARING TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN2314N_2_TE | P_AIn | Val
868 | MCR5 R5G2M0 | 1771-IR | 5 | 4 | CH5 | 1756-IRT8I | 5 | 12 | 4 | FN2314_TE | N68:50 | FN | FN 2314 MOTOR WIND #2 TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN2314_TE_IO | MCR5_R05:12:I.Ch[4].Data | FN2314_TE_IO:= MCR5_R05:12:I.Ch[4].Data; //FN 2314 MOTOR WIND #2 TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN2314_TE | P_AIn | Val
869 | MCR5 R5G2M0 | 1771-IR | 5 | 4 | CH6 | 1756-IRT8I | 5 | 12 | 5 |  |  |  | SPARE | RTD | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT |  | MCR5_R05:12:I.Ch[5].Data | // MCR5_R05:12:I.Ch[5].Data SPARE
870 | [5 empty] | 1756-IRT8I | 5 | 12 | 6 |  |  |  | SPARE | RTD | [9 empty] | MCR5_R05 | I.Ch[ | INPUT |  | MCR5_R05:12:I.Ch[6].Data | // MCR5_R05:12:I.Ch[6].Data SPARE
871 | [5 empty] | 1756-IRT8I | 5 | 12 | 7 |  |  |  | SPARE | RTD | [9 empty] | MCR5_R05 | I.Ch[ | INPUT |  | MCR5_R05:12:I.Ch[7].Data | // MCR5_R05:12:I.Ch[7].Data SPARE
872 | MCR5 R5G2M1 | 1771-IR | 5 | 5 | CH1 | 1756-IRT8I | 5 | 13 | 0 | FN23141_TE | N68:68 | FN | FN 2314 MOTOR WIND #1 TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN23141_TE_IO | MCR5_R05:13:I.Ch[0].Data | FN23141_TE_IO:= MCR5_R05:13:I.Ch[0].Data; //FN 2314 MOTOR WIND #1 TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN23141_TE | P_AIn | Val
873 | MCR5 R5G2M1 | 1771-IR | 5 | 5 | CH2 | 1756-IRT8I | 5 | 13 | 1 |  |  |  | BAD CHANNEL (PLC 5) | RTD | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT |  | MCR5_R05:13:I.Ch[1].Data | // MCR5_R05:13:I.Ch[1].Data BAD CHANNEL (PLC 5)
874 | MCR5 R5G2M1 | 1771-IR | 5 | 5 | CH3 | 1756-IRT8I | 5 | 13 | 2 | FN23143_TE | N68:70 | FN | FN 2314 MOTOR WIND #3 TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN23143_TE_IO | MCR5_R05:13:I.Ch[2].Data | FN23143_TE_IO:= MCR5_R05:13:I.Ch[2].Data; //FN 2314 MOTOR WIND #3 TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN23143_TE | P_AIn | Val
875 | MCR5 R5G2M1 | 1771-IR | 5 | 5 | CH4 | 1756-IRT8I | 5 | 13 | 3 | FN23144_TE | N68:71 | FN | FN 2314 MOTOR WIND #4 TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN23144_TE_IO | MCR5_R05:13:I.Ch[3].Data | FN23144_TE_IO:= MCR5_R05:13:I.Ch[3].Data; //FN 2314 MOTOR WIND #4 TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN23144_TE | P_AIn | Val
876 | MCR5 R5G2M1 | 1771-IR | 5 | 5 | CH5 | 1756-IRT8I | 5 | 13 | 4 | FN23145_TE | N68:72 | FN | FN 2314 MOTOR WIND #5 TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN23145_TE_IO | MCR5_R05:13:I.Ch[4].Data | FN23145_TE_IO:= MCR5_R05:13:I.Ch[4].Data; //FN 2314 MOTOR WIND #5 TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN23145_TE | P_AIn | Val
877 | MCR5 R5G2M1 | 1771-IR | 5 | 5 | CH6 | 1756-IRT8I | 5 | 13 | 5 | FN23146_TE | N68:73 | FN | FN 2314 MOTOR WIND #6 TEMP KILN 2 ID FAN (32-428 deg F) | RTD ? | EU: °F; V.MIN: 32; V.MAX: 428 | MCR5_R05 | I.Ch[ | INPUT | FN23146_TE_IO | MCR5_R05:13:I.Ch[5].Data | FN23146_TE_IO:= MCR5_R05:13:I.Ch[5].Data; //FN 2314 MOTOR WIND #6 TEMP KILN 2 ID FAN (32-428 deg F) |  | _FN23146_TE | P_AIn | Val
878 | [5 empty] | 1756-IRT8I | 5 | 13 | 6 |  |  |  | SPARE | RTD | [9 empty] | MCR5_R05 | I.Ch[ | INPUT |  | MCR5_R05:13:I.Ch[6].Data | // MCR5_R05:13:I.Ch[6].Data SPARE
879 | [5 empty] | 1756-IRT8I | 5 | 13 | 7 |  |  |  | SPARE | RTD | [9 empty] | MCR5_R05 | I.Ch[ | INPUT |  | MCR5_R05:13:I.Ch[7].Data | // MCR5_R05:13:I.Ch[7].Data SPARE
880 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 00 | 1756-IA16 | 5 | REMOVE | 00 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.00 | // MCR5_R05:REMOVE:I.Data.00 SPARE
881 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 01 | 1756-IA16 | 5 | REMOVE | 01 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.01 | // MCR5_R05:REMOVE:I.Data.01 SPARE
882 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 02 | 1756-IA16 | 5 | REMOVE | 02 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.02 | // MCR5_R05:REMOVE:I.Data.02 SPARE
883 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 03 | 1756-IA16 | 5 | REMOVE | 03 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.03 | // MCR5_R05:REMOVE:I.Data.03 SPARE
884 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 04 | 1756-IA16 | 5 | REMOVE | 04 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.04 | // MCR5_R05:REMOVE:I.Data.04 SPARE
885 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 05 | 1756-IA16 | 5 | REMOVE | 05 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.05 | // MCR5_R05:REMOVE:I.Data.05 SPARE
886 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 06 | 1756-IA16 | 5 | REMOVE | 06 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.06 | // MCR5_R05:REMOVE:I.Data.06 SPARE
887 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 07 | 1756-IA16 | 5 | REMOVE | 07 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.07 | // MCR5_R05:REMOVE:I.Data.07 SPARE
888 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 10 | 1756-IA16 | 5 | REMOVE | 08 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.08 | // MCR5_R05:REMOVE:I.Data.08 SPARE
889 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 11 | 1756-IA16 | 5 | REMOVE | 09 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.09 | // MCR5_R05:REMOVE:I.Data.09 SPARE
890 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 12 | 1756-IA16 | 5 | REMOVE | 10 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.10 | // MCR5_R05:REMOVE:I.Data.10 SPARE
891 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 13 | 1756-IA16 | 5 | REMOVE | 11 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.11 | // MCR5_R05:REMOVE:I.Data.11 SPARE
892 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 14 | 1756-IA16 | 5 | REMOVE | 12 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.12 | // MCR5_R05:REMOVE:I.Data.12 SPARE
893 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 15 | 1756-IA16 | 5 | REMOVE | 13 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.13 | // MCR5_R05:REMOVE:I.Data.13 SPARE
894 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 16 | 1756-IA16 | 5 | REMOVE | 14 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.14 | // MCR5_R05:REMOVE:I.Data.14 SPARE
895 | MCR5 R5G3M0 | 1771-IAD | 5 | 6 | 17 | 1756-IA16 | 5 | REMOVE | 15 |  |  |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:REMOVE:I.Data.15 | // MCR5_R05:REMOVE:I.Data.15 SPARE
896 | MCR5 R5G3M1 | 1771_OFE | 5 | 7 | CH1+ | 1756-OF8I | 5 | 10 | 0 | VF3016_SPT | N111:0 | VF | VF 301-6 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR5_R05 | O.Ch[ | OUTPUT | VF3016_SPT_IO | MCR5_R05:10:O.Ch[0].Data | MCR5_R05:10:O.Ch[0].Data:=VF3016_SPT_IO; //VF 301-6 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | _VF3016_SPT | P_VSD | Out_SpeedRef
897 | MCR5 R5G3M1 | 1771_OFE | 5 | 7 | CH2+ | 1756-OF8I | 5 | 10 | 1 | VF3015_SPT | N111.1 | VF | VF 301-5 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR5_R05 | O.Ch[ | OUTPUT | VF3015_SPT_IO | MCR5_R05:10:O.Ch[1].Data | MCR5_R05:10:O.Ch[1].Data:=VF3015_SPT_IO; //VF 301-5 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | _VF3015_SPT | P_VSD | Out_SpeedRef
898 | MCR5 R5G3M1 | 1771_OFE | 5 | 7 | CH3+ | 1756-OF8I | 5 | 10 | 2 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:10:O.Ch[2].Data | // MCR5_R05:10:O.Ch[2].Data SPARE
899 | MCR5 R5G3M1 | 1771_OFE | 5 | 7 | CH4+ | 1756-OF8I | 5 | 10 | 3 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:10:O.Ch[3].Data | // MCR5_R05:10:O.Ch[3].Data SPARE
900 | [5 empty] | 1756-OF8I | 5 | 10 | 4 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:10:O.Ch[4].Data | // MCR5_R05:10:O.Ch[4].Data SPARE
901 | [5 empty] | 1756-OF8I | 5 | 10 | 5 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:10:O.Ch[5].Data | // MCR5_R05:10:O.Ch[5].Data SPARE
902 | [5 empty] | 1756-OF8I | 5 | 10 | 6 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:10:O.Ch[6].Data | // MCR5_R05:10:O.Ch[6].Data SPARE
903 | [5 empty] | 1756-OF8I | 5 | 10 | 7 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:10:O.Ch[7].Data | // MCR5_R05:10:O.Ch[7].Data SPARE
904 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 00 | 1756-IA16 | 5 | 0 | 00 | VF3011_AUX | I:054/0 | VF | VF 301-1 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF3011_AUX_IO | MCR5_R05:0:I.Data.00 | VF3011_AUX_IO:= MCR5_R05:0:I.Data.00; //VF 301-1 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER |  | _VF83011_M01 | P_VSD | Sts_Running |  | Stone_Feed_TaskC | Task_C | _VF83011_M01
905 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 01 | 1756-IA16 | 5 | 0 | 01 | VF3012_AUX | I:054/1 | VF | VF 301-2 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF3012_AUX_IO | MCR5_R05:0:I.Data.01 | VF3012_AUX_IO:= MCR5_R05:0:I.Data.01; //VF 301-2 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER |  | _VF83012_M01 | P_VSD | Sts_Running |  | Stone_Feed_TaskC | Task_C | _VF83012_M01
906 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 02 | 1756-IA16 | 5 | 0 | 02 | VF3013_AUX | I:054/2 | VF | VF 301-3 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF3013_AUX_IO | MCR5_R05:0:I.Data.02 | VF3013_AUX_IO:= MCR5_R05:0:I.Data.02; //VF 301-3 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER |  | _VF3013_M01 | P_VSD | Sts_Running
907 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 03 | 1756-IA16 | 5 | 0 | 03 | VF3014_AUX | I:054/3 | VF | VF 301-4 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF3014_AUX_IO | MCR5_R05:0:I.Data.03 | VF3014_AUX_IO:= MCR5_R05:0:I.Data.03; //VF 301-4 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER |  | _VF3014_M01 | P_VSD | Sts_Running
908 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 04 | 1756-IA16 | 5 | 0 | 04 | VF3015_AUX | I:054/4 | VF | VF 301-5 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF3015_AUX_IO | MCR5_R05:0:I.Data.04 | VF3015_AUX_IO:= MCR5_R05:0:I.Data.04; //VF 301-5 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER |  | _VF3015_M01 | P_VSD | Sts_Running
909 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 05 | 1756-IA16 | 5 | 0 | 05 | VF3016_AUX | I:054/5 | VF | VF 301-6 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF3016_AUX_IO | MCR5_R05:0:I.Data.05 | VF3016_AUX_IO:= MCR5_R05:0:I.Data.05; //VF 301-6 VFD AUX FDBK STONE SYSTEM VIBRATORY FEEDER |  | _VF3016_M01 | P_VSD | Sts_Running
910 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 06 | 1756-IA16 | 5 | 0 | 06 |  | I:054/6 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.06 | // MCR5_R05:0:I.Data.06 SPARE
911 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 07 | 1756-IA16 | 5 | 0 | 07 |  | I:054/7 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.07 | // MCR5_R05:0:I.Data.07 SPARE
912 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 10 | 1756-IA16 | 5 | 0 | 08 |  | I:054/10 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.08 | // MCR5_R05:0:I.Data.08 SPARE
913 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 11 | 1756-IA16 | 5 | 0 | 09 |  | I:054/11 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.09 | // MCR5_R05:0:I.Data.09 SPARE
914 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 12 | 1756-IA16 | 5 | 0 | 10 |  | I:054/12 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.10 | // MCR5_R05:0:I.Data.10 SPARE
915 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 13 | 1756-IA16 | 5 | 0 | 11 |  | I:054/13 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.11 | // MCR5_R05:0:I.Data.11 SPARE
916 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 14 | 1756-IA16 | 5 | 0 | 12 |  | I:054/14 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.12 | // MCR5_R05:0:I.Data.12 SPARE
917 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 15 | 1756-IA16 | 5 | 0 | 13 |  | I:054/15 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.13 | // MCR5_R05:0:I.Data.13 SPARE
918 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 16 | 1756-IA16 | 5 | 0 | 14 |  | I:054/16 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.14 | // MCR5_R05:0:I.Data.14 SPARE
919 | MCR5 R5G4M0 | 1771-IAD | 5 | 8 | 17 | 1756-IA16 | 5 | 0 | 15 |  | I:054/17 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:0:I.Data.15 | // MCR5_R05:0:I.Data.15 SPARE
920 | MCR5 R5G4M1 | 1771_OFE | 5 | 9 | CH1+ | 1756-OF8I | 5 | 11 | 0 | VF3011_SPT | N111.20 | VF | VF 301-1 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR5_R05 | O.Ch[ | OUTPUT | VF3011_SPT_IO | MCR5_R05:11:O.Ch[0].Data | MCR5_R05:11:O.Ch[0].Data:=VF3011_SPT_IO; //VF 301-1 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | _VF3011_SPT | P_VSD | Out_SpeedRef
921 | MCR5 R5G4M1 | 1771_OFE | 5 | 9 | CH2+ | 1756-OF8I | 5 | 11 | 1 | VF3012_SPT | N111.21 | VF | VF 301-2 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR5_R05 | O.Ch[ | OUTPUT | VF3012_SPT_IO | MCR5_R05:11:O.Ch[1].Data | MCR5_R05:11:O.Ch[1].Data:=VF3012_SPT_IO; //VF 301-2 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | _VF3012_SPT | P_VSD | Out_SpeedRef
922 | MCR5 R5G4M1 | 1771_OFE | 5 | 9 | CH3+ | 1756-OF8I | 5 | 11 | 2 | VF3013_SPT | N111.22 | VF | VF 301-3 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR5_R05 | O.Ch[ | OUTPUT | VF3013_SPT_IO | MCR5_R05:11:O.Ch[2].Data | MCR5_R05:11:O.Ch[2].Data:=VF3013_SPT_IO; //VF 301-3 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | _VF3013_SPT | P_VSD | Out_SpeedRef
923 | MCR5 R5G4M1 | 1771_OFE | 5 | 9 | CH4+ | 1756-OF8I | 5 | 11 | 3 | VF3014_SPT | N111.23 | VF | VF 301-4 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR5_R05 | O.Ch[ | OUTPUT | VF3014_SPT_IO | MCR5_R05:11:O.Ch[3].Data | MCR5_R05:11:O.Ch[3].Data:=VF3014_SPT_IO; //VF 301-4 SPEED STONE SYSTEM VFD VIBRATORY FEEDER |  | _VF3014_SPT | P_VSD | Out_SpeedRef
924 | [5 empty] | 1756-OF8I | 5 | 11 | 4 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:11:O.Ch[4].Data | // MCR5_R05:11:O.Ch[4].Data SPARE
925 | [5 empty] | 1756-OF8I | 5 | 11 | 5 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:11:O.Ch[5].Data | // MCR5_R05:11:O.Ch[5].Data SPARE
926 | [5 empty] | 1756-OF8I | 5 | 11 | 6 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:11:O.Ch[6].Data | // MCR5_R05:11:O.Ch[6].Data SPARE
927 | [5 empty] | 1756-OF8I | 5 | 11 | 7 |  |  |  | SPARE | [10 empty] | MCR5_R05 | O.Ch[ | OUTPUT |  | MCR5_R05:11:O.Ch[7].Data | // MCR5_R05:11:O.Ch[7].Data SPARE
928 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 00 | 1756-IA16 | 5 | 1 | 00 | VF83011_SSA | I:055/0 |  | VF 8301-1 AUTO STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83011_SSA_IO | MCR5_R05:1:I.Data.00 | VF83011_SSA_IO:= MCR5_R05:1:I.Data.00; //VF 8301-1 AUTO STONE FEED VIBRATING FEEDER |  | _VF83011_SSA | P_DIn | Sts_PV | 0 | Stone_Feed_TaskC | Task_C | _VF8301
929 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 01 | 1756-IA16 | 5 | 1 | 01 | VF83011_AUX | I:055/1 | VF | VF 8301-1 AUX FDBK STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83011_AUX_IO | MCR5_R05:1:I.Data.01 | VF83011_AUX_IO:= MCR5_R05:1:I.Data.01; //VF 8301-1 AUX FDBK STONE FEED VIBRATING FEEDER |  | _VF83011_AUX | P_DIn | Sts_PV |  | Stone_Feed_TaskC | Task_C | _VF8301
930 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 02 | 1756-IA16 | 5 | 1 | 02 | VF83012_SSA | I:055/2 |  | VF 8301-2 AUTO STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83012_SSA_IO | MCR5_R05:1:I.Data.02 | VF83012_SSA_IO:= MCR5_R05:1:I.Data.02; //VF 8301-2 AUTO STONE FEED VIBRATING FEEDER |  | _VF83012_SSA | P_DIn | Sts_PV | 0 | Stone_Feed_TaskC | Task_C | _VF8301
931 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 03 | 1756-IA16 | 5 | 1 | 03 | VF83012_AUX | I:055/3 | VF | VF 8301-2 AUX FDBK STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83012_AUX_IO | MCR5_R05:1:I.Data.03 | VF83012_AUX_IO:= MCR5_R05:1:I.Data.03; //VF 8301-2 AUX FDBK STONE FEED VIBRATING FEEDER |  | _VF83012_AUX | P_DIn | Sts_PV |  | Stone_Feed_TaskC | Task_C | _VF8301
932 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 04 | 1756-IA16 | 5 | 1 | 04 | VF83013_SSA | I:055/4 |  | VF 8301-3 AUTO STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83013_SSA_IO | MCR5_R05:1:I.Data.04 | VF83013_SSA_IO:= MCR5_R05:1:I.Data.04; //VF 8301-3 AUTO STONE FEED VIBRATING FEEDER |  | _VF83013_SSA | P_DIn | Sts_PV | 0 | Stone_Feed_TaskC | Task_C | _VF8301
933 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 05 | 1756-IA16 | 5 | 1 | 05 | VF83013_AUX | I:055/5 | VF | VF 8301-3 AUX FDBK STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83013_AUX_IO | MCR5_R05:1:I.Data.05 | VF83013_AUX_IO:= MCR5_R05:1:I.Data.05; //VF 8301-3 AUX FDBK STONE FEED VIBRATING FEEDER |  | _VF83013_AUX | P_DIn | Sts_PV |  | Stone_Feed_TaskC | Task_C | _VF8301
934 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 06 | 1756-IA16 | 5 | 1 | 06 |  | I:055/6 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.06 | // MCR5_R05:1:I.Data.06 SPARE
935 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 07 | 1756-IA16 | 5 | 1 | 07 |  | I:055/7 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.07 | // MCR5_R05:1:I.Data.07 SPARE
936 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 10 | 1756-IA16 | 5 | 1 | 08 |  | I:055/10 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.08 | // MCR5_R05:1:I.Data.08 SPARE
937 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 11 | 1756-IA16 | 5 | 1 | 09 |  | I:055/11 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.09 | // MCR5_R05:1:I.Data.09 SPARE
938 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 12 | 1756-IA16 | 5 | 1 | 10 |  | I:055/12 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.10 | // MCR5_R05:1:I.Data.10 SPARE
939 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 13 | 1756-IA16 | 5 | 1 | 11 |  | I:055/13 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.11 | // MCR5_R05:1:I.Data.11 SPARE
940 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 14 | 1756-IA16 | 5 | 1 | 12 |  | I:055/14 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.12 | // MCR5_R05:1:I.Data.12 SPARE
941 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 15 | 1756-IA16 | 5 | 1 | 13 |  | I:055/15 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.13 | // MCR5_R05:1:I.Data.13 SPARE
942 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 16 | 1756-IA16 | 5 | 1 | 14 |  | I:055/16 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.14 | // MCR5_R05:1:I.Data.14 SPARE
943 | MCR5 R5G5M0 | 1771-IAD | 5 | 10 | 17 | 1756-IA16 | 5 | 1 | 15 |  | I:055/17 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:1:I.Data.15 | // MCR5_R05:1:I.Data.15 SPARE
944 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-0 | 1756-OA16I | 5 | 5 | 0 |  | O:055/0 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.0 | // MCR5_R05:5:O.Data.0 SPARE
945 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-1 | 1756-OA16I | 5 | 5 | 1 |  | O:055/1 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.1 | // MCR5_R05:5:O.Data.1 SPARE
946 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-2 | 1756-OA16I | 5 | 5 | 2 |  | O:055/2 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.2 | // MCR5_R05:5:O.Data.2 SPARE
947 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-3 | 1756-OA16I | 5 | 5 | 3 |  | O:055/3 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.3 | // MCR5_R05:5:O.Data.3 SPARE
948 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-4 | 1756-OA16I | 5 | 5 | 4 |  | O:055/4 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.4 | // MCR5_R05:5:O.Data.4 SPARE
949 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-5 | 1756-OA16I | 5 | 5 | 5 |  | O:055/5 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.5 | // MCR5_R05:5:O.Data.5 SPARE
950 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-6 | 1756-OA16I | 5 | 5 | 6 |  | O:055/6 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.6 | // MCR5_R05:5:O.Data.6 SPARE
951 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-7 | 1756-OA16I | 5 | 5 | 7 |  | O:055/7 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.7 | // MCR5_R05:5:O.Data.7 SPARE
952 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-10 | 1756-OA16I | 5 | 5 | 8 |  | O:055/10 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.8 | // MCR5_R05:5:O.Data.8 SPARE
953 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-11 | 1756-OA16I | 5 | 5 | 9 |  | O:055/11 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.9 | // MCR5_R05:5:O.Data.9 SPARE
954 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-12 | 1756-OA16I | 5 | 5 | 10 |  | O:055/12 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.10 | // MCR5_R05:5:O.Data.10 SPARE
955 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-13 | 1756-OA16I | 5 | 5 | 11 |  | O:055/13 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.11 | // MCR5_R05:5:O.Data.11 SPARE
956 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-14 | 1756-OA16I | 5 | 5 | 12 |  | O:055/14 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.12 | // MCR5_R05:5:O.Data.12 SPARE
957 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-15 | 1756-OA16I | 5 | 5 | 13 |  | O:055/15 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.13 | // MCR5_R05:5:O.Data.13 SPARE
958 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-16 | 1756-OA16I | 5 | 5 | 14 |  | O:055/16 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.14 | // MCR5_R05:5:O.Data.14 SPARE
959 | MCR5 R5G5M1 | 1771-ODD | 5 | 11 | L1-17 | 1756-OA16I | 5 | 5 | 15 |  | O:055/17 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:5:O.Data.15 | // MCR5_R05:5:O.Data.15 SPARE
960 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 00 | 1756-IA16 | 5 | 2 | 00 | FN2321_AUX | I:056/0 | FN | FN 2321 AUX FDBK KILN 2 DC FAN | [10 empty] | MCR5_R05 | I.Data | INPUT | FN2321_AUX_IO | MCR5_R05:2:I.Data.00 | FN2321_AUX_IO:= MCR5_R05:2:I.Data.00; //FN 2321 AUX FDBK KILN 2 DC FAN |  | _FN2321_M01 | P_Motor | Sts_Running | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _FN2321_M01 | Kill 2 Dust Collection
961 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 01 | 1756-IA16 | 5 | 2 | 01 | SC2316_1_AUX | I:056/1 | SC | SC 2316 FDBK KILN 2 SCREW CONVEYOR INTLK | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316_1_AUX_IO | MCR5_R05:2:I.Data.01 | SC2316_1_AUX_IO:= MCR5_R05:2:I.Data.01; //SC 2316 FDBK KILN 2 SCREW CONVEYOR INTLK |  | _SC2316_1_AUX | P_DIn | Sts_PV
962 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 02 | 1756-IA16 | 5 | 2 | 02 | SC2316A_1_AUX | I:056/2 | SC | SC 2316-A FDBK KILN 2 SCREW CONVEYOR INTLK | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316A_1_AUX_IO | MCR5_R05:2:I.Data.02 | SC2316A_1_AUX_IO:= MCR5_R05:2:I.Data.02; //SC 2316-A FDBK KILN 2 SCREW CONVEYOR INTLK |  | _SC2316A_1_AUX | P_DIn | Sts_PV
963 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 03 | 1756-IA16 | 5 | 2 | 03 | SC2316B_1_AUX | I:056/3 | SC | SC 2316-B FDBK KILN 2 SCREW CONVEYOR INTLK | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316B_1_AUX_IO | MCR5_R05:2:I.Data.03 | SC2316B_1_AUX_IO:= MCR5_R05:2:I.Data.03; //SC 2316-B FDBK KILN 2 SCREW CONVEYOR INTLK |  | _SC2316B_1_AUX | P_DIn | Sts_PV
964 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 04 | 1756-IA16 | 5 | 2 | 04 | SC2316C_1_AUX | I:056/4 | SC | SC 2316-C FDBK KILN 2 SCREW CONVEYOR INTLK | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316C_1_AUX_IO | MCR5_R05:2:I.Data.04 | SC2316C_1_AUX_IO:= MCR5_R05:2:I.Data.04; //SC 2316-C FDBK KILN 2 SCREW CONVEYOR INTLK |  | _SC2316C_1_AUX | P_DIn | Sts_PV
965 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 05 | 1756-IA16 | 5 | 2 | 05 | BE2317_1_AUX | I:056/5 | BE | BE 2317 FDBK KILN 2 BUCKET ELEVATOR | [10 empty] | MCR5_R05 | I.Data | INPUT | BE2317_1_AUX_IO | MCR5_R05:2:I.Data.05 | BE2317_1_AUX_IO:= MCR5_R05:2:I.Data.05; //BE 2317 FDBK KILN 2 BUCKET ELEVATOR |  | NOT USED | NOT USED | NOT USED
966 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 06 | 1756-IA16 | 5 | 2 | 06 | BN2318_LAH | I:056/6 |  | ALARM #2 DUST BIN HIGH LEVEL | [10 empty] | MCR5_R05 | I.Data | INPUT | BN2318_LAH_IO | MCR5_R05:2:I.Data.06 | BN2318_LAH_IO:= MCR5_R05:2:I.Data.06; //ALARM #2 DUST BIN HIGH LEVEL |  | _BN2318_LAH | P_DIn | Sts_PV | 0 | bar: Notes
967 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 07 | 1756-IA16 | 5 | 2 | 07 | KN2KD_ALM | I:056/7 |  | ALARM KILN 2 KILN DRIVE ROOM FIRE | [10 empty] | MCR5_R05 | I.Data | INPUT | KN2KD_ALM_IO | MCR5_R05:2:I.Data.07 | KN2KD_ALM_IO:= MCR5_R05:2:I.Data.07; //ALARM KILN 2 KILN DRIVE ROOM FIRE |  | _KN2KD_ALM | P_DIn | Sts_PV | bar: Notes
968 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 10 | 1756-IA16 | 5 | 2 | 08 | DG8330_ZS_KN1 | I:056/10 |  | DG 8330 LIMIT SWITCH STONE FEED DIVERTER GATE TO KILN 1 | [10 empty] | MCR5_R05 | I.Data | INPUT | DG8330_ZS_KN1_IO | MCR5_R05:2:I.Data.08 | DG8330_ZS_KN1_IO:= MCR5_R05:2:I.Data.08; //DG 8330 LIMIT SWITCH STONE FEED DIVERTER GATE TO KILN 1 |  | _DG8330 | P_D4SD | Sts_St0 | 1 | Stone_Feed_TaskC | Task_C | _DG8330 | Stone feed | bar: Notes
969 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 11 | 1756-IA16 | 5 | 2 | 09 | DG8330_ZS_KN2 | I:056/11 |  | DG 8330 LIMIT SWITCH STONE FEED DIVERTER GATE TO KILN 2 | [10 empty] | MCR5_R05 | I.Data | INPUT | DG8330_ZS_KN2_IO | MCR5_R05:2:I.Data.09 | DG8330_ZS_KN2_IO:= MCR5_R05:2:I.Data.09; //DG 8330 LIMIT SWITCH STONE FEED DIVERTER GATE TO KILN 2 |  | _DG8330 | P_D4SD | Sts_St1 | 1 | Stone_Feed_TaskC | Task_C | _DG8330 | Stone feed | bar: Notes
970 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 12 | 1756-IA16 | 5 | 2 | 10 | WS8329_WQS | I:056/12 |  | WS 8329 WS PULSE STONE FEED WEIGH SCALE | [10 empty] | MCR5_R05 | I.Data | INPUT | WS8329_WQS_IO | MCR5_R05:2:I.Data.10 | WS8329_WQS_IO:= MCR5_R05:2:I.Data.10; //WS 8329 WS PULSE STONE FEED WEIGH SCALE |  | _WS8329_WQS | P_DIn | Sts_PV |  | Stone_Feed_TaskB | Task_B | _WS8329_WQS
971 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 13 | 1756-IA16 | 5 | 2 | 11 | WS8303A_WQS | I:056/13 |  | WS 8303-A WS PULSE STONE FEED WEIGH SCALE | [10 empty] | MCR5_R05 | I.Data | INPUT | WS8303A_WQS_IO | MCR5_R05:2:I.Data.11 | WS8303A_WQS_IO:= MCR5_R05:2:I.Data.11; //WS 8303-A WS PULSE STONE FEED WEIGH SCALE |  | _WS8303A_WQS | P_DIn | Sts_PV
972 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 14 | 1756-IA16 | 5 | 2 | 12 | BE2317_PCD | I:056/14 |  | 2-317 PLUGGED CHUTE | [10 empty] | MCR5_R05 | I.Data | INPUT | BE2317_PCD_IO | MCR5_R05:2:I.Data.12 | BE2317_PCD_IO:= MCR5_R05:2:I.Data.12; //2-317 PLUGGED CHUTE |  | _BE2317_PCD | P_DIn | Sts_PV | 0 | bar: Notes
973 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 15 | 1756-IA16 | 5 | 2 | 13 | MCR5_ALM | I:056/15 |  | ALARM MCR 5 FIRE | [10 empty] | MCR5_R05 | I.Data | INPUT | MCR5_ALM_IO | MCR5_R05:2:I.Data.13 | MCR5_ALM_IO:= MCR5_R05:2:I.Data.13; //ALARM MCR 5 FIRE |  | _MCR5_ALM | P_DIn | Sts_PV
974 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 16 | 1756-IA16 | 5 | 2 | 14 | CAP_ALM | I:056/16 |  | ALARM CAPACITOR ROOM FIRE | [10 empty] | MCR5_R05 | I.Data | INPUT | CAP_ALM_IO | MCR5_R05:2:I.Data.14 | CAP_ALM_IO:= MCR5_R05:2:I.Data.14; //ALARM CAPACITOR ROOM FIRE |  | _CAP_ALM | P_DIn | Sts_PV | 0 | bar: Notes
975 | MCR5 R5G6M0 | 1771-IAD | 5 | 12 | 17 | 1756-IA16 | 5 | 2 | 15 |  | I:056/17 |  | SPARE | [10 empty] | MCR5_R05 | I.Data | INPUT |  | MCR5_R05:2:I.Data.15 | // MCR5_R05:2:I.Data.15 SPARE
976 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-0 | 1756-OA16I | 5 | 6 | 0 | SC2316_COIL | O:056/0 | SC | SC 2316 RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | O.Data | OUTPUT | SC2316_COIL_IO | MCR5_R05:6:O.Data.0 | MCR5_R05:6:O.Data.0:=SC2316_COIL_IO; //SC 2316 RUN KILN 2 SCREW CONVEYOR |  | _SC2316_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316_M01
977 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-1 | 1756-OA16I | 5 | 6 | 1 | SC2316A_COIL | O:056/1 | SC | SC 2316-A RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | O.Data | OUTPUT | SC2316A_COIL_IO | MCR5_R05:6:O.Data.1 | MCR5_R05:6:O.Data.1:=SC2316A_COIL_IO; //SC 2316-A RUN KILN 2 SCREW CONVEYOR |  | _SC2316A_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316A_M01
978 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-2 | 1756-OA16I | 5 | 6 | 2 | SC2316B_COIL | O:056/2 | SC | SC 2316-B RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | O.Data | OUTPUT | SC2316B_COIL_IO | MCR5_R05:6:O.Data.2 | MCR5_R05:6:O.Data.2:=SC2316B_COIL_IO; //SC 2316-B RUN KILN 2 SCREW CONVEYOR |  | _SC2316B_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316B_M01
979 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-3 | 1756-OA16I | 5 | 6 | 3 | SC2316C_COIL | O:056/3 | SC | SC 2316-C RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | O.Data | OUTPUT | SC2316C_COIL_IO | MCR5_R05:6:O.Data.3 | MCR5_R05:6:O.Data.3:=SC2316C_COIL_IO; //SC 2316-C RUN KILN 2 SCREW CONVEYOR |  | _SC2316C_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316C_M01
980 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-4 | 1756-OA16I | 5 | 6 | 4 | BE2317_COIL | O:056/4 | BE | BE 2317 RUN KILN 2 BUCKET ELEVATOR | [10 empty] | MCR5_R05 | O.Data | OUTPUT | BE2317_COIL_IO | MCR5_R05:6:O.Data.4 | MCR5_R05:6:O.Data.4:=BE2317_COIL_IO; //BE 2317 RUN KILN 2 BUCKET ELEVATOR |  | _BE2317_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _BE2317_M01 | Kill 2 Dust Collection
981 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-5 | 1756-OA16I | 5 | 6 | 5 | RA2319_COIL | O:056/5 | RA | RA 2319 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5_R05 | O.Data | OUTPUT | RA2319_COIL_IO | MCR5_R05:6:O.Data.5 | MCR5_R05:6:O.Data.5:=RA2319_COIL_IO; //RA 2319 RUN KILN 2 ROTARY AIRLOCK |  | _RA2319_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA2319_M01
982 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-6 | 1756-OA16I | 5 | 6 | 6 | FN2321_COIL | O:056/6 | FN | FN 2321 RUN KILN 2 DC FAN | [10 empty] | MCR5_R05 | O.Data | OUTPUT | FN2321_COIL_IO | MCR5_R05:6:O.Data.6 | MCR5_R05:6:O.Data.6:=FN2321_COIL_IO; //FN 2321 RUN KILN 2 DC FAN |  | _FN2321_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _FN2321_M01 | Kill 2 Dust Collection
983 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-7 | 1756-OA16I | 5 | 6 | 7 |  | O:056/7 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:6:O.Data.7 | // MCR5_R05:6:O.Data.7 SPARE
984 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-10 | 1756-OA16I | 5 | 6 | 8 | DG8330_COIL_KN1 | O:056/10 | DG | DG 8330 RUN STONE FEED DIVERTER GATE TO KILN 1 | [10 empty] | MCR5_R05 | O.Data | OUTPUT | DG8330_COIL_KN1_IO | MCR5_R05:6:O.Data.8 | MCR5_R05:6:O.Data.8:=DG8330_COIL_KN1_IO; //DG 8330 RUN STONE FEED DIVERTER GATE TO KILN 1 |  | _DG8330 | P_D4SD | PCmd_St0 | 1 | Stone_Feed_TaskC | Task_C | _DG8330 | Stone feed | bar: Notes
985 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-11 | 1756-OA16I | 5 | 6 | 9 | DG8330_COIL_KN2 | O:056/11 | DG | DG 8330 RUN STONE FEED DIVERTER GATE TO KILN 2 | [10 empty] | MCR5_R05 | O.Data | OUTPUT | DG8330_COIL_KN2_IO | MCR5_R05:6:O.Data.9 | MCR5_R05:6:O.Data.9:=DG8330_COIL_KN2_IO; //DG 8330 RUN STONE FEED DIVERTER GATE TO KILN 2 |  | _DG8330 | P_D4SD | PCmd_St1 | 1 | Stone_Feed_TaskC | Task_C | _DG8330 | Stone feed | bar: Notes
986 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-12 | 1756-OA16I | 5 | 6 | 10 | VF83011_COIL | O:056/12 | VF | VF 8301-1 RUN STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | O.Data | OUTPUT | VF83011_COIL_IO | MCR5_R05:6:O.Data.10 | MCR5_R05:6:O.Data.10:=VF83011_COIL_IO; //VF 8301-1 RUN STONE FEED VIBRATING FEEDER |  | _VF83011_M01 | P_VSD | PCmd_StartFwd |  | Stone_Feed_TaskC | Task_C | _VF83011_M01
987 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-13 | 1756-OA16I | 5 | 6 | 11 | VF83012_COIL | O:056/13 | VF | VF 8301-2 RUN STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | O.Data | OUTPUT | VF83012_COIL_IO | MCR5_R05:6:O.Data.11 | MCR5_R05:6:O.Data.11:=VF83012_COIL_IO; //VF 8301-2 RUN STONE FEED VIBRATING FEEDER |  | _VF83012_M01 | P_VSD | PCmd_StartFwd |  | Stone_Feed_TaskC | Task_C | _VF83012_M01
988 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-14 | 1756-OA16I | 5 | 6 | 12 | VF83013_COIL | O:056/14 | VF | VF 8301-3 RUN STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | O.Data | OUTPUT | VF83013_COIL_IO | MCR5_R05:6:O.Data.12 | MCR5_R05:6:O.Data.12:=VF83013_COIL_IO; //VF 8301-3 RUN STONE FEED VIBRATING FEEDER |  | _VF83013_M01 | P_VSD | PCmd_StartFwd |  | Stone_Feed_TaskC | Task_C | _VF83013_M01
989 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-15 | 1756-OA16I | 5 | 6 | 13 |  | O:056/15 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:6:O.Data.13 | // MCR5_R05:6:O.Data.13 SPARE
990 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-16 | 1756-OA16I | 5 | 6 | 14 |  | O:056/16 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:6:O.Data.14 | // MCR5_R05:6:O.Data.14 SPARE
991 | MCR5 R5G6M1 | 1771-ODD | 5 | 13 | L1-17 | 1756-OA16I | 5 | 6 | 15 |  | O:056/17 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:6:O.Data.15 | // MCR5_R05:6:O.Data.15 SPARE
992 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 00 | 1756-IA16 | 5 | 3 | 00 | BL4460_AUX | I:057/0 | PC | BL 4460 FDBK DUST BLENDING BLOWER | [10 empty] | MCR5_R05 | I.Data | INPUT | BL4460_AUX_IO | MCR5_R05:3:I.Data.00 | BL4460_AUX_IO:= MCR5_R05:3:I.Data.00; //BL 4460 FDBK DUST BLENDING BLOWER |  | _BL4460_AUX | P_DIn | Sts_PV | 0 | bar: Notes
993 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 01 | 1756-IA16 | 5 | 3 | 01 | PM4461_AUX | I:057/1 |  | PM 4461 DUST BLENDING SCREW PUMP | [10 empty] | MCR5_R05 | I.Data | INPUT | PM4461_AUX_IO | MCR5_R05:3:I.Data.01 | PM4461_AUX_IO:= MCR5_R05:3:I.Data.01; //PM 4461 DUST BLENDING SCREW PUMP |  | _PM4461_M01 | P_Motor | Sts_Running |  | Dust_Blending_TaskC | Task_C | _PM4461_M01 | bar: Notes
994 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 02 | 1756-IA16 | 5 | 3 | 02 | RA2319_AUX | I:057/2 | RA | RA 2319 FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5_R05 | I.Data | INPUT | RA2319_AUX_IO | MCR5_R05:3:I.Data.02 | RA2319_AUX_IO:= MCR5_R05:3:I.Data.02; //RA 2319 FDBK KILN 2 ROTARY AIRLOCK |  | _RA2319_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA2319_M01
995 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 03 | 1756-IA16 | 5 | 3 | 03 | BC8303A_MS | I:057/3 |  | BC 8303-A MOTION SWITCH STONE FEED BELT CONVEYOR | [10 empty] | MCR5_R05 | I.Data | INPUT | BC8303A_MS_IO | MCR5_R05:3:I.Data.03 | BC8303A_MS_IO:= MCR5_R05:3:I.Data.03; //BC 8303-A MOTION SWITCH STONE FEED BELT CONVEYOR |  | _BC8303A_MS | P_DIn | Sts_PV | 1 | Stone_Feed_TaskB | Task_B | _BC8303A_MS | Stone feed | bar: Notes
996 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 04 | 1756-IA16 | 5 | 3 | 04 | VF83015_AUX | I:057/4 | VF | VF 8301-5 AUX FDBK STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83015_AUX_IO | MCR5_R05:3:I.Data.04 | VF83015_AUX_IO:= MCR5_R05:3:I.Data.04; //VF 8301-5 AUX FDBK STONE FEED VIBRATING FEEDER |  | _VF83015_AUX | P_DIn | Sts_PV |  | Stone_Feed_TaskC | Task_C | _VF8301
997 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 05 | 1756-IA16 | 5 | 3 | 05 | VF83016_AUX | I:057/5 | VF | VF 8301-6 AUX FDBK STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83016_AUX_IO | MCR5_R05:3:I.Data.05 | VF83016_AUX_IO:= MCR5_R05:3:I.Data.05; //VF 8301-6 AUX FDBK STONE FEED VIBRATING FEEDER |  | _VF83015_AUX | P_DIn | Sts_PV |  | Stone_Feed_TaskC | Task_C | _VF8301
998 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 06 | 1756-IA16 | 5 | 3 | 06 | VF83014_AUX | I:057/6 | VF | VF 8301-4 AUX FDBK STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | I.Data | INPUT | VF83014_AUX_IO | MCR5_R05:3:I.Data.06 | VF83014_AUX_IO:= MCR5_R05:3:I.Data.06; //VF 8301-4 AUX FDBK STONE FEED VIBRATING FEEDER |  | _VF83014_AUX | P_DIn | Sts_PV |  | Stone_Feed_TaskC | Task_C | _VF8301
999 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 07 | 1756-IA16 | 5 | 3 | 07 | BC8303A_AUX | I:057/7 | BC | BC 8303-A AUX FDBK STONE FEED BELT CONVEYOR | [10 empty] | MCR5_R05 | I.Data | INPUT | BC8303A_AUX_IO | MCR5_R05:3:I.Data.07 | BC8303A_AUX_IO:= MCR5_R05:3:I.Data.07; //BC 8303-A AUX FDBK STONE FEED BELT CONVEYOR |  | _BC8303A_M01 | P_Motor | Sts_Running | 1 | Stone_Feed_TaskC | Task_C | _BC8303A_M01 | Stone feed
1000 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 10 | 1756-IA16 | 5 | 3 | 08 | BE2317_2_AUX | I:057/10 | BE | BE 2317 FDBK KILN 2 BUCKET ELEVATOR | [10 empty] | MCR5_R05 | I.Data | INPUT | BE2317_2_AUX_IO | MCR5_R05:3:I.Data.08 | BE2317_2_AUX_IO:= MCR5_R05:3:I.Data.08; //BE 2317 FDBK KILN 2 BUCKET ELEVATOR |  | _BE2317_MS | P_DIn | Sts_PV | 1 | Kiln2_Dust_Collection_TaskB | Task_B | _BE2317_MS | Kill 2 Dust Collection
1001 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 11 | 1756-IA16 | 5 | 3 | 09 | KD1308_1_ALM | I:057/11 |  | KD 1308 ALARM KILN 1 LUBE FAILURE | [10 empty] | MCR5_R05 | I.Data | INPUT | KD1308_1_ALM_IO | MCR5_R05:3:I.Data.09 | KD1308_1_ALM_IO:= MCR5_R05:3:I.Data.09; //KD 1308 ALARM KILN 1 LUBE FAILURE |  | _KD1308_1_ALM | P_DIn | Sts_PV
1002 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 12 | 1756-IA16 | 5 | 3 | 10 | KD1308_2_ALM | I:057/12 |  | KD 1308 ALARM KILN 1 LUBE FAILURE | [10 empty] | MCR5_R05 | I.Data | INPUT | KD1308_2_ALM_IO | MCR5_R05:3:I.Data.10 | KD1308_2_ALM_IO:= MCR5_R05:3:I.Data.10; //KD 1308 ALARM KILN 1 LUBE FAILURE |  | _KD1308_2_ALM | P_DIn | Sts_PV
1003 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 13 | 1756-IA16 | 5 | 3 | 11 | SC2316_2_AUX | I:057/13 | SC | SC 2316 AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316_2_AUX_IO | MCR5_R05:3:I.Data.11 | SC2316_2_AUX_IO:= MCR5_R05:3:I.Data.11; //SC 2316 AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316_2_AUX | P_Motor | Sts_Running
1004 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 14 | 1756-IA16 | 5 | 3 | 12 | SC2316A_2_AUX | I:057/14 | SC | SC 2316-A AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316A_2_AUX_IO | MCR5_R05:3:I.Data.12 | SC2316A_2_AUX_IO:= MCR5_R05:3:I.Data.12; //SC 2316-A AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316A_2_AUX | P_Motor | Sts_Running
1005 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 15 | 1756-IA16 | 5 | 3 | 13 | SC2316B_2_AUX | I:057/15 | SC | SC 2316-B AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316B_2_AUX_IO | MCR5_R05:3:I.Data.13 | SC2316B_2_AUX_IO:= MCR5_R05:3:I.Data.13; //SC 2316-B AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316B_2_AUX | P_Motor | Sts_Running
1006 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 16 | 1756-IA16 | 5 | 3 | 14 | SC2316C_2_AUX | I:057/16 | SC | SC 2316-C AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5_R05 | I.Data | INPUT | SC2316C_2_AUX_IO | MCR5_R05:3:I.Data.14 | SC2316C_2_AUX_IO:= MCR5_R05:3:I.Data.14; //SC 2316-C AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316C_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316C_M01
1007 | MCR5 R5G7M0 | 1771-IAD | 5 | 14 | 17 | 1756-IA16 | 5 | 3 | 15 | BE2317_3_AUX | I:057/17 | BE | BE 2317 AUX FDBK KILN 2 BUCKET ELEVATOR | [10 empty] | MCR5_R05 | I.Data | INPUT | BE2317_3_AUX_IO | MCR5_R05:3:I.Data.15 | BE2317_3_AUX_IO:= MCR5_R05:3:I.Data.15; //BE 2317 AUX FDBK KILN 2 BUCKET ELEVATOR |  | _BE2317_M01 | P_Motor | Sts_Running | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _BE2317_M01 | Kill 2 Dust Collection
1008 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-0 | 1756-OA16I | 5 | 7 | 0 | PC4460_COIL | O:057/0 | PC | PC 4460 RUN DUST BLENDING FAN | [10 empty] | MCR5_R05 | O.Data | OUTPUT | PC4460_COIL_IO | MCR5_R05:7:O.Data.0 | MCR5_R05:7:O.Data.0:=PC4460_COIL_IO; //PC 4460 RUN DUST BLENDING FAN |  | _PC4460_M01 | P_Motor | PCmd_On |  | Dust_Blending_TaskC | Task_C | _PC4460_M01
1009 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-1 | 1756-OA16I | 5 | 7 | 1 | PM4461_COIL | O:057/1 | PM | PM 4461 RUN DUST BLENDING SCREW PUMP | [10 empty] | MCR5_R05 | O.Data | OUTPUT | PM4461_COIL_IO | MCR5_R05:7:O.Data.1 | MCR5_R05:7:O.Data.1:=PM4461_COIL_IO; //PM 4461 RUN DUST BLENDING SCREW PUMP |  | _PM4461_M01 | P_Motor | PCmd_Start |  | Dust_Blending_TaskC | Task_C | _PM4461_M01
1010 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-2 | 1756-OA16I | 5 | 7 | 2 |  | O:057/2 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:7:O.Data.2 | // MCR5_R05:7:O.Data.2 SPARE | bar: Notes to EU
1011 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-3 | 1756-OA16I | 5 | 7 | 3 | SG4462_SV | O:057/3 |  | SG 4462 OPEN DUST BLENDING KNIFE GATE SOLENOID | [10 empty] | MCR5_R05 | O.Data | OUTPUT | SG4462_SV_IO | MCR5_R05:7:O.Data.3 | MCR5_R05:7:O.Data.3:=SG4462_SV_IO; //SG 4462 OPEN DUST BLENDING KNIFE GATE SOLENOID |  | _SG4462_SV | P_ValveSO | Out |  | Dust_Blending_TaskC | Task_C | _SG4462 | bar: Notes
1012 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-4 | 1756-OA16I | 5 | 7 | 4 | VF83015_COIL | O:057/4 | VF | VF 8301-5 RUN STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | O.Data | OUTPUT | VF83015_COIL_IO | MCR5_R05:7:O.Data.4 | MCR5_R05:7:O.Data.4:=VF83015_COIL_IO; //VF 8301-5 RUN STONE FEED VIBRATING FEEDER |  | _VF83015_M01 | P_VSD | PCmd_StartFwd |  | Stone_Feed_TaskC | Task_C | _VF83015_M01
1013 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-5 | 1756-OA16I | 5 | 7 | 5 | VF83016_COIL | O:057/5 | VF | VF 8301-6 RUN STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | O.Data | OUTPUT | VF83016_COIL_IO | MCR5_R05:7:O.Data.5 | MCR5_R05:7:O.Data.5:=VF83016_COIL_IO; //VF 8301-6 RUN STONE FEED VIBRATING FEEDER |  | _VF83016_M01 | P_VSD | PCmd_StartFwd |  | Stone_Feed_TaskC | Task_C | _VF83016_M01
1014 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-6 | 1756-OA16I | 5 | 7 | 6 | VF83014_COIL | O:057/6 | VF | VF 8301-4 RUN STONE FEED VIBRATING FEEDER | [10 empty] | MCR5_R05 | O.Data | OUTPUT | VF83014_COIL_IO | MCR5_R05:7:O.Data.6 | MCR5_R05:7:O.Data.6:=VF83014_COIL_IO; //VF 8301-4 RUN STONE FEED VIBRATING FEEDER |  | _VF83014_M01 | P_VSD | PCmd_StartFwd |  | Stone_Feed_TaskC | Task_C | _VF83014_M01
1015 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-7 | 1756-OA16I | 5 | 7 | 7 | BC8303A_COIL | O:057/7 | BC | BC 8303-A RUN STONE FEED BELT CONVEYOR | [10 empty] | MCR5_R05 | O.Data | OUTPUT | BC8303A_COIL_IO | MCR5_R05:7:O.Data.7 | MCR5_R05:7:O.Data.7:=BC8303A_COIL_IO; //BC 8303-A RUN STONE FEED BELT CONVEYOR |  | _BC8303A_M01 | P_Motor | PCmd_Start | 1 | Stone_Feed_TaskC | Task_C | _BC8303A_M01 | Stone feed
1016 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-10 | 1756-OA16I | 5 | 7 | 8 |  | O:057/10 |  | SPARE | [10 empty] | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:7:O.Data.8 | // MCR5_R05:7:O.Data.8 SPARE
1017 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-11 | 1756-OA16I | 5 | 7 | 9 | KD1308_LUBE_SV | O:057/11 | TBD | KILN DRIVE ON START KILN 1 DRIVE LUBE SYSTEM RELAY | [10 empty] | MCR5_R05 | O.Data | OUTPUT | KD1308_LUBE_SV_IO | MCR5_R05:7:O.Data.9 | MCR5_R05:7:O.Data.9:=KD1308_LUBE_SV_IO; //KILN DRIVE ON START KILN 1 DRIVE LUBE SYSTEM RELAY |  | _KD1308_LUBE_SV | P_Dout | PCmd_On | bar: Notes
1018 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-12 | 1756-OA16I | 5 | 7 | 10 |  | O:057/12 | TBD | INITIATE KILN 1 OPACITY CALIBRATION (ESC) |  | Notes: LOCATED IN CEMS. IS THIS NEEDED?; EU: TBD | MCR5_R05 | O.Data | OUTPUT |  | MCR5_R05:7:O.Data.10 | // MCR5_R05:7:O.Data.10 INITIATE KILN 1 OPACITY CALIBRATION (ESC)
1019 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-13 | 1756-OA16I | 5 | 7 | 11 | FN1331_AUX_DO | O:057/13 | FN | FN 1331 FDBK KILN 1 VENT FAN (ESC) |  | Notes: LOOK AT PHYSICAL WIRING | MCR5_R05 | O.Data | OUTPUT | FN1331_AUX_DO_IO | MCR5_R05:7:O.Data.11 | MCR5_R05:7:O.Data.11:=FN1331_AUX_DO_IO; //FN 1331 FDBK KILN 1 VENT FAN (ESC) |  | NA | NA | NA
1020 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-14 | 1756-OA16I | 5 | 7 | 12 | BM1602_AUX_DO | O:057/14 | BM | BM 1602 FDBK KILN 1 COAL MILL (ESC) |  | Notes: WHY IS THIS NEEDED? AUX FEEDBACK IS IN MCR 1?; EU: TBD | MCR5_R05 | O.Data | OUTPUT | BM1602_AUX_DO_IO | MCR5_R05:7:O.Data.12 | MCR5_R05:7:O.Data.12:=BM1602_AUX_DO_IO; //BM 1602 FDBK KILN 1 COAL MILL (ESC) |  | NA | NA | NA | 0
1021 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-15 | 1756-OA16I | 5 | 7 | 13 | SPARE | O:057/15 | TBD | INITIATE KILN 2 OPACITY CALIBRATION (ESC) |  | Notes: LOCATED IN CEMS. IS THIS NEEDED?; EU: TBD | MCR5_R05 | O.Data | OUTPUT | SPARE_IO | MCR5_R05:7:O.Data.13 | MCR5_R05:7:O.Data.13:=SPARE_IO; //INITIATE KILN 2 OPACITY CALIBRATION (ESC) |  | NA | NA | NA
1022 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-16 | 1756-OA16I | 5 | 7 | 14 | FN2314_AUX_DO | O:057/16 | FN | FN 2314 FDBK KILN 2 ID FAN (ESC) |  | Notes: FN 2314 ON ETHERNET. IS THIS NEEDED; EU: TBD | MCR5_R05 | O.Data | OUTPUT | FN2314_AUX_DO_IO | MCR5_R05:7:O.Data.14 | MCR5_R05:7:O.Data.14:=FN2314_AUX_DO_IO; //FN 2314 FDBK KILN 2 ID FAN (ESC) |  | NA | NA | NA
1023 | MCR5 R5G7M1 | 1771-ODD | 5 | 15 | L1-17 | 1756-OA16I | 5 | 7 | 15 | BM2602_AUX_DO | O:057/17 | BM | BM 2602 FDBK KILN 2 COAL MILL (ESC) |  | Notes: WHY IS THIS NEEDED? AUX FEEDBACK IN MCR 4; EU: TBD | MCR5_R05 | O.Data | OUTPUT | BM2602_AUX_DO_IO | MCR5_R05:7:O.Data.15 | MCR5_R05:7:O.Data.15:=BM2602_AUX_DO_IO; //BM 2602 FDBK KILN 2 COAL MILL (ESC) |  | NA | NA | NA
1024 | R6G0M0 | 1771-IAD | 6 | 0 | 00 | 1756-IA16 | 6 | 0 | 00 | KN2PNY_SLOCK_DI | I:060/0 |  | K2 PONY CHAIN BOX SAFETY INTERLOCK | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | KN2PNY_SLOCK_DI_IO | K2_DriveRoom_R06:0:I.Data.00 | KN2PNY_SLOCK_DI_IO:= K2_DriveRoom_R06:0:I.Data.00; //K2 PONY CHAIN BOX SAFETY INTERLOCK |  | _KN2PNY_SLOCK_DI | P_DIn | Sts_PV | bar: Notes
1025 | R6G0M0 | 1771-IAD | 6 | 0 | 01 | 1756-IA16 | 6 | 0 | 01 | KL2KD_YZ | I:060/1 |  | K2 KILN DRIVE ESTOP | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | KL2KD_YZ_IO | K2_DriveRoom_R06:0:I.Data.01 | KL2KD_YZ_IO:= K2_DriveRoom_R06:0:I.Data.01; //K2 KILN DRIVE ESTOP |  | _KL2KD_YZ | P_DIn | Sts_PV
1026 | R6G0M0 | 1771-IAD | 6 | 0 | 02 | 1756-IA16 | 6 | 0 | 02 |  | I:060/2 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.02 | // K2_DriveRoom_R06:0:I.Data.02 SPARE
1027 | R6G0M0 | 1771-IAD | 6 | 0 | 03 | 1756-IA16 | 6 | 0 | 03 |  | I:060/3 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.03 | // K2_DriveRoom_R06:0:I.Data.03 SPARE
1028 | R6G0M0 | 1771-IAD | 6 | 0 | 04 | 1756-IA16 | 6 | 0 | 04 |  | I:060/4 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.04 | // K2_DriveRoom_R06:0:I.Data.04 SPARE
1029 | R6G0M0 | 1771-IAD | 6 | 0 | 05 | 1756-IA16 | 6 | 0 | 05 | KD2308A_RES_DI | I:060/5 |  | KD 2-308-A BRAKE RESISTOR HI TEMP (NO) KILN 2 KILN DRIVE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | KD2308A_RES_DI_IO | K2_DriveRoom_R06:0:I.Data.05 | KD2308A_RES_DI_IO:= K2_DriveRoom_R06:0:I.Data.05; //KD 2-308-A BRAKE RESISTOR HI TEMP (NO) KILN 2 KILN DRIVE |  | _KD2308A_RES_DI | P_DIn | Sts_PV | bar: Notes
1030 | R6G0M0 | 1771-IAD | 6 | 0 | 06 | 1756-IA16 | 6 | 0 | 06 | FN2308A_EY | I:060/6 |  | FN 2-308-A Overloads Not Tripped Kiln 2 Motor Blower Fan | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | FN2308A_EY_IO | K2_DriveRoom_R06:0:I.Data.06 | FN2308A_EY_IO:= K2_DriveRoom_R06:0:I.Data.06; //FN 2-308-A Overloads Not Tripped Kiln 2 Motor Blower Fan |  | _FN2308A_EY | P_DIn | Sts_PV
1031 | R6G0M0 | 1771-IAD | 6 | 0 | 07 | 1756-IA16 | 6 | 0 | 07 | FN2308A_2_AUX | I:060/7 |  | FN 2-308-A Aux Contact Kiln 2 Motor Blower Fan | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | FN2308A_2_AUX_IO | K2_DriveRoom_R06:0:I.Data.07 | FN2308A_2_AUX_IO:= K2_DriveRoom_R06:0:I.Data.07; //FN 2-308-A Aux Contact Kiln 2 Motor Blower Fan |  | _FN2308A_M01 | P_VSD | Sts_Running |  | Kiln2_Main_TaskC | Task_C | _FN2308A_M01
1032 | R6G0M0 | 1771-IAD | 6 | 0 | 10 | 1756-IA16 | 6 | 0 | 08 |  | I:060/10 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.08 | // K2_DriveRoom_R06:0:I.Data.08 SPARE
1033 | R6G0M0 | 1771-IAD | 6 | 0 | 11 | 1756-IA16 | 6 | 0 | 09 |  | I:060/11 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.09 | // K2_DriveRoom_R06:0:I.Data.09 SPARE
1034 | R6G0M0 | 1771-IAD | 6 | 0 | 12 | 1756-IA16 | 6 | 0 | 10 |  | I:060/12 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.10 | // K2_DriveRoom_R06:0:I.Data.10 SPARE
1035 | R6G0M0 | 1771-IAD | 6 | 0 | 13 | 1756-IA16 | 6 | 0 | 11 |  | I:060/13 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.11 | // K2_DriveRoom_R06:0:I.Data.11 SPARE
1036 | R6G0M0 | 1771-IAD | 6 | 0 | 14 | 1756-IA16 | 6 | 0 | 12 |  | I:060/14 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT |  | K2_DriveRoom_R06:0:I.Data.12 | // K2_DriveRoom_R06:0:I.Data.12 SPARE
1037 | R6G0M0 | 1771-IAD | 6 | 0 | 15 | 1756-IA16 | 6 | 0 | 13 | KD2308B_RES_DI | I:060/15 |  | KD 2-308-B BRAKE RESISTOR HI TEMP (NO) KILN 2 KILN DRIVE | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | KD2308B_RES_DI_IO | K2_DriveRoom_R06:0:I.Data.13 | KD2308B_RES_DI_IO:= K2_DriveRoom_R06:0:I.Data.13; //KD 2-308-B BRAKE RESISTOR HI TEMP (NO) KILN 2 KILN DRIVE |  | _KD2308B_RES_DI | P_DIn | Sts_PV | bar: Notes
1038 | R6G0M0 | 1771-IAD | 6 | 0 | 16 | 1756-IA16 | 6 | 0 | 14 | FN2308B_EY | I:060/16 |  | FN 2-308-B Overloads Not Tripped Kiln 2 Motor Blower Fan | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | FN2308B_EY_IO | K2_DriveRoom_R06:0:I.Data.14 | FN2308B_EY_IO:= K2_DriveRoom_R06:0:I.Data.14; //FN 2-308-B Overloads Not Tripped Kiln 2 Motor Blower Fan |  | _FN2308B_EY | P_DIn | Sts_PV
1039 | R6G0M0 | 1771-IAD | 6 | 0 | 17 | 1756-IA16 | 6 | 0 | 15 | FN2308B_AUX | I:060/17 |  | FN 2-308-B Aux Contact Kiln 2 Motor Blower Fan | [10 empty] | K2_DriveRoom_R06 | I.Data | INPUT | FN2308B_AUX_IO | K2_DriveRoom_R06:0:I.Data.15 | FN2308B_AUX_IO:= K2_DriveRoom_R06:0:I.Data.15; //FN 2-308-B Aux Contact Kiln 2 Motor Blower Fan |  | _FN2308B_M01 | P_Motor | Sts_Running
1040 | R6G1M0 | 1771-ODD | 6 | 1 | L1-0 | 1756-OA16I | 6 | 1 | 0 |  | O:061/0 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.0 | // K2_DriveRoom_R06:1:O.Data.0 SPARE
1041 | R6G1M0 | 1771-ODD | 6 | 1 | L1-1 | 1756-OA16I | 6 | 1 | 1 |  | O:061/1 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.1 | // K2_DriveRoom_R06:1:O.Data.1 SPARE
1042 | R6G1M0 | 1771-ODD | 6 | 1 | L1-2 | 1756-OA16I | 6 | 1 | 2 |  | O:061/2 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.2 | // K2_DriveRoom_R06:1:O.Data.2 SPARE
1043 | R6G1M0 | 1771-ODD | 6 | 1 | L1-3 | 1756-OA16I | 6 | 1 | 3 |  | O:061/3 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.3 | // K2_DriveRoom_R06:1:O.Data.3 SPARE
1044 | R6G1M0 | 1771-ODD | 6 | 1 | L1-4 | 1756-OA16I | 6 | 1 | 4 |  | O:061/4 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.4 | // K2_DriveRoom_R06:1:O.Data.4 SPARE
1045 | R6G1M0 | 1771-ODD | 6 | 1 | L1-5 | 1756-OA16I | 6 | 1 | 5 |  | O:061/5 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.5 | // K2_DriveRoom_R06:1:O.Data.5 SPARE
1046 | R6G1M0 | 1771-ODD | 6 | 1 | L1-6 | 1756-OA16I | 6 | 1 | 6 |  | O:061/6 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.6 | // K2_DriveRoom_R06:1:O.Data.6 SPARE
1047 | R6G1M0 | 1771-ODD | 6 | 1 | L1-7 | 1756-OA16I | 6 | 1 | 7 |  | O:061/7 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.7 | // K2_DriveRoom_R06:1:O.Data.7 SPARE
1048 | R6G1M0 | 1771-ODD | 6 | 1 | L1-10 | 1756-OA16I | 6 | 1 | 8 | FN2308A_COIL | O:061/10 | FN | FN 2-308-A Run Kiln 2 DRIVE MOTOR COOLING FAN NORTH | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT | FN2308A_COIL_IO | K2_DriveRoom_R06:1:O.Data.8 | K2_DriveRoom_R06:1:O.Data.8:=FN2308A_COIL_IO; //FN 2-308-A Run Kiln 2 DRIVE MOTOR COOLING FAN NORTH |  | _FN2308A_M01 | P_VSD | PCmd_Start |  | Kiln2_Main_TaskC | Task_C | _FN2308A_M01
1049 | R6G1M0 | 1771-ODD | 6 | 1 | L1-11 | 1756-OA16I | 6 | 1 | 9 | FN2308B_COIL | O:061/11 | FN | FN 2-308-B RUN KILN 2 DRIVE MOTOR COOLING FAN SOUTH | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT | FN2308B_COIL_IO | K2_DriveRoom_R06:1:O.Data.9 | K2_DriveRoom_R06:1:O.Data.9:=FN2308B_COIL_IO; //FN 2-308-B RUN KILN 2 DRIVE MOTOR COOLING FAN SOUTH |  | _FN2308B_M01 | P_Motor | PCmd_Start
1050 | R6G1M0 | 1771-ODD | 6 | 1 | L1-12 | 1756-OA16I | 6 | 1 | 10 | KD2308_LUBE_SV | O:061/12 |  | K2 KILN DRIVE LUBE TIMER | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT | KD2308_LUBE_SV_IO | K2_DriveRoom_R06:1:O.Data.10 | K2_DriveRoom_R06:1:O.Data.10:=KD2308_LUBE_SV_IO; //K2 KILN DRIVE LUBE TIMER |  | _KD2308_LUBE_SV | P_Dout | PCmd_On | bar: Notes
1051 | R6G1M0 | 1771-ODD | 6 | 1 | L1-13 | 1756-OA16I | 6 | 1 | 11 |  | O:061/13 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.11 | // K2_DriveRoom_R06:1:O.Data.11 SPARE
1052 | R6G1M0 | 1771-ODD | 6 | 1 | L1-14 | 1756-OA16I | 6 | 1 | 12 |  | O:061/14 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.12 | // K2_DriveRoom_R06:1:O.Data.12 SPARE
1053 | R6G1M0 | 1771-ODD | 6 | 1 | L1-15 | 1756-OA16I | 6 | 1 | 13 |  | O:061/15 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.13 | // K2_DriveRoom_R06:1:O.Data.13 SPARE
1054 | R6G1M0 | 1771-ODD | 6 | 1 | L1-16 | 1756-OA16I | 6 | 1 | 14 |  | O:061/16 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.14 | // K2_DriveRoom_R06:1:O.Data.14 SPARE
1055 | R6G1M0 | 1771-ODD | 6 | 1 | L1-17 | 1756-OA16I | 6 | 1 | 15 |  | O:061/17 |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Data | OUTPUT |  | K2_DriveRoom_R06:1:O.Data.15 | // K2_DriveRoom_R06:1:O.Data.15 SPARE
1056 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH1 | 1756-IF16 | 6 | 2 | 0 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch0Data | // K2_DriveRoom_R06:2:I.Ch0Data SPARE
1057 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH2 | 1756-IF16 | 6 | 2 | 1 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch1Data | // K2_DriveRoom_R06:2:I.Ch1Data SPARE
1058 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH3 | 1756-IF16 | 6 | 2 | 2 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch2Data | // K2_DriveRoom_R06:2:I.Ch2Data SPARE
1059 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH4 | 1756-IF16 | 6 | 2 | 3 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch3Data | // K2_DriveRoom_R06:2:I.Ch3Data SPARE
1060 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH5 | 1756-IF16 | 6 | 2 | 4 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch4Data | // K2_DriveRoom_R06:2:I.Ch4Data SPARE
1061 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH6 | 1756-IF16 | 6 | 2 | 5 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch5Data | // K2_DriveRoom_R06:2:I.Ch5Data SPARE
1062 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH7 | 1756-IF16 | 6 | 2 | 6 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch6Data | // K2_DriveRoom_R06:2:I.Ch6Data SPARE
1063 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH8 | 1756-IF16 | 6 | 2 | 7 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch7Data | // K2_DriveRoom_R06:2:I.Ch7Data SPARE
1064 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH9 | 1756-IF16 | 6 | 2 | 8 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch8Data | // K2_DriveRoom_R06:2:I.Ch8Data SPARE
1065 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH10 | 1756-IF16 | 6 | 2 | 9 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch9Data | // K2_DriveRoom_R06:2:I.Ch9Data SPARE
1066 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH11 | 1756-IF16 | 6 | 2 | 10 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch10Data | // K2_DriveRoom_R06:2:I.Ch10Data SPARE
1067 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH12 | 1756-IF16 | 6 | 2 | 11 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch11Data | // K2_DriveRoom_R06:2:I.Ch11Data SPARE
1068 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH13 | 1756-IF16 | 6 | 2 | 12 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch12Data | // K2_DriveRoom_R06:2:I.Ch12Data SPARE
1069 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH14 | 1756-IF16 | 6 | 2 | 13 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch13Data | // K2_DriveRoom_R06:2:I.Ch13Data SPARE
1070 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH15 | 1756-IF16 | 6 | 2 | 14 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch14Data | // K2_DriveRoom_R06:2:I.Ch14Data SPARE
1071 | R6G2M0 | 1771-IFE/C | 6 | 2 | CH16 | 1756-IF16 | 6 | 2 | 15 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | I.Ch | INPUT |  | K2_DriveRoom_R06:2:I.Ch15Data | // K2_DriveRoom_R06:2:I.Ch15Data SPARE
1072 | R6G3M0 | 1771-OFE2/B | 6 | 3 | CH1+ | 1756-OF8I | 6 | 3 | 0 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[0].Data | // K2_DriveRoom_R06:3:O.Ch[0].Data SPARE
1073 | R6G3M0 | 1771-OFE2/B | 6 | 3 | CH2+ | 1756-OF8I | 6 | 3 | 1 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[1].Data | // K2_DriveRoom_R06:3:O.Ch[1].Data SPARE
1074 | R6G3M0 | 1771-OFE2/B | 6 | 3 | CH3+ | 1756-OF8I | 6 | 3 | 2 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[2].Data | // K2_DriveRoom_R06:3:O.Ch[2].Data SPARE
1075 | R6G3M0 | 1771-OFE2/B | 6 | 3 | CH4+ | 1756-OF8I | 6 | 3 | 3 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[3].Data | // K2_DriveRoom_R06:3:O.Ch[3].Data SPARE
1076 | [5 empty] | 1756-OF8I | 6 | 3 | 4 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[4].Data | // K2_DriveRoom_R06:3:O.Ch[4].Data SPARE
1077 | [5 empty] | 1756-OF8I | 6 | 3 | 5 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[5].Data | // K2_DriveRoom_R06:3:O.Ch[5].Data SPARE
1078 | [5 empty] | 1756-OF8I | 6 | 3 | 6 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[6].Data | // K2_DriveRoom_R06:3:O.Ch[6].Data SPARE
1079 | [5 empty] | 1756-OF8I | 6 | 3 | 7 |  |  |  | SPARE | [10 empty] | K2_DriveRoom_R06 | O.Ch[ | OUTPUT |  | K2_DriveRoom_R06:3:O.Ch[7].Data | // K2_DriveRoom_R06:3:O.Ch[7].Data SPARE
1080 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 00 | 1756-IA16 | 10 | 0 | 00 | BC4401_YYS | I:100/0 |  | BC 4401 HAND BACK SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4401_YYS_IO | MCR1_R10:0:I.Data.00 | BC4401_YYS_IO:= MCR1_R10:0:I.Data.00; //BC 4401 HAND BACK SYSTEM BELT CONVEYOR |  | _BC4401_YYS | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BC4401_YYS | Back Handling
1081 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 01 | 1756-IA16 | 10 | 0 | 01 | BC4401_AUX | I:100/1 | BC | BC 4401 FDBK BACK SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4401_AUX_IO | MCR1_R10:0:I.Data.01 | BC4401_AUX_IO:= MCR1_R10:0:I.Data.01; //BC 4401 FDBK BACK SYSTEM BELT CONVEYOR |  | _BC4401_M01 | P_Motor | Sts_Running | 1 | Kiln1_Main_TaskC | Task_C | _BC4401_M01 | Back Handling
1082 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 02 | 1756-IA16 | 10 | 0 | 02 | BC4401_EY | I:100/2 |  | BC 4401 OVERLOADS BACK SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4401_EY_IO | MCR1_R10:0:I.Data.02 | BC4401_EY_IO:= MCR1_R10:0:I.Data.02; //BC 4401 OVERLOADS BACK SYSTEM BELT CONVEYOR |  | _BC4401_EY | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BC4401_EY | Back Handling
1083 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 03 | 1756-IA16 | 10 | 0 | 03 | BE4403_YYS | I:100/3 |  | BE 4403 HAND BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4403_YYS_IO | MCR1_R10:0:I.Data.03 | BE4403_YYS_IO:= MCR1_R10:0:I.Data.03; //BE 4403 HAND BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_YYS | P_DIn | Sts_PV | 0
1084 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 04 | 1756-IA16 | 10 | 0 | 04 | BE4403_AUX | I:100/4 | BE | BE 4403 AUX FDBK BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4403_AUX_IO | MCR1_R10:0:I.Data.04 | BE4403_AUX_IO:= MCR1_R10:0:I.Data.04; //BE 4403 AUX FDBK BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_M01 | P_Motor | Sts_Running | 1 | Back_Handling_TaskC | Task_C | _BE4403_M01 | Back Lime Handling
1085 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 05 | 1756-IA16 | 10 | 0 | 05 | BE4403_EY | I:100/5 |  | BE 4403 OVERLOADS BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4403_EY_IO | MCR1_R10:0:I.Data.05 | BE4403_EY_IO:= MCR1_R10:0:I.Data.05; //BE 4403 OVERLOADS BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_EY | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4403_EY | Back Handling
1086 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 06 | 1756-IA16 | 10 | 0 | 06 | SC443_YYS | I:100/6 |  | SC 4443 HAND BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC443_YYS_IO | MCR1_R10:0:I.Data.06 | SC443_YYS_IO:= MCR1_R10:0:I.Data.06; //SC 4443 HAND BACK SYSTEM SCREW CONVEYOR |  | _SC443_YYS | P_DIn | Sts_PV | 0
1087 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 07 | 1756-IA16 | 10 | 0 | 07 | SC4443_1_AUX | I:100/7 | SC | SC 4443 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4443_1_AUX_IO | MCR1_R10:0:I.Data.07 | SC4443_1_AUX_IO:= MCR1_R10:0:I.Data.07; //SC 4443 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4443_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4443_M01
1088 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 10 | 1756-IA16 | 10 | 0 | 08 | SC4443_EY | I:100/10 |  | SC 4443 OVERLOADS BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4443_EY_IO | MCR1_R10:0:I.Data.08 | SC4443_EY_IO:= MCR1_R10:0:I.Data.08; //SC 4443 OVERLOADS BACK SYSTEM SCREW CONVEYOR |  | _SC4443_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4443_EY
1089 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 11 | 1756-IA16 | 10 | 0 | 09 | RC44441_YYS | I:100/11 |  | RC 4444-1 HAND BACK SYSTEM ROLL CRUSHER | [10 empty] | MCR1_R10 | I.Data | INPUT | RC44441_YYS_IO | MCR1_R10:0:I.Data.09 | RC44441_YYS_IO:= MCR1_R10:0:I.Data.09; //RC 4444-1 HAND BACK SYSTEM ROLL CRUSHER |  | _RC44441_YYS | P_DIn | Sts_PV | 0
1090 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 12 | 1756-IA16 | 10 | 0 | 10 | RC44441_1_AUX | I:100/12 | RC | RC 4444-1 AUX FDBK BACK SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR1_R10 | I.Data | INPUT | RC44441_1_AUX_IO | MCR1_R10:0:I.Data.10 | RC44441_1_AUX_IO:= MCR1_R10:0:I.Data.10; //RC 4444-1 AUX FDBK BACK SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC44441_1_M01 | P_Motor | Sts_Running
1091 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 13 | 1756-IA16 | 10 | 0 | 11 | RC44441_EY | I:100/13 |  | RC 4444-1 OVERLOADS BACK SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR1_R10 | I.Data | INPUT | RC44441_EY_IO | MCR1_R10:0:I.Data.11 | RC44441_EY_IO:= MCR1_R10:0:I.Data.11; //RC 4444-1 OVERLOADS BACK SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC44441_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _RC44441_EY
1092 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 14 | 1756-IA16 | 10 | 0 | 12 | RC44442_1_AUX | I:100/14 | RC | RC 4444-2 AUX FDBK BACK SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR1_R10 | I.Data | INPUT | RC44442_1_AUX_IO | MCR1_R10:0:I.Data.12 | RC44442_1_AUX_IO:= MCR1_R10:0:I.Data.12; //RC 4444-2 AUX FDBK BACK SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC44442_1_AUX | P_Motor | Sts_Running
1093 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 15 | 1756-IA16 | 10 | 0 | 13 | RC44442_EY | I:100/15 |  | RC 4444-2 OVERLOADS BACK SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR1_R10 | I.Data | INPUT | RC44442_EY_IO | MCR1_R10:0:I.Data.13 | RC44442_EY_IO:= MCR1_R10:0:I.Data.13; //RC 4444-2 OVERLOADS BACK SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC44442_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _RC44442_EY
1094 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 16 | 1756-IA16 | 10 | 0 | 14 | RC44442_YYS | I:100/16 |  | RC 4444-2 HAND BACK SYSTEM ROLL CRUSHER | [10 empty] | MCR1_R10 | I.Data | INPUT | RC44442_YYS_IO | MCR1_R10:0:I.Data.14 | RC44442_YYS_IO:= MCR1_R10:0:I.Data.14; //RC 4444-2 HAND BACK SYSTEM ROLL CRUSHER |  | _RC44442_YYS | P_DIn | Sts_PV | 0
1095 | MCR1 R10G0M- | 1771-IAD | 10 | 0 | 17 | 1756-IA16 | 10 | 0 | 15 | SC4412_AUX | I:100/17 | SC | SC 4412 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4412_AUX_IO | MCR1_R10:0:I.Data.15 | SC4412_AUX_IO:= MCR1_R10:0:I.Data.15; //SC 4412 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4412_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _SC4412_M01
1096 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 00 | 1756-IA16 | 10 | 1 | 00 | SC4445_YYS | I:101/0 |  | SC 4445 HAND BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4445_YYS_IO | MCR1_R10:1:I.Data.00 | SC4445_YYS_IO:= MCR1_R10:1:I.Data.00; //SC 4445 HAND BACK SYSTEM SCREW CONVEYOR |  | _SC4445_YYS | P_DIn | Sts_PV | 0
1097 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 01 | 1756-IA16 | 10 | 1 | 01 | SC4445_AUX | I:101/1 | SC | SC 4445 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4445_AUX_IO | MCR1_R10:1:I.Data.01 | SC4445_AUX_IO:= MCR1_R10:1:I.Data.01; //SC 4445 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4445_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _SC4445_M01
1098 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 02 | 1756-IA16 | 10 | 1 | 02 | SC4445_EY | I:101/2 |  | SC 4445 OVERLOADS BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4445_EY_IO | MCR1_R10:1:I.Data.02 | SC4445_EY_IO:= MCR1_R10:1:I.Data.02; //SC 4445 OVERLOADS BACK SYSTEM SCREW CONVEYOR |  | _SC4445_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4445_EY
1099 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 03 | 1756-IA16 | 10 | 1 | 03 | BE4446_YYS | I:101/3 |  | BE 4446 HAND BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4446_YYS_IO | MCR1_R10:1:I.Data.03 | BE4446_YYS_IO:= MCR1_R10:1:I.Data.03; //BE 4446 HAND BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_YYS | P_DIn | Sts_PV | 0
1100 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 04 | 1756-IA16 | 10 | 1 | 04 | BE4446_AUX | I:101/4 | BE | BE 4446 AUX FDBK BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4446_AUX_IO | MCR1_R10:1:I.Data.04 | BE4446_AUX_IO:= MCR1_R10:1:I.Data.04; //BE 4446 AUX FDBK BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_M01 | P_Motor | Sts_Running | 1 | Back_Handling_TaskC | Task_C | _BE4446_M01 | Back lime Handling
1101 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 05 | 1756-IA16 | 10 | 1 | 05 | BE4446_EY | I:101/5 |  | BE 4446 OVERLOADS BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4446_EY_IO | MCR1_R10:1:I.Data.05 | BE4446_EY_IO:= MCR1_R10:1:I.Data.05; //BE 4446 OVERLOADS BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_EY | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4446_EY | BackHandling
1102 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 06 | 1756-IA16 | 10 | 1 | 06 | HM44051_HS | I:101/6 |  | HM 4405-1 SWITCH BACK SYSTEM FIELD OFF/AUTO | [10 empty] | MCR1_R10 | I.Data | INPUT | HM44051_HS_IO | MCR1_R10:1:I.Data.06 | HM44051_HS_IO:= MCR1_R10:1:I.Data.06; //HM 4405-1 SWITCH BACK SYSTEM FIELD OFF/AUTO |  | _HM44051_HS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _HM44051_HS
1103 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 07 | 1756-IA16 | 10 | 1 | 07 | HM44051_1_AUX | I:101/7 | HM | HM 4405-1 FDBK BACK SYSTEM HAMMERMILL FORWARD | [10 empty] | MCR1_R10 | I.Data | INPUT | HM44051_1_AUX_IO | MCR1_R10:1:I.Data.07 | HM44051_1_AUX_IO:= MCR1_R10:1:I.Data.07; //HM 4405-1 FDBK BACK SYSTEM HAMMERMILL FORWARD |  | _HM44051_1_AUX | P_Motor | Sts_Running
1104 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 10 | 1756-IA16 | 10 | 1 | 08 | HM44051_EY | I:101/10 |  | HM 4405-1 OVERLOADS BACK SYSTEM HAMMERMILL | [10 empty] | MCR1_R10 | I.Data | INPUT | HM44051_EY_IO | MCR1_R10:1:I.Data.08 | HM44051_EY_IO:= MCR1_R10:1:I.Data.08; //HM 4405-1 OVERLOADS BACK SYSTEM HAMMERMILL |  | _HM44051_EY | P_DIn | Sts_PV
1105 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 11 | 1756-IA16 | 10 | 1 | 09 | HM44051_2_AUX | I:101/11 | HM | HM 4405-1 AUX FDBK BACK SYSTEM HAMMERMILL REVERSE | [10 empty] | MCR1_R10 | I.Data | INPUT | HM44051_2_AUX_IO | MCR1_R10:1:I.Data.09 | HM44051_2_AUX_IO:= MCR1_R10:1:I.Data.09; //HM 4405-1 AUX FDBK BACK SYSTEM HAMMERMILL REVERSE |  | _HM44051_2_AUX | P_Motor | Sts_Running
1106 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 12 | 1756-IA16 | 10 | 1 | 10 | SC4412_YYS | I:101/12 |  | SC 4412 FIELD START BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4412_YYS_IO | MCR1_R10:1:I.Data.10 | SC4412_YYS_IO:= MCR1_R10:1:I.Data.10; //SC 4412 FIELD START BACK SYSTEM SCREW CONVEYOR |  | _SC4412_YYS | P_DIn | Sts_PV | 0
1107 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 13 | 1756-IA16 | 10 | 1 | 11 | HM44051REV_HS | I:101/13 |  | HM 4405-1 AUTO BACK SYSTEM HAMMERMILL REVERSE | [10 empty] | MCR1_R10 | I.Data | INPUT | HM44051REV_HS_IO | MCR1_R10:1:I.Data.11 | HM44051REV_HS_IO:= MCR1_R10:1:I.Data.11; //HM 4405-1 AUTO BACK SYSTEM HAMMERMILL REVERSE |  | _HM44051REV_HS | NA | NA |  | Back_Handling_TaskB | Task_B | _HM44051REV_HS
1108 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 14 | 1756-IA16 | 10 | 1 | 12 | VS4404_YYS | I:101/14 |  | VS 4404 HAND BACK SYSTEM VIBRATING SCREEN | [10 empty] | MCR1_R10 | I.Data | INPUT | VS4404_YYS_IO | MCR1_R10:1:I.Data.12 | VS4404_YYS_IO:= MCR1_R10:1:I.Data.12; //VS 4404 HAND BACK SYSTEM VIBRATING SCREEN |  | _VS4404_YYS | P_DIn | Sts_PV | 0
1109 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 15 | 1756-IA16 | 10 | 1 | 13 | VS4404_AUX | I:101/15 | VS | VS 4404 AUX FDBK BACK SYSTEM VIBRATING SCREEN | [10 empty] | MCR1_R10 | I.Data | INPUT | VS4404_AUX_IO | MCR1_R10:1:I.Data.13 | VS4404_AUX_IO:= MCR1_R10:1:I.Data.13; //VS 4404 AUX FDBK BACK SYSTEM VIBRATING SCREEN |  | _VS4404_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _VS4404_M01
1110 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 16 | 1756-IA16 | 10 | 1 | 14 | VS4404_EY | I:101/16 |  | VS 4404 OVERLOADS BACK SYSTEM VIBRATING SCREEN | [10 empty] | MCR1_R10 | I.Data | INPUT | VS4404_EY_IO | MCR1_R10:1:I.Data.14 | VS4404_EY_IO:= MCR1_R10:1:I.Data.14; //VS 4404 OVERLOADS BACK SYSTEM VIBRATING SCREEN |  | _VS4404_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _VS4404_EY
1111 | MCR1 R10G1M- | 1771-IAD | 10 | 1 | 17 | 1756-IA16 | 10 | 1 | 15 |  | I:101/17 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:1:I.Data.15 | // MCR1_R10:1:I.Data.15 SPARE | bar: Notes to EU
1112 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 00 | 1756-IA16 | 10 | 2 | 00 | SC4447_YYS | I:102/0 |  | SC 4447 HAND BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4447_YYS_IO | MCR1_R10:2:I.Data.00 | SC4447_YYS_IO:= MCR1_R10:2:I.Data.00; //SC 4447 HAND BACK SYSTEM SCREW CONVEYOR |  | _SC4447_YYS | P_DIn | Sts_PV | 0
1113 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 01 | 1756-IA16 | 10 | 2 | 01 | SC4447_AUX | I:102/1 | SC | SC 4447 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4447_AUX_IO | MCR1_R10:2:I.Data.01 | SC4447_AUX_IO:= MCR1_R10:2:I.Data.01; //SC 4447 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4447_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _SC4447_M01
1114 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 02 | 1756-IA16 | 10 | 2 | 02 | SC4447_EY | I:102/2 | SC | SC 4447 OVERLOADS BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4447_EY_IO | MCR1_R10:2:I.Data.02 | SC4447_EY_IO:= MCR1_R10:2:I.Data.02; //SC 4447 OVERLOADS BACK SYSTEM SCREW CONVEYOR |  | _SC4447_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4447_EY
1115 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 03 | 1756-IA16 | 10 | 2 | 03 | BE4406W_YYS | I:102/3 | BE | BE 4406-W HAND BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406W_YYS_IO | MCR1_R10:2:I.Data.03 | BE4406W_YYS_IO:= MCR1_R10:2:I.Data.03; //BE 4406-W HAND BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_YYS | P_DIn | Sts_PV | 0
1116 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 04 | 1756-IA16 | 10 | 2 | 04 | BE4406W_AUX | I:102/4 | BE | BE 4406-W AUX FDBK BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406W_AUX_IO | MCR1_R10:2:I.Data.04 | BE4406W_AUX_IO:= MCR1_R10:2:I.Data.04; //BE 4406-W AUX FDBK BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_M01 | P_Motor | Sts_Running | 1 | Back_Handling_TaskC | Task_C | _BE4406W_M01 | Back lime Handling
1117 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 05 | 1756-IA16 | 10 | 2 | 05 | BE4406W_EY | I:102/5 | BE | BE 4406-W OVERLOADS BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406W_EY_IO | MCR1_R10:2:I.Data.05 | BE4406W_EY_IO:= MCR1_R10:2:I.Data.05; //BE 4406-W OVERLOADS BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_EY | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4406W_EY | Back Handling
1118 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 06 | 1756-IA16 | 10 | 2 | 06 | SC1613B_AUX | I:102/6 | SC | SC 1613-B AUX FDBK KILN 1 N. FUEL FEED SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC1613B_AUX_IO | MCR1_R10:2:I.Data.06 | SC1613B_AUX_IO:= MCR1_R10:2:I.Data.06; //SC 1613-B AUX FDBK KILN 1 N. FUEL FEED SCREW CONVEYOR |  | _SC1613B_AUX | P_DIn | Sts_PV
1119 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 07 | 1756-IA16 | 10 | 2 | 07 | SC4408A_AUX | I:102/7 | SC | SC 4408-A AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4408A_AUX_IO | MCR1_R10:2:I.Data.07 | SC4408A_AUX_IO:= MCR1_R10:2:I.Data.07; //SC 4408-A AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4408A_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _SC4408A_M01
1120 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 10 | 1756-IA16 | 10 | 2 | 08 | SC1613B_HS | I:102/10 | SC | SC 1613-B AUTO KILN 1 N. FUEL FEED SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC1613B_HS_IO | MCR1_R10:2:I.Data.08 | SC1613B_HS_IO:= MCR1_R10:2:I.Data.08; //SC 1613-B AUTO KILN 1 N. FUEL FEED SCREW CONVEYOR |  | _SC1613B_HS | P_DIn | Sts_PV
1121 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 11 | 1756-IA16 | 10 | 2 | 09 | SC1613A_HS | I:102/11 | SC | SC 1613-A AUTO KILN 1 S. FUAL FEED SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC1613A_HS_IO | MCR1_R10:2:I.Data.09 | SC1613A_HS_IO:= MCR1_R10:2:I.Data.09; //SC 1613-A AUTO KILN 1 S. FUAL FEED SCREW CONVEYOR |  | _SC1613A_HS | P_DIn | Sts_PV
1122 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 12 | 1756-IA16 | 10 | 2 | 10 | SC4408B_AUX | I:102/12 | SC | SC 4408-B AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4408B_AUX_IO | MCR1_R10:2:I.Data.10 | SC4408B_AUX_IO:= MCR1_R10:2:I.Data.10; //SC 4408-B AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4408B_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _SC4408B_M01
1123 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 13 | 1756-IA16 | 10 | 2 | 11 | SC1613B_MS | I:102/13 | SC | SC 1613-B ZERO SPEED KILN 1 N. FUEL FEED SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC1613B_MS_IO | MCR1_R10:2:I.Data.11 | SC1613B_MS_IO:= MCR1_R10:2:I.Data.11; //SC 1613-B ZERO SPEED KILN 1 N. FUEL FEED SCREW CONVEYOR |  | _SC1613B_MS | P_DIn | Sts_PV | bar: Notes
1124 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 14 | 1756-IA16 | 10 | 2 | 12 | BE4406E_YYS | I:102/14 | BE | BE 4406-E HAND BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406E_YYS_IO | MCR1_R10:2:I.Data.12 | BE4406E_YYS_IO:= MCR1_R10:2:I.Data.12; //BE 4406-E HAND BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_YYS | P_DIn | Sts_PV | 0
1125 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 15 | 1756-IA16 | 10 | 2 | 13 | BE4406E_AUX | I:102/15 | BE | BE 4406-E AUX FDBK BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406E_AUX_IO | MCR1_R10:2:I.Data.13 | BE4406E_AUX_IO:= MCR1_R10:2:I.Data.13; //BE 4406-E AUX FDBK BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_M01 | P_Motor | Sts_Running | 1 | Back_Handling_TaskC | Task_C | _BE4406E_M01 | Back lime Handling
1126 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 16 | 1756-IA16 | 10 | 2 | 14 | BE4406E_EY | I:102/16 | BE | BE 4406-E OVERLOADS BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406E_EY_IO | MCR1_R10:2:I.Data.14 | BE4406E_EY_IO:= MCR1_R10:2:I.Data.14; //BE 4406-E OVERLOADS BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_EY | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4406E_EY | Back Handling
1127 | MCR1 R10G2M- | 1771-IAD | 10 | 2 | 17 | 1756-IA16 | 10 | 2 | 15 |  | I:102/17 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:2:I.Data.15 | // MCR1_R10:2:I.Data.15 SPARE
1128 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 00 | 1756-IA16 | 10 | 3 | 00 | HM44051_SSA | I:103/0 |  | HM 4405-1 AUTO BACK SYSTEM HAMMERMILL FORWARD | [10 empty] | MCR1_R10 | I.Data | INPUT | HM44051_SSA_IO | MCR1_R10:3:I.Data.00 | HM44051_SSA_IO:= MCR1_R10:3:I.Data.00; //HM 4405-1 AUTO BACK SYSTEM HAMMERMILL FORWARD |  | _HM44051_SSA | P_DIn | Sts_PV | 0 | bar: Notes
1129 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 01 | 1756-IA16 | 10 | 3 | 01 | SC4408_AUX | I:103/1 | SC | SC 4408 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4408_AUX_IO | MCR1_R10:3:I.Data.01 | SC4408_AUX_IO:= MCR1_R10:3:I.Data.01; //SC 4408 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4408_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _SC4408_M01
1130 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 02 | 1756-IA16 | 10 | 3 | 02 | SC_1613_PCD | I:103/2 | SC | SC-1613 PLUGGED CHUTE DETECTOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC_1613_PCD_IO | MCR1_R10:3:I.Data.02 | SC_1613_PCD_IO:= MCR1_R10:3:I.Data.02; //SC-1613 PLUGGED CHUTE DETECTOR |  | _SC_1613_PCD | P_DIn | Sts_PV | bar: Notes
1131 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 03 | 1756-IA16 | 10 | 3 | 03 | SC4408C_YYS | I:103/3 | SC | SC 4408-C HAND BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4408C_YYS_IO | MCR1_R10:3:I.Data.03 | SC4408C_YYS_IO:= MCR1_R10:3:I.Data.03; //SC 4408-C HAND BACK SYSTEM SCREW CONVEYOR |  | _SC4408C_YYS | P_DIn | Sts_PV | 0
1132 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 04 | 1756-IA16 | 10 | 3 | 04 | SC4408C_AUX | I:103/4 | SC | SC 4408-C AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4408C_AUX_IO | MCR1_R10:3:I.Data.04 | SC4408C_AUX_IO:= MCR1_R10:3:I.Data.04; //SC 4408-C AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC4408C_M01 | P_Motor | Sts_Running |  | Back_Handling2_TaskC | Task_C | _SC4408C_M01
1133 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 05 | 1756-IA16 | 10 | 3 | 05 | SC4408C_EY | I:103/5 | SC | SC 4408-C OVERLOADS BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4408C_EY_IO | MCR1_R10:3:I.Data.05 | SC4408C_EY_IO:= MCR1_R10:3:I.Data.05; //SC 4408-C OVERLOADS BACK SYSTEM SCREW CONVEYOR |  | _SC4408C_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4408C_EY
1134 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 06 | 1756-IA16 | 10 | 3 | 06 | FN44141_YYS | I:103/6 | FN | FN 4414-1 HAND BACK SYSTEM DC FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN44141_YYS_IO | MCR1_R10:3:I.Data.06 | FN44141_YYS_IO:= MCR1_R10:3:I.Data.06; //FN 4414-1 HAND BACK SYSTEM DC FAN |  | _FN44141_YYS | P_DIn | Sts_PV | 0
1135 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 07 | 1756-IA16 | 10 | 3 | 07 | FN44141_AUX | I:103/7 | FN | FN 4414-1 AUX FDBK BACK SYSTEM DC FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN44141_AUX_IO | MCR1_R10:3:I.Data.07 | FN44141_AUX_IO:= MCR1_R10:3:I.Data.07; //FN 4414-1 AUX FDBK BACK SYSTEM DC FAN |  | _FN44141_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _FN44141_M01
1136 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 10 | 1756-IA16 | 10 | 3 | 08 | FN44141_EY | I:103/10 | FN | FN 4414-1 OVERLOADS BACK SYSTEM DC FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN44141_EY_IO | MCR1_R10:3:I.Data.08 | FN44141_EY_IO:= MCR1_R10:3:I.Data.08; //FN 4414-1 OVERLOADS BACK SYSTEM DC FAN |  | _FN44141_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _FN44141_EY
1137 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 11 | 1756-IA16 | 10 | 3 | 09 | SC44122_YYS | I:103/11 | SC | SC 4414-2 HAND BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC44122_YYS_IO | MCR1_R10:3:I.Data.09 | SC44122_YYS_IO:= MCR1_R10:3:I.Data.09; //SC 4414-2 HAND BACK SYSTEM SCREW CONVEYOR |  | _SC44122_YYS | P_DIn | Sts_PV | 0
1138 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 12 | 1756-IA16 | 10 | 3 | 10 | SC44142_AUX | I:103/12 | SC | SC 4414-2 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC44142_AUX_IO | MCR1_R10:3:I.Data.10 | SC44142_AUX_IO:= MCR1_R10:3:I.Data.10; //SC 4414-2 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | _SC44142_M01 | P_Motor | Sts_Running |  | Back_Handling2_TaskC | Task_C | _SC44142_M01
1139 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 13 | 1756-IA16 | 10 | 3 | 11 | SC44142_EY | I:103/13 | SC | SC 4414-2 OVERLOADS BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC44142_EY_IO | MCR1_R10:3:I.Data.11 | SC44142_EY_IO:= MCR1_R10:3:I.Data.11; //SC 4414-2 OVERLOADS BACK SYSTEM SCREW CONVEYOR |  | _SC44142_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC44142_EY
1140 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 14 | 1756-IA16 | 10 | 3 | 12 |  | I:103/14 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:3:I.Data.12 | // MCR1_R10:3:I.Data.12 SPARE
1141 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 15 | 1756-IA16 | 10 | 3 | 13 |  | I:103/15 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:3:I.Data.13 | // MCR1_R10:3:I.Data.13 SPARE
1142 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 16 | 1756-IA16 | 10 | REMOVE | 14 |  | I:103/16 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.14 | // MCR1_R10:REMOVE:I.Data.14 SPARE
1143 | MCR1 R10G3M- | 1771-IAD | 10 | 3 | 17 | 1756-IA16 | 10 | REMOVE | 15 |  | I:103/17 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.15 | // MCR1_R10:REMOVE:I.Data.15 SPARE
1144 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 00 | 1756-IA16 | 10 | 4 | 00 | BE4403_PB_JOG | I:104/0 | BE | BE 4403 JOG BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4403_PB_JOG_IO | MCR1_R10:4:I.Data.00 | BE4403_PB_JOG_IO:= MCR1_R10:4:I.Data.00; //BE 4403 JOG BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_M01 | P_Motor | Sts_Jogging | 0 | Back_Handling_TaskC | Task_C | _BE4403_M01 | bar: Notes
1145 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 01 | 1756-IA16 | 10 | 4 | 01 | BE4403_JOG_SET | I:104/1 | BE | BE 4403 JOG PLUG IN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4403_JOG_SET_IO | MCR1_R10:4:I.Data.01 | BE4403_JOG_SET_IO:= MCR1_R10:4:I.Data.01; //BE 4403 JOG PLUG IN BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_M01 | P_Motor | Sts_Ext | 0 | Back_Handling_TaskC | Task_C | _BE4403_M01 | bar: Notes
1146 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 02 | 1756-IA16 | 10 | 4 | 02 | BE4406E_PB_JOG | I:104/2 | BE | BE 4406-E JOG BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406E_PB_JOG_IO | MCR1_R10:4:I.Data.02 | BE4406E_PB_JOG_IO:= MCR1_R10:4:I.Data.02; //BE 4406-E JOG BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_M01 | P_Motor | Sts_Jogging | 0 | Back_Handling_TaskC | Task_C | _BE4406E_M01 | bar: Notes
1147 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 03 | 1756-IA16 | 10 | 4 | 03 | RA44144_YYS | I:104/3 | RA | RA 4414-4 HAND BACK SYSTEM ROTARY AIRLOCK | [10 empty] | MCR1_R10 | I.Data | INPUT | RA44144_YYS_IO | MCR1_R10:4:I.Data.03 | RA44144_YYS_IO:= MCR1_R10:4:I.Data.03; //RA 4414-4 HAND BACK SYSTEM ROTARY AIRLOCK |  | _RA44144_YYS | P_DIn | Sts_PV | 0
1148 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 04 | 1756-IA16 | 10 | 4 | 04 | RA44144_AUX | I:104/4 | RA | RA 4414-4 AUX FDBK BACK SYSTEM ROTARY AIRLOCK | [10 empty] | MCR1_R10 | I.Data | INPUT | RA44144_AUX_IO | MCR1_R10:4:I.Data.04 | RA44144_AUX_IO:= MCR1_R10:4:I.Data.04; //RA 4414-4 AUX FDBK BACK SYSTEM ROTARY AIRLOCK |  | _RA44144_M01 | P_Motor | Sts_Running |  | Back_Handling_TaskC | Task_C | _RA44144_M01
1149 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 05 | 1756-IA16 | 10 | 4 | 05 | RA44144_EY | I:104/5 | RA | RA 4414-4 OVERLOADS BACK SYSTEM ROTARY AIRLOCK | [10 empty] | MCR1_R10 | I.Data | INPUT | RA44144_EY_IO | MCR1_R10:4:I.Data.05 | RA44144_EY_IO:= MCR1_R10:4:I.Data.05; //RA 4414-4 OVERLOADS BACK SYSTEM ROTARY AIRLOCK |  | _RA44144_EY | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _RA44144_EY
1150 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 06 | 1756-IA16 | 10 | 4 | 06 | BE4406E_JOG_SET | I:104/6 | BE | BE 4406-E JOG PLUG IN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406E_JOG_SET_IO | MCR1_R10:4:I.Data.06 | BE4406E_JOG_SET_IO:= MCR1_R10:4:I.Data.06; //BE 4406-E JOG PLUG IN BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_M01 | P_Motor | Sts_Ext | 0 | Back_Handling_TaskC | Task_C | _BE4406E_M01 | bar: Notes
1151 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 07 | 1756-IA16 | 10 | 4 | 07 | BE4406W_PB_JOG | I:104/7 | BE | BE 4406-W JOG BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406W_PB_JOG_IO | MCR1_R10:4:I.Data.07 | BE4406W_PB_JOG_IO:= MCR1_R10:4:I.Data.07; //BE 4406-W JOG BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_M01 | P_Motor | Sts_Jogging | 0 | Back_Handling_TaskC | Task_C | _BE4406W_M01 | bar: Notes
1152 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 10 | 1756-IA16 | 10 | 4 | 08 | BE4406W_JOG_SET | I:104/10 | BE | BE 4406-W JOG PLUG IN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4406W_JOG_SET_IO | MCR1_R10:4:I.Data.08 | BE4406W_JOG_SET_IO:= MCR1_R10:4:I.Data.08; //BE 4406-W JOG PLUG IN BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_M01 | P_Motor | Sts_Ext | 1 | Back_Handling_TaskC | Task_C | _BE4406W_M01 | Back lime Handling | bar: Notes
1153 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 11 | 1756-IA16 | 10 | REMOVE | 09 |  | I:104/11 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.09 | // MCR1_R10:REMOVE:I.Data.09 SPARE
1154 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 12 | 1756-IA16 | 10 | REMOVE | 10 |  | I:104/12 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.10 | // MCR1_R10:REMOVE:I.Data.10 SPARE
1155 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 13 | 1756-IA16 | 10 | REMOVE | 11 |  | I:104/13 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.11 | // MCR1_R10:REMOVE:I.Data.11 SPARE
1156 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 14 | 1756-IA16 | 10 | 4 | 15 | MCR1_ALM | I:104/14 |  | ALARM FIRE IN MCR 1 | [10 empty] | MCR1_R10 | I.Data | INPUT | MCR1_ALM_IO | MCR1_R10:4:I.Data.15 | MCR1_ALM_IO:= MCR1_R10:4:I.Data.15; //ALARM FIRE IN MCR 1 |  | _MCR1_ALM | P_DIn | Sts_PV
1157 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 15 | 1756-IA16 | 10 | REMOVE | 13 |  | I:104/15 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.13 | // MCR1_R10:REMOVE:I.Data.13 SPARE
1158 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 16 | 1756-IA16 | 10 | REMOVE | 14 |  | I:104/16 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.14 | // MCR1_R10:REMOVE:I.Data.14 SPARE
1159 | MCR1 R10G4M- | 1771-IAD | 10 | 4 | 17 | 1756-IA16 | 10 | REMOVE | 12 |  | I:104/17 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.12 | // MCR1_R10:REMOVE:I.Data.12 SPARE
1160 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 00 | 1756-IA16 | 10 | 4 | 14 | MCR1_UPS_DI | I:105/0 | UPS | INDICATES POWER TO UPS FOR PLC | [10 empty] | MCR1_R10 | I.Data | INPUT | MCR1_UPS_DI_IO | MCR1_R10:4:I.Data.14 | MCR1_UPS_DI_IO:= MCR1_R10:4:I.Data.14; //INDICATES POWER TO UPS FOR PLC |  | _MCR1_UPS_DI | P_DIn | Sts_PV | bar: Notes to EU
1161 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 01 | 1756-IA16 | 10 | REMOVE | 01 |  | I:105/1 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.01 | // MCR1_R10:REMOVE:I.Data.01 SPARE
1162 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 02 | 1756-IA16 | 10 | 3 | 14 | VF2311_YYS | I:105/2 | VF | VF 2311 REMOTE STOP KILN 2 COOLER VIBRATORY FEEDER | [10 empty] | MCR1_R10 | I.Data | INPUT | VF2311_YYS_IO | MCR1_R10:3:I.Data.14 | VF2311_YYS_IO:= MCR1_R10:3:I.Data.14; //VF 2311 REMOTE STOP KILN 2 COOLER VIBRATORY FEEDER |  | _VF2311_YYS | P_DIn | Sts_PV | 0
1163 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 03 | 1756-IA16 | 10 | 3 | 15 | CL2310_LAH | I:105/3 | CL | C 2310 ALARM KILN 2 COOLER FULL A2D2 | [10 empty] | MCR1_R10 | I.Data | INPUT | CL2310_LAH_IO | MCR1_R10:3:I.Data.15 | CL2310_LAH_IO:= MCR1_R10:3:I.Data.15; //C 2310 ALARM KILN 2 COOLER FULL A2D2 |  | _CL2310_LAH | P_DIn | Sts_PV | 0 | bar: Notes
1164 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 04 | 1756-IA16 | 10 | 4 | 9 | BC4504C_AUX | I:105/4 | BC | BC 4504-C FDBK COAL SYSTEM VFD BELT CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4504C_AUX_IO | MCR1_R10:4:I.Data.9 | BC4504C_AUX_IO:= MCR1_R10:4:I.Data.9; //BC 4504-C FDBK COAL SYSTEM VFD BELT CONVEYOR |  | _BC4504C_M01 | P_VSD | Sts_Running | 1 | Fuel_Handling_TaskC | Task_C | _BC4504C_M01 | Fuel Handling
1165 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 05 | 1756-IA16 | 10 | 4 | 10 | BC4504C_DI | I:105/5 | PS | PS 4504-C FDBK COAL SYSTEM PADDLE SWITCH | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4504C_DI_IO | MCR1_R10:4:I.Data.10 | BC4504C_DI_IO:= MCR1_R10:4:I.Data.10; //PS 4504-C FDBK COAL SYSTEM PADDLE SWITCH |  | _BC4504C_DI | P_DIn | Sts_PV | 1 | Fuel_Handling_TaskB | Task_B | _BC4504C_DI | Fuel Handling | bar: Notes
1166 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 06 | 1756-IA16 | 10 | 4 | 11 | BC4506_1_AUX | I:105/6 | BC | BC 4506 FDBK COAL SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4506_1_AUX_IO | MCR1_R10:4:I.Data.11 | BC4506_1_AUX_IO:= MCR1_R10:4:I.Data.11; //BC 4506 FDBK COAL SYSTEM BELT CONVEYOR |  | _BC4506_M01 | P_VSD | Sts_Running | 1 | Fuel_Handling_TaskC | Task_C | _BC4506_M01 | Fuel Handling
1167 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 07 | 1756-IA16 | 10 | 4 | 12 | BC4504C_FLT_DI | I:105/7 | BC | BC 4504C ALARM COAL SYSTEM VFD BELT CONVEYOR FAULT |  | Notes: FOR HMI ALARM | MCR1_R10 | I.Data | INPUT | BC4504C_FLT_DI_IO | MCR1_R10:4:I.Data.12 | BC4504C_FLT_DI_IO:= MCR1_R10:4:I.Data.12; //BC 4504C ALARM COAL SYSTEM VFD BELT CONVEYOR FAULT |  | _BC4504C_M01 | P_VSD | Sts_IOFault | 1 | Fuel_Handling_TaskC | Task_C | _BC4504C_M01 | Fuel Handling
1168 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 10 | 1756-IA16 | 10 | 4 | 13 | SC4443_2_AUX | I:105/10 | SC | SC 4443 AUX FDBK BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | SC4443_2_AUX_IO | MCR1_R10:4:I.Data.13 | SC4443_2_AUX_IO:= MCR1_R10:4:I.Data.13; //SC 4443 AUX FDBK BACK SYSTEM SCREW CONVEYOR |  | NA | NA | NA
1169 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 11 | 1756-IA16 | 10 | REMOVE | 09 |  | I:105/11 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.09 | // MCR1_R10:REMOVE:I.Data.09 SPARE
1170 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 12 | 1756-IA16 | 10 | REMOVE | 10 |  | I:105/12 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.10 | // MCR1_R10:REMOVE:I.Data.10 SPARE
1171 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 13 | 1756-IA16 | 10 | REMOVE | 11 |  | I:105/13 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.11 | // MCR1_R10:REMOVE:I.Data.11 SPARE
1172 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 14 | 1756-IA16 | 10 | REMOVE | 12 |  | I:105/14 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.12 | // MCR1_R10:REMOVE:I.Data.12 SPARE
1173 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 15 | 1756-IA16 | 10 | REMOVE | 13 |  | I:105/15 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.13 | // MCR1_R10:REMOVE:I.Data.13 SPARE
1174 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 16 | 1756-IA16 | 10 | REMOVE | 14 |  | I:105/16 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.14 | // MCR1_R10:REMOVE:I.Data.14 SPARE
1175 | MCR1 R10G5M- | 1771-IAD | 10 | 5 | 17 | 1756-IA16 | 10 | REMOVE | 15 |  | I:105/17 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.15 | // MCR1_R10:REMOVE:I.Data.15 SPARE
1176 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 00 | 1756-IA16 | 10 | 5 | 00 | FN1605_AUX | I:106/0 | FN | FN 1605 AUX FDBK KILN 1 MILL EXHAUST FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN1605_AUX_IO | MCR1_R10:5:I.Data.00 | FN1605_AUX_IO:= MCR1_R10:5:I.Data.00; //FN 1605 AUX FDBK KILN 1 MILL EXHAUST FAN |  | _FN1605_M01 | P_VSD | Sts_Running |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _FN1605_M01
1177 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 01 | 1756-IA16 | 10 | 5 | 01 |  | I:106/1 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:5:I.Data.01 | // MCR1_R10:5:I.Data.01 SPARE
1178 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 02 | 1756-IA16 | 10 | 5 | 02 | FN1335_AUX | I:106/2 | FN | FN 1335 FDBK KILN 1 NOSE RING FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN1335_AUX_IO | MCR1_R10:5:I.Data.02 | FN1335_AUX_IO:= MCR1_R10:5:I.Data.02; //FN 1335 FDBK KILN 1 NOSE RING FAN |  | _FN1308A_M01 | P_Motor | Sts_Running
1179 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 03 | 1756-IA16 | 10 | 5 | 03 | FN1614_AUX | I:106/3 | FN | FN 1614 AUX FDBK KILN 1 FAN | delete UNIT ON ETHERNET | Notes: TBD | MCR1_R10 | I.Data | INPUT | FN1614_AUX_IO | MCR1_R10:5:I.Data.03 | FN1614_AUX_IO:= MCR1_R10:5:I.Data.03; //FN 1614 AUX FDBK KILN 1 FAN |  | _FN1614_M01 | P_Motor | Sts_Running
1180 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 04 | 1756-IA16 | 10 | 5 | 04 | BV1518_AUX | I:106/4 | BV | BV 1518 AUX FDBK KILN 1 BIN VIBRATER | [10 empty] | MCR1_R10 | I.Data | INPUT | BV1518_AUX_IO | MCR1_R10:5:I.Data.04 | BV1518_AUX_IO:= MCR1_R10:5:I.Data.04; //BV 1518 AUX FDBK KILN 1 BIN VIBRATER |  | _BV1518_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _BV1518_M01 | Kiln 1 Solid Fuel System
1181 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 05 | 1756-IA16 | 10 | 5 | 05 | RA1614_AUX | I:106/5 | RA | RA 1614 AUX FDBK KILN 1 COAL ROTARY AIRLOCK | delete UNIT ON ETHERNET | Notes: TBD | MCR1_R10 | I.Data | INPUT | RA1614_AUX_IO | MCR1_R10:5:I.Data.05 | RA1614_AUX_IO:= MCR1_R10:5:I.Data.05; //RA 1614 AUX FDBK KILN 1 COAL ROTARY AIRLOCK |  | _RA1614_M01 | P_Motor | Sts_Running
1182 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 06 | 1756-IA16 | 10 | 5 | 06 | BM1602_AUX | I:106/6 | BM | BM 1602 AUX FDBK KILN 1 COAL BALL MILL | [10 empty] | MCR1_R10 | I.Data | INPUT | BM1602_AUX_IO | MCR1_R10:5:I.Data.06 | BM1602_AUX_IO:= MCR1_R10:5:I.Data.06; //BM 1602 AUX FDBK KILN 1 COAL BALL MILL |  | _BM1602_M01 | P_Motor | Sts_Running | 1 | Kiln1_Solid_Fuel_System_TaskC | Task_C | _BM1602_M01 | Kiln 1 Solid Fuel System
1183 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 07 | 1756-IA16 | 10 | 5 | 07 | FN1605_SSA | I:106/7 |  | FN 1-605 AUTO KILN 1 MILL EXHAUST FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN1605_SSA_IO | MCR1_R10:5:I.Data.07 | FN1605_SSA_IO:= MCR1_R10:5:I.Data.07; //FN 1-605 AUTO KILN 1 MILL EXHAUST FAN |  | _FN1605_SSA | P_DIn | Sts_PV | 1 | Kiln1_Main_TaskB | Task_B | _FN1605_SSA | Kiln 1 | bar: Notes
1184 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 10 | 1756-IA16 | 10 | 5 | 08 | FN1341_AUX | I:106/10 | FN | FN 1341 AUX FDBK KILN 1 SEAL AIR FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN1341_AUX_IO | MCR1_R10:5:I.Data.08 | FN1341_AUX_IO:= MCR1_R10:5:I.Data.08; //FN 1341 AUX FDBK KILN 1 SEAL AIR FAN |  | _FN1341_M01 | P_Motor | Sts_Running | 1 | Kiln1_Main_TaskC | Task_C | _FN1341_M01 | Kiln 1 | bar: Notes
1185 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 11 | 1756-IA16 | 10 | 5 | 09 |  | I:106/11 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:5:I.Data.09 | // MCR1_R10:5:I.Data.09 SPARE
1186 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 12 | 1756-IA16 | 10 | 5 | 10 | VF4504A_AUX | I:106/12 | VF | VF 4504-A AUX FDBK FUEL SYSTEM VIBRATING FEEDER | [10 empty] | MCR1_R10 | I.Data | INPUT | VF4504A_AUX_IO | MCR1_R10:5:I.Data.10 | VF4504A_AUX_IO:= MCR1_R10:5:I.Data.10; //VF 4504-A AUX FDBK FUEL SYSTEM VIBRATING FEEDER |  | _VF4504A_M01 | P_VSD | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _VF4504A_M01
1187 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 13 | 1756-IA16 | 10 | 5 | 11 |  | I:106/13 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:5:I.Data.11 | // MCR1_R10:5:I.Data.11 SPARE
1188 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 14 | 1756-IA16 | 10 | 5 | 12 | VF4504B_AUX | I:106/14 | VF | VF 4504-B AUX FDBK FUEL SYSTEM VIBRATING FEEDER | [10 empty] | MCR1_R10 | I.Data | INPUT | VF4504B_AUX_IO | MCR1_R10:5:I.Data.12 | VF4504B_AUX_IO:= MCR1_R10:5:I.Data.12; //VF 4504-B AUX FDBK FUEL SYSTEM VIBRATING FEEDER |  | _VF4504B_M01 | P_VSD | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _VF4504B_M01
1189 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 15 | 1756-IA16 | 10 | 5 | 13 | FN1605_ATSPD_DI | I:106/15 |  | FN 1-605 VFD AT SPEED KILN 1 MILL EXHAUST FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN1605_ATSPD_DI_IO | MCR1_R10:5:I.Data.13 | FN1605_ATSPD_DI_IO:= MCR1_R10:5:I.Data.13; //FN 1-605 VFD AT SPEED KILN 1 MILL EXHAUST FAN |  | _FN1605_M01 | P_VSD | Sts_AtSpeed |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _FN1605_M01 | bar: Notes
1190 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 16 | 1756-IA16 | 10 | 5 | 14 | RC45051_AUX | I:106/16 | RC | RC 4505-1 AUX FDBK FUEL SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR1_R10 | I.Data | INPUT | RC45051_AUX_IO | MCR1_R10:5:I.Data.14 | RC45051_AUX_IO:= MCR1_R10:5:I.Data.14; //RC 4505-1 AUX FDBK FUEL SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC45051_M01 | P_Motor | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _RC45051_M01
1191 | MCR1 R10G6M- | 1771-IAD | 10 | 6 | 17 | 1756-IA16 | 10 | 5 | 15 | FN1605_FLT_DI | I:106/17 |  | FN 1-605 VFD FAULT KILN 1 MILL EXHAUST FAN | [10 empty] | MCR1_R10 | I.Data | INPUT | FN1605_FLT_DI_IO | MCR1_R10:5:I.Data.15 | FN1605_FLT_DI_IO:= MCR1_R10:5:I.Data.15; //FN 1-605 VFD FAULT KILN 1 MILL EXHAUST FAN |  | _FN1605_M01 | P_VSD | Sts_DriveFault |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _FN1605_M01 | bar: Notes
1192 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 00 | 1756-IA16 | 10 | 6 | 00 | RC45052_AUX | I:107/0 | RC | RC 4505-2 AUX FDBK FUEL SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR1_R10 | I.Data | INPUT | RC45052_AUX_IO | MCR1_R10:6:I.Data.00 | RC45052_AUX_IO:= MCR1_R10:6:I.Data.00; //RC 4505-2 AUX FDBK FUEL SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC45052_M01 | P_Motor | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _RC45052_M01
1193 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 01 | 1756-IA16 | 10 | 6 | 01 |  | I:107/1 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:6:I.Data.01 | // MCR1_R10:6:I.Data.01 SPARE
1194 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 02 | 1756-IA16 | 10 | 6 | 02 | BC4506_2_AUX | I:107/2 | BC | BC 4506 FDBK FUEL SYSTEM BELT CONVEYOR ZERO SPEED MS | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4506_2_AUX_IO | MCR1_R10:6:I.Data.02 | BC4506_2_AUX_IO:= MCR1_R10:6:I.Data.02; //BC 4506 FDBK FUEL SYSTEM BELT CONVEYOR ZERO SPEED MS |  | _BC4506_MS | P_DIn | Sts_PV | 1 | Fuel_Handling_TaskB | Task_B | _BC4506_MS | Fuel Handling
1195 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 03 | 1756-IA16 | 10 | 6 | 03 |  | I:107/3 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:6:I.Data.03 | // MCR1_R10:6:I.Data.03 SPARE
1196 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 04 | 1756-IA16 | 10 | 6 | 04 | BC4514_AUX | I:107/4 | BC | BC 4514 FDBK FUEL SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BC4514_AUX_IO | MCR1_R10:6:I.Data.04 | BC4514_AUX_IO:= MCR1_R10:6:I.Data.04; //BC 4514 FDBK FUEL SYSTEM BELT CONVEYOR |  | _BC4514_M01 | P_Motor | Sts_Running | 1 | Fuel_Handling_TaskC | Task_C | _BC4514_M01 | Fuel Handling
1197 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 05 | 1756-IA16 | 10 | 6 | 05 | BM1602_LUBE_LAL | I:107/5 |  | BM 1-602 LOW LUBE ALARM | [10 empty] | MCR1_R10 | I.Data | INPUT | BM1602_LUBE_LAL_IO | MCR1_R10:6:I.Data.05 | BM1602_LUBE_LAL_IO:= MCR1_R10:6:I.Data.05; //BM 1-602 LOW LUBE ALARM |  | NA | NA | NA | 0 | bar: Notes
1198 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 06 | 1756-IA16 | 10 | 6 | 06 | BE4446_JOG_SET | I:107/6 |  | BE 4446 JOG INSERTED BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4446_JOG_SET_IO | MCR1_R10:6:I.Data.06 | BE4446_JOG_SET_IO:= MCR1_R10:6:I.Data.06; //BE 4446 JOG INSERTED BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_M01 | P_Motor | Sts_Ext | 0 | Back_Handling_TaskC | Task_C | _BE4446_M01 | bar: Notes
1199 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 07 | 1756-IA16 | 10 | 6 | 07 | BE4446_PB_JOG | I:107/7 |  | BE 4446 JOG BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | I.Data | INPUT | BE4446_PB_JOG_IO | MCR1_R10:6:I.Data.07 | BE4446_PB_JOG_IO:= MCR1_R10:6:I.Data.07; //BE 4446 JOG BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_M01 | P_Motor | Sts_Jogging | 0 | Back_Handling_TaskC | Task_C | _BE4446_M01 | bar: Notes
1200 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 10 | 1756-IA16 | 10 | 6 | 08 | VF4504A_SSA | I:107/10 |  | VF 4504-A AUTO FUEL SYSTEM VIBRATORY FEEDER | [10 empty] | MCR1_R10 | I.Data | INPUT | VF4504A_SSA_IO | MCR1_R10:6:I.Data.08 | VF4504A_SSA_IO:= MCR1_R10:6:I.Data.08; //VF 4504-A AUTO FUEL SYSTEM VIBRATORY FEEDER |  | _VF4504A_SSA | P_DIn | Sts_PV | 1 | Fuel_Handling_TaskB | Task_B | _VF4504A_SSA | Fuel Handling | bar: Notes
1201 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 11 | 1756-IA16 | 10 | 6 | 09 |  | I:107/11 | [12 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:6:I.Data.09 | // MCR1_R10:6:I.Data.09
1202 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 12 | 1756-IA16 | 10 | 6 | 10 | VF4504B_SSA | I:107/12 |  | VF 4504-B AUTO FUEL SYSTEM VIBRATORY FEEDER | [10 empty] | MCR1_R10 | I.Data | INPUT | VF4504B_SSA_IO | MCR1_R10:6:I.Data.10 | VF4504B_SSA_IO:= MCR1_R10:6:I.Data.10; //VF 4504-B AUTO FUEL SYSTEM VIBRATORY FEEDER |  | _VF4504B_SSA | P_DIn | Sts_PV | 1 | Fuel_Handling_TaskB | Task_B | _VF4504B_SSA | Fuel Handling | bar: Notes
1203 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 13 | 1756-IA16 | 10 | 6 | 11 |  | I:107/13 | [12 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:6:I.Data.11 | // MCR1_R10:6:I.Data.11
1204 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 14 | 1756-IA16 | 10 | 6 | 12 | PM1602A1_AUX | I:107/14 |  | PM 1-602-A1 AUX IN | [10 empty] | MCR1_R10 | I.Data | INPUT | PM1602A1_AUX_IO | MCR1_R10:6:I.Data.12 | PM1602A1_AUX_IO:= MCR1_R10:6:I.Data.12; //PM 1-602-A1 AUX IN |  | _PM1602A1_M01 | P_Motor | Sts_Running
1205 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 15 | 1756-IA16 | 10 | 6 | 13 | PM1602A2_AUX | I:107/15 |  | PM 1-602-A2 AUX IN | [10 empty] | MCR1_R10 | I.Data | INPUT | PM1602A2_AUX_IO | MCR1_R10:6:I.Data.13 | PM1602A2_AUX_IO:= MCR1_R10:6:I.Data.13; //PM 1-602-A2 AUX IN |  | _PM1602A2_M01 | P_Motor | Sts_Running
1206 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 16 | 1756-IA16 | 10 | 6 | 14 | VF504A_PGE_PS | I:107/16 |  | VF-504-A PURGE SWITCH | [10 empty] | MCR1_R10 | I.Data | INPUT | VF504A_PGE_PS_IO | MCR1_R10:6:I.Data.14 | VF504A_PGE_PS_IO:= MCR1_R10:6:I.Data.14; //VF-504-A PURGE SWITCH |  | _VF504A_PGE_PS | P_DIn | Sts_PV | bar: Notes
1207 | MCR1 R10G7M- | 1771-IAD | 10 | 7 | 17 | 1756-IA16 | 10 | 6 | 15 | VF504B_PGE_PS | I:107/17 |  | VF-504-B PURGE SWITCH | [10 empty] | MCR1_R10 | I.Data | INPUT | VF504B_PGE_PS_IO | MCR1_R10:6:I.Data.15 | VF504B_PGE_PS_IO:= MCR1_R10:6:I.Data.15; //VF-504-B PURGE SWITCH |  | _VF504B_PGE_PS | P_DIn | Sts_PV | bar: Notes
1208 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 00 | 1756-IA16 | 10 | REMOVE | 00 |  | I:110/0 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.00 | // MCR1_R10:REMOVE:I.Data.00 SPARE
1209 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 01 | 1756-IA16 | 10 | REMOVE | 01 |  | I:110/1 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.01 | // MCR1_R10:REMOVE:I.Data.01 SPARE
1210 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 02 | 1756-IA16 | 10 | REMOVE | 02 |  | I:110/2 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.02 | // MCR1_R10:REMOVE:I.Data.02 SPARE
1211 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 03 | 1756-IA16 | 10 | REMOVE | 03 |  | I:110/3 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.03 | // MCR1_R10:REMOVE:I.Data.03 SPARE
1212 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 04 | 1756-IA16 | 10 | REMOVE | 04 |  | I:110/4 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.04 | // MCR1_R10:REMOVE:I.Data.04 SPARE
1213 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 05 | 1756-IA16 | 10 | REMOVE | 05 |  | I:110/5 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.05 | // MCR1_R10:REMOVE:I.Data.05 SPARE
1214 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 06 | 1756-IA16 | 10 | REMOVE | 06 |  | I:110/6 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.06 | // MCR1_R10:REMOVE:I.Data.06 SPARE
1215 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 07 | 1756-IA16 | 10 | REMOVE | 07 |  | I:110/7 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.07 | // MCR1_R10:REMOVE:I.Data.07 SPARE
1216 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 10 | 1756-IA16 | 10 | REMOVE | 08 |  | I:110/10 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.08 | // MCR1_R10:REMOVE:I.Data.08 SPARE
1217 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 11 | 1756-IA16 | 10 | REMOVE | 09 |  | I:110/11 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.09 | // MCR1_R10:REMOVE:I.Data.09 SPARE
1218 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 12 | 1756-IA16 | 10 | REMOVE | 10 |  | I:110/12 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.10 | // MCR1_R10:REMOVE:I.Data.10 SPARE
1219 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 13 | 1756-IA16 | 10 | REMOVE | 11 |  | I:110/13 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.11 | // MCR1_R10:REMOVE:I.Data.11 SPARE
1220 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 14 | 1756-IA16 | 10 | REMOVE | 12 |  | I:110/14 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.12 | // MCR1_R10:REMOVE:I.Data.12 SPARE
1221 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 15 | 1756-IA16 | 10 | REMOVE | 13 |  | I:110/15 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.13 | // MCR1_R10:REMOVE:I.Data.13 SPARE
1222 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 16 | 1756-IA16 | 10 | REMOVE | 14 |  | I:110/16 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.14 | // MCR1_R10:REMOVE:I.Data.14 SPARE
1223 | MCR1 R11G0M- | 1771-IAD | 11 | 8 | 17 | 1756-IA16 | 10 | REMOVE | 15 |  | I:110/17 |  | SPARE | [10 empty] | MCR1_R10 | I.Data | INPUT |  | MCR1_R10:REMOVE:I.Data.15 | // MCR1_R10:REMOVE:I.Data.15 SPARE
1224 | MCR1 R11G1M- | 1771-OFE2/B | 11 | 9 | CH1+ | 1756-OF8I | 10 | 14 | 0 | FN1605_SPT | N31:5 | FN | FN 1-605 VFD SPEED KILN 1 MILL EXHAUST FAN |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR1_R10 | O.Ch[ | OUTPUT | FN1605_SPT_IO | MCR1_R10:14:O.Ch[0].Data | MCR1_R10:14:O.Ch[0].Data:=FN1605_SPT_IO; //FN 1-605 VFD SPEED KILN 1 MILL EXHAUST FAN |  | _FN1605_SPT | P_AOut | Val
1225 | MCR1 R11G1M- | 1771-OFE2/B | 11 | 9 | CH2+ | 1756-OF8I | 10 | 14 | 1 | DG2420_SPT | N31:6 | DG | K2VORTEX GATE APC 420 DG2420 |  | EU: SPT; V.MIN: 4; V.MAX: 20 | MCR1_R10 | O.Ch[ | OUTPUT | DG2420_SPT_IO | MCR1_R10:14:O.Ch[1].Data | MCR1_R10:14:O.Ch[1].Data:=DG2420_SPT_IO; //K2VORTEX GATE APC 420 DG2420 |  | _DG2420_SPT | P_AOut | Out_CV | 0
1226 | MCR1 R11G1M- | 1771-OFE2/B | 11 | 9 | CH3+ | 1756-OF8I | 10 | 14 | 2 | DG2401_SPT | N31:7 | DG | K2VORTEX GATE BC-401 DG 2401 |  | EU: SPT; V.MIN: 4; V.MAX: 20 | MCR1_R10 | O.Ch[ | OUTPUT | DG2401_SPT_IO | MCR1_R10:14:O.Ch[2].Data | MCR1_R10:14:O.Ch[2].Data:=DG2401_SPT_IO; //K2VORTEX GATE BC-401 DG 2401 |  | _DG2401_SPT | P_AOut | Out_CV | 0 | Kiln2_Main_TaskC | Task_C | _DG2401
1227 | MCR1 R11G1M- | 1771-OFE2/B | 11 | 9 | CH4+ | 1756-OF8I | 10 | 14 | 3 | DG1420_SPT | N31:8 | DG | K1VORTEX GATE APC 420 DG 1420 |  | EU: SPT; V.MIN: 4; V.MAX: 20 | MCR1_R10 | O.Ch[ | OUTPUT | DG1420_SPT_IO | MCR1_R10:14:O.Ch[3].Data | MCR1_R10:14:O.Ch[3].Data:=DG1420_SPT_IO; //K1VORTEX GATE APC 420 DG 1420 |  | _DG1420_SPT | P_AOut | Out_CV | 0
1228 | [5 empty] | 1756-OF8I | 10 | 14 | 4 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:14:O.Ch[4].Data | // MCR1_R10:14:O.Ch[4].Data SPARE
1229 | [5 empty] | 1756-OF8I | 10 | 14 | 5 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:14:O.Ch[5].Data | // MCR1_R10:14:O.Ch[5].Data SPARE
1230 | [5 empty] | 1756-OF8I | 10 | 14 | 6 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:14:O.Ch[6].Data | // MCR1_R10:14:O.Ch[6].Data SPARE
1231 | [5 empty] | 1756-OF8I | 10 | 14 | 7 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:14:O.Ch[7].Data | // MCR1_R10:14:O.Ch[7].Data SPARE
1232 | MCR1 R11G2M- | 1771-OFE2 | 11 | 10 | CH1+ | 1756-OF8I | 10 | 15 | 0 | DG1401_SPT | N52:5 | DG | K1VORTEX GATE BC-401 DG 1401 |  | EU: SPT; V.MIN: 4; V.MAX: 20 | MCR1_R10 | O.Ch[ | OUTPUT | DG1401_SPT_IO | MCR1_R10:15:O.Ch[0].Data | MCR1_R10:15:O.Ch[0].Data:=DG1401_SPT_IO; //K1VORTEX GATE BC-401 DG 1401 |  | _DG1401_SPT | P_AOut | Out_CV | 0
1233 | MCR1 R11G2M- | 1771-OFE2 | 11 | 10 | CH2+ | 1756-OF8I | 10 | 15 | 1 | BC4504C_SPT | N52:6 | BC | BC 4504-C SPEED FUEL SYSTEM VFD BELT CONVEYOR |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR1_R10 | O.Ch[ | OUTPUT | BC4504C_SPT_IO | MCR1_R10:15:O.Ch[1].Data | MCR1_R10:15:O.Ch[1].Data:=BC4504C_SPT_IO; //BC 4504-C SPEED FUEL SYSTEM VFD BELT CONVEYOR |  | _BC4504C_SPT |  |  | 0
1234 | MCR1 R11G2M- | 1771-OFE2 | 11 | 10 | CH3+ | 1756-OF8I | 10 | 15 | 2 | VF4504A_SPT | N52:7 | VF | VF 4504-A SPEED FUEL SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR1_R10 | O.Ch[ | OUTPUT | VF4504A_SPT_IO | MCR1_R10:15:O.Ch[2].Data | MCR1_R10:15:O.Ch[2].Data:=VF4504A_SPT_IO; //VF 4504-A SPEED FUEL SYSTEM VFD VIBRATORY FEEDER |  | _VF4504A_SPT | P_VSD | Out_SpeedRef
1235 | MCR1 R11G2M- | 1771-OFE2 | 11 | 10 | CH4+ | 1756-OF8I | 10 | 15 | 3 | VF4504B_SPT | N52:8 | VF | VF 4504-B SPEED FUEL SYSTEM VFD VIBRATORY FEEDER |  | EU: % Speed; V.MIN: 0; V.MAX: 100 | MCR1_R10 | O.Ch[ | OUTPUT | VF4504B_SPT_IO | MCR1_R10:15:O.Ch[3].Data | MCR1_R10:15:O.Ch[3].Data:=VF4504B_SPT_IO; //VF 4504-B SPEED FUEL SYSTEM VFD VIBRATORY FEEDER |  | _VF4504B_SPT | P_VSD | Out_SpeedRef
1236 | [5 empty] | 1756-OF8I | 10 | 15 | 4 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:15:O.Ch[4].Data | // MCR1_R10:15:O.Ch[4].Data SPARE
1237 | [5 empty] | 1756-OF8I | 10 | 15 | 5 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:15:O.Ch[5].Data | // MCR1_R10:15:O.Ch[5].Data SPARE
1238 | [5 empty] | 1756-OF8I | 10 | 15 | 6 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:15:O.Ch[6].Data | // MCR1_R10:15:O.Ch[6].Data SPARE
1239 | [5 empty] | 1756-OF8I | 10 | 15 | 7 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Ch[ | OUTPUT |  | MCR1_R10:15:O.Ch[7].Data | // MCR1_R10:15:O.Ch[7].Data SPARE
1240 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH1 | 1756-IF16 | 10 | 11 | 0 | BE4403_IT | N53:0 | BE | BE 4403 AMPS BACK SYSTEM BUCKET ELEVATOR |  | EU: Ampers; V.MIN: 0; V.MAX: 30 | MCR1_R10 | I.Ch | INPUT | BE4403_IT_IO | MCR1_R10:11:I.Ch0Data | BE4403_IT_IO:= MCR1_R10:11:I.Ch0Data; //BE 4403 AMPS BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_IT | P_AIn | Val | 1 | Back_Handling_TaskD | Task_D | _BE4403_IT | Back LimeHandling
1241 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH2 | 1756-IF16 | 10 | 11 | 1 | SC4443_IT | N53:1 | SC | SC 4443 AMPS BACK SYSTEM SCREW CONVEYOR |  | EU: Ampers; V.MIN: 0; V.MAX: 40 | MCR1_R10 | I.Ch | INPUT | SC4443_IT_IO | MCR1_R10:11:I.Ch1Data | SC4443_IT_IO:= MCR1_R10:11:I.Ch1Data; //SC 4443 AMPS BACK SYSTEM SCREW CONVEYOR |  | _SC4443_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _SC4443_IT
1242 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH3 | 1756-IF16 | 10 | 11 | 2 | RC44441_IT | N53:2 | RC | RC 4444-1 AMPS BACK SYSTEM ROLL CRUSHER MOTOR #1 |  | EU: Ampers; V.MIN: 0; V.MAX: 60 | MCR1_R10 | I.Ch | INPUT | RC44441_IT_IO | MCR1_R10:11:I.Ch2Data | RC44441_IT_IO:= MCR1_R10:11:I.Ch2Data; //RC 4444-1 AMPS BACK SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC44441_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _RC44441_IT
1243 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH4 | 1756-IF16 | 10 | 11 | 3 | RC44442_IT | N53:3 | RC | RC 4444-2 AMPS BACK SYSTEM ROLL CRUSHER MOTOR #2 |  | EU: Ampers; V.MIN: 0; V.MAX: 60 | MCR1_R10 | I.Ch | INPUT | RC44442_IT_IO | MCR1_R10:11:I.Ch3Data | RC44442_IT_IO:= MCR1_R10:11:I.Ch3Data; //RC 4444-2 AMPS BACK SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC44442_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _RC44442_IT
1244 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH5 | 1756-IF16 | 10 | 11 | 4 | SC4445_IT | N53:4 | SC | SC 4445 AMPS BACK SYSTEM SCREW CONVEYOR |  | EU: Ampers; V.MIN: 0; V.MAX: 25 | MCR1_R10 | I.Ch | INPUT | SC4445_IT_IO | MCR1_R10:11:I.Ch4Data | SC4445_IT_IO:= MCR1_R10:11:I.Ch4Data; //SC 4445 AMPS BACK SYSTEM SCREW CONVEYOR |  | _SC4445_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _SC4445_IT
1245 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH6 | 1756-IF16 | 10 | 11 | 5 | VS4404_IT | N53:5 | VS | VS 4404 AMPS BACK SYSTEM VIBRATING SCREEN |  | EU: Ampers; V.MIN: 0; V.MAX: 30 | MCR1_R10 | I.Ch | INPUT | VS4404_IT_IO | MCR1_R10:11:I.Ch5Data | VS4404_IT_IO:= MCR1_R10:11:I.Ch5Data; //VS 4404 AMPS BACK SYSTEM VIBRATING SCREEN |  | _VS4404_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _VS4404_IT
1246 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH7 | 1756-IF16 | 10 | 11 | 6 | HM44051_IT | N53:6 | HM | HM 4405-1 AMPS BACK SYSTEM HAMMERMILL |  | EU: Ampers; V.MIN: 0; V.MAX: 240 | MCR1_R10 | I.Ch | INPUT | HM44051_IT_IO | MCR1_R10:11:I.Ch6Data | HM44051_IT_IO:= MCR1_R10:11:I.Ch6Data; //HM 4405-1 AMPS BACK SYSTEM HAMMERMILL |  | _HM44051_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _HM44051_IT
1247 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH8 | 1756-IF16 | 10 | 11 | 7 | SC1613A_IT | N53:7 | SC | SC 1-613A AMPS |  | EU: Ampers; V.MIN: 0; V.MAX: 15 | MCR1_R10 | I.Ch | INPUT | SC1613A_IT_IO | MCR1_R10:11:I.Ch7Data | SC1613A_IT_IO:= MCR1_R10:11:I.Ch7Data; //SC 1-613A AMPS |  | _SC1613A_IT | P_AIn | Val
1248 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH9 | 1756-IF16 | 10 | 11 | 8 | SC4447_IT | N53:8 | SC | SC 4447 AMPS BACK SYSTEM SCREW CONVEYOR |  | EU: Ampers; V.MIN: 0; V.MAX: 20 | MCR1_R10 | I.Ch | INPUT | SC4447_IT_IO | MCR1_R10:11:I.Ch8Data | SC4447_IT_IO:= MCR1_R10:11:I.Ch8Data; //SC 4447 AMPS BACK SYSTEM SCREW CONVEYOR |  | _SC4447_IT | P_AIn | Val |  | Back_Handling_TaskD | Task_D | _SC4447_IT
1249 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH10 | 1756-IF16 | 10 | 11 | 9 | BE4406W_IT | N53:9 | BE | BE 4406-W AMPS BACK SYSTEM BUCKET ELEVATOR |  | EU: Ampers; V.MIN: 0; V.MAX: 25 | MCR1_R10 | I.Ch | INPUT | BE4406W_IT_IO | MCR1_R10:11:I.Ch9Data | BE4406W_IT_IO:= MCR1_R10:11:I.Ch9Data; //BE 4406-W AMPS BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_IT | P_AIn | Val | 1 | Back_Handling_TaskD | Task_D | _BE4406W_IT | Back LimeHandling
1250 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH11 | 1756-IF16 | 10 | 11 | 10 | BE4406E_IT | N53:10 | BE | BE 4406-E AMPS BACK SYSTEM BUCKET ELEVATOR |  | EU: Ampers; V.MIN: 0; V.MAX: 25 | MCR1_R10 | I.Ch | INPUT | BE4406E_IT_IO | MCR1_R10:11:I.Ch10Data | BE4406E_IT_IO:= MCR1_R10:11:I.Ch10Data; //BE 4406-E AMPS BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_IT | P_AIn | Val | 1 | Back_Handling_TaskD | Task_D | _BE4406E_IT | Back LimeHandling
1251 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH12 | 1756-IF16 | 10 | 11 | 11 | SC4408C_IT | N53:11 | SC | SC 4408-C AMPS BACK SYSTEM SCREW CONVEYOR |  | EU: Ampers; V.MIN: 0; V.MAX: 25 | MCR1_R10 | I.Ch | INPUT | SC4408C_IT_IO | MCR1_R10:11:I.Ch11Data | SC4408C_IT_IO:= MCR1_R10:11:I.Ch11Data; //SC 4408-C AMPS BACK SYSTEM SCREW CONVEYOR |  | _SC4408C_IT | P_AIn | Val
1252 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH13 | 1756-IF16 | 10 | 11 | 12 | BE4446_IT | N53:12 | BE | BE 4446 AMPS BACK SYSTEM BUCKET ELEVATOR |  | EU: Ampers; V.MIN: 0; V.MAX: 55 | MCR1_R10 | I.Ch | INPUT | BE4446_IT_IO | MCR1_R10:11:I.Ch12Data | BE4446_IT_IO:= MCR1_R10:11:I.Ch12Data; //BE 4446 AMPS BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_IT | P_AIn | Val | 1 | Back_Handling_TaskD | Task_D | _BE4446_IT | Back LimeHandling
1253 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH14 | 1756-IF16 | 10 | 11 | 13 | FN1314_IT | N53:13 | FN | FN 1314 AMPS KILN 1 SEAL AIR FAN |  | EU: Ampers; V.MIN: 0; V.MAX: 200 | MCR1_R10 | I.Ch | INPUT | FN1314_IT_IO | MCR1_R10:11:I.Ch13Data | FN1314_IT_IO:= MCR1_R10:11:I.Ch13Data; //FN 1314 AMPS KILN 1 SEAL AIR FAN |  | _'FN1314_IT | P_AIn | Val
1254 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH15 | 1756-IF16 | 10 | 11 | 14 | BC4401_TE | N53:14 | BC | BC 4401 TEMPERATURE BACK SYSTEM BELT CONVEYOR PRODUCT |  | EU: °F; V.MIN: 0; V.MAX: 800 | MCR1_R10 | I.Ch | INPUT | BC4401_TE_IO | MCR1_R10:11:I.Ch14Data | BC4401_TE_IO:= MCR1_R10:11:I.Ch14Data; //BC 4401 TEMPERATURE BACK SYSTEM BELT CONVEYOR PRODUCT |  | _BC4401_TE | P_AIn | Val | 1 | Back_Handling_TaskD | Task_D | _BC4401_TE | Back LimeHandling
1255 | MCR1 R11G3M- | 1771-IFE | 11 | 11 | CH16 | 1756-IF16 | 10 | 11 | 15 | BC4402_LT | N53:15 | BC | BC 4402 % LOAD BACK SYSTEM VFD BELT CONVEYOR |  | EU: % Load; V.MIN: 0; V.MAX: 100 | MCR1_R10 | I.Ch | INPUT | BC4402_LT_IO | MCR1_R10:11:I.Ch15Data | BC4402_LT_IO:= MCR1_R10:11:I.Ch15Data; //BC 4402 % LOAD BACK SYSTEM VFD BELT CONVEYOR |  | _BC4402_LT | P_AIn | Val | 1 | Back_Handling_TaskD | Task_D | _BC4402_LT | Back LimeHandling
1256 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH1 | 1756-IF16 | 10 | 12 | 0 | FN1605_HZ | N31:22 | FN | FN 1-605 VFD HERTZ KILN 1 MILL EXHAUST FAN |  | EU: Hertz; V.MIN: 0; V.MAX: 60 | MCR1_R10 | I.Ch | INPUT | FN1605_HZ_IO | MCR1_R10:12:I.Ch0Data | FN1605_HZ_IO:= MCR1_R10:12:I.Ch0Data; //FN 1-605 VFD HERTZ KILN 1 MILL EXHAUST FAN |  | _FN1605_M01 | P_VSD | Out_SpeedRef |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _FN1605_M01
1257 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH2 | 1756-IF16 | 10 | 12 | 1 | FN1605_IT | N31:23 | FN | FN 1-605 VFD AMPS KILN 1 MILL EXHAUST FAN |  | EU: Ampers; V.MIN: 0; V.MAX: 150 | MCR1_R10 | I.Ch | INPUT | FN1605_IT_IO | MCR1_R10:12:I.Ch1Data | FN1605_IT_IO:= MCR1_R10:12:I.Ch1Data; //FN 1-605 VFD AMPS KILN 1 MILL EXHAUST FAN |  | _FN1605_IT | P_AIn | Val |  | Kiln1_Main_TaskD | Task_D | _FN1605_IT
1258 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH3 | 1756-IF16 | 10 | 12 | 2 | SC1613B_IT | N31:24 | SC | SC 1-613B AMPS |  | EU: Ampers; V.MIN: 0; V.MAX: 15 | MCR1_R10 | I.Ch | INPUT | SC1613B_IT_IO | MCR1_R10:12:I.Ch2Data | SC1613B_IT_IO:= MCR1_R10:12:I.Ch2Data; //SC 1-613B AMPS |  | _SC1613B_IT | P_AIn | Val
1259 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH4 | 1756-IF16 | 10 | 12 | 3 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:12:I.Ch3Data | // MCR1_R10:12:I.Ch3Data SPARE
1260 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH5 | 1756-IF16 | 10 | 12 | 4 | DG2420_ZT | N31:26 | DG | K2 VORTEX GATE APC 420 OPEN 0-100% DG2420 |  | EU: %; V.MIN: 0; V.MAX: 100 | MCR1_R10 | I.Ch | INPUT | DG2420_ZT_IO | MCR1_R10:12:I.Ch4Data | DG2420_ZT_IO:= MCR1_R10:12:I.Ch4Data; //K2 VORTEX GATE APC 420 OPEN 0-100% DG2420 |  | _DG2420_ZT | P_AIn | Val | 0
1261 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH6 | 1756-IF16 | 10 | 12 | 5 | DG2401_ZT | N31:27 | DG | K2 VORTEX GATE BC-401 OPEN 0-100% DG 2401 |  | EU: %; V.MIN: 0; V.MAX: 100 | MCR1_R10 | I.Ch | INPUT | DG2401_ZT_IO | MCR1_R10:12:I.Ch5Data | DG2401_ZT_IO:= MCR1_R10:12:I.Ch5Data; //K2 VORTEX GATE BC-401 OPEN 0-100% DG 2401 |  | _DG2401_ZT | P_AIn | Val | 0 | Kiln2_Main_TaskC | Task_C | _DG2401
1262 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH7 | 1756-IF16 | 10 | 12 | 6 | DG1420_ZT | N31:28 | DG | K1 VORTEX GATE APC 420 OPEN 0-100% DG 1420 |  | EU: %; V.MIN: 0; V.MAX: 100 | MCR1_R10 | I.Ch | INPUT | DG1420_ZT_IO | MCR1_R10:12:I.Ch6Data | DG1420_ZT_IO:= MCR1_R10:12:I.Ch6Data; //K1 VORTEX GATE APC 420 OPEN 0-100% DG 1420 |  | _DG1420_ZT | P_AIn | Val | 0
1263 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH8 | 1756-IF16 | 10 | 12 | 7 | DG1401_ZT | N31:29 | DG | K1 VORTEX GATE BC-401 OPEN 0-100% DG 1401 |  | EU: %; V.MIN: 0; V.MAX: 100 | MCR1_R10 | I.Ch | INPUT | DG1401_ZT_IO | MCR1_R10:12:I.Ch7Data | DG1401_ZT_IO:= MCR1_R10:12:I.Ch7Data; //K1 VORTEX GATE BC-401 OPEN 0-100% DG 1401 |  | _DG1401_ZT | P_AIn | Val | 0
1264 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH9 | 1756-IF16 | 10 | 12 | 8 | KN1BP_PT | N31:30 |  | K1 BURNER PIPE PRESSURE XMTR - |  | EU: "H2O; V.MIN: 0; V.MAX: 10 | MCR1_R10 | I.Ch | INPUT | KN1BP_PT_IO | MCR1_R10:12:I.Ch8Data | KN1BP_PT_IO:= MCR1_R10:12:I.Ch8Data; //K1 BURNER PIPE PRESSURE XMTR - |  | _KN1BP_PT | P_AIn | Val
1265 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH10 | 1756-IF16 | 10 | 12 | 9 | KN1HD_PT | N31:31 |  | K1HOOD DRAFT PRESSURE TRANSMITTER -1 TO 1" WC |  | EU: "WC; V.MIN: -1; V.MAX: 1 | MCR1_R10 | I.Ch | INPUT | KN1HD_PT_IO | MCR1_R10:12:I.Ch9Data | KN1HD_PT_IO:= MCR1_R10:12:I.Ch9Data; // K1HOOD DRAFT PRESSURE TRANSMITTER -1 TO 1" WC |  | _KN1HD_PT | P_AIn | Val
1266 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH11 | 1756-IF16 | 10 | 12 | 10 | KN1BM_DPT | N31:32 |  | KN1 BALL MILL DIFFERENTIAL PRESSURE XMTR 0-10"WC |  | EU: "WC; V.MIN: 0; V.MAX: 10 | MCR1_R10 | I.Ch | INPUT | KN1BM_DPT_IO | MCR1_R10:12:I.Ch10Data | KN1BM_DPT_IO:= MCR1_R10:12:I.Ch10Data; // KN1 BALL MILL DIFFERENTIAL PRESSURE XMTR 0-10"WC |  | _KN1BM_DPT | P_AIn | Val
1267 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH12 | 1756-IF16 | 10 | 12 | 11 |  | N31:33 |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:12:I.Ch11Data | // MCR1_R10:12:I.Ch11Data SPARE
1268 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH13 | 1756-IF16 | 10 | 12 | 12 |  | N31:34 |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:12:I.Ch12Data | // MCR1_R10:12:I.Ch12Data SPARE
1269 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH14 | 1756-IF16 | 10 | 12 | 13 | BM1602_IT | N31:35 | BM | 1-602 BALLMILL AMPS 0-150 |  | EU: Ampers; V.MIN: 0; V.MAX: 150 | MCR1_R10 | I.Ch | INPUT | BM1602_IT_IO | MCR1_R10:12:I.Ch13Data | BM1602_IT_IO:= MCR1_R10:12:I.Ch13Data; //1-602 BALLMILL AMPS 0-150 |  | _BM1602_IT | P_AIn | Val | 0 | Kiln1_Solid_Fuel_System_TaskD | Task_D | _BM1602_IT
1270 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH15 | 1756-IF16 | 10 | 12 | 14 | COALSILO_TE | N31:36 | SI | COAL SILO TEMP 4-20mA 0-500*F |  | EU: °F; V.MIN: 0; V.MAX: 500 | MCR1_R10 | I.Ch | INPUT | COALSILO_TE_IO | MCR1_R10:12:I.Ch14Data | COALSILO_TE_IO:= MCR1_R10:12:I.Ch14Data; //COAL SILO TEMP 4-20mA 0-500*F |  | _COALSILO_TE | P_AIn | Val | 0
1271 | MCR1 R11G4M- | 1771-IFE/A | 11 | 12 | CH16 | 1756-IF16 | 10 | 12 | 15 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:12:I.Ch15Data | // MCR1_R10:12:I.Ch15Data SPARE
1272 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-0 | 1756-OA16I | 10 | 7 | 0 |  | O:115/0 |  | DO NOT USE (Blown Fuse?) | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:7:O.Data.0 | // MCR1_R10:7:O.Data.0 DO NOT USE (Blown Fuse?)
1273 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-1 | 1756-OA16I | 10 | 7 | 1 | FN1605_1_COIL | O:115/1 | FN | FN 1605 RUN KILN 1 COAL EXHAUST FAN (NO COINCIDE) | [10 empty] | MCR1_R10 | O.Data | OUTPUT | FN1605_1_COIL_IO | MCR1_R10:7:O.Data.1 | MCR1_R10:7:O.Data.1:=FN1605_1_COIL_IO; //FN 1605 RUN KILN 1 COAL EXHAUST FAN (NO COINCIDE) |  | NA | NA | NA
1274 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-2 | 1756-OA16I | 10 | 7 | 2 | FN1335_COIL | O:115/2 | FN | FN 1308-A RUN KILN 1 NOSE RING FAN (NO COINCIDE) | [10 empty] | MCR1_R10 | O.Data | OUTPUT | FN1335_COIL_IO | MCR1_R10:7:O.Data.2 | MCR1_R10:7:O.Data.2:=FN1335_COIL_IO; //FN 1308-A RUN KILN 1 NOSE RING FAN (NO COINCIDE) |  | _FN1308A_M01 | P_Motor | PCmd_Start
1275 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-3 | 1756-OA16I | 10 | 7 | 3 |  | O:115/3 |  | SPARE (NO COINCIDE) | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:7:O.Data.3 | // MCR1_R10:7:O.Data.3 SPARE (NO COINCIDE) | bar: Notes to EU
1276 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-4 | 1756-OA16I | 10 | 7 | 4 | BV4518_COIL | O:115/4 | BV | BV 4518 RUN KILN 1 COAL BIN VIBRATOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BV4518_COIL_IO | MCR1_R10:7:O.Data.4 | MCR1_R10:7:O.Data.4:=BV4518_COIL_IO; //BV 4518 RUN KILN 1 COAL BIN VIBRATOR |  | _BV4518_M01 | P_Motor | PCmd_Start | 0
1277 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-5 | 1756-OA16I | 10 | 7 | 5 | RA1604_COIL | O:115/5 | RA | RA 1604 RUN KILN 1 COAL ROTARY AIRLOCK | [10 empty] | MCR1_R10 | O.Data | OUTPUT | RA1604_COIL_IO | MCR1_R10:7:O.Data.5 | MCR1_R10:7:O.Data.5:=RA1604_COIL_IO; //RA 1604 RUN KILN 1 COAL ROTARY AIRLOCK |  | _RA1604_M01 | P_Motor | PCmd_Start |  | Kiln1_Main_TaskC | Task_C | _RA1604_M01
1278 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-6 | 1756-OA16I | 10 | 7 | 6 | BM1602_COIL | O:115/6 | BM | BM 1602 RUN KILN 1 BALL MILL (MUST ENERGIZE) | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BM1602_COIL_IO | MCR1_R10:7:O.Data.6 | MCR1_R10:7:O.Data.6:=BM1602_COIL_IO; //BM 1602 RUN KILN 1 BALL MILL (MUST ENERGIZE) |  | _BM1602_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Solid_Fuel_System_TaskC | Task_C | _BM1602_M01 | Kiln 1 Solid Fuel System
1279 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-7 | 1756-OA16I | 10 | 7 | 7 | BM1602_YYS | O:115/7 |  | BM 1602 ENABLE KILN 1 BALL MILL | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BM1602_YYS_IO | MCR1_R10:7:O.Data.7 | MCR1_R10:7:O.Data.7:=BM1602_YYS_IO; //BM 1602 ENABLE KILN 1 BALL MILL |  | NA | NA | NA
1280 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-10 | 1756-OA16I | 10 | 7 | 8 | FN1341_COIL | O:115/10 | FN | FN 1341 RUN KILN 1 SEAL AIR FAN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | FN1341_COIL_IO | MCR1_R10:7:O.Data.8 | MCR1_R10:7:O.Data.8:=FN1341_COIL_IO; //FN 1341 RUN KILN 1 SEAL AIR FAN |  | _FN1341_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Main_TaskC | Task_C | _FN1341_M01 | Kiln 1 | bar: Notes
1281 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-11 | 1756-OA16I | 10 | 7 | 9 | BV4504C_COIL | O:115/11 | BV | BV 4504-C RUN FUEL SYSTEM BIN VIBRATOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BV4504C_COIL_IO | MCR1_R10:7:O.Data.9 | MCR1_R10:7:O.Data.9:=BV4504C_COIL_IO; //BV 4504-C RUN FUEL SYSTEM BIN VIBRATOR |  | _BV4504C_M01 | P_Motor | PCmd_Start | 1 |  |  |  | Fuel Handling | bar: Notes
1282 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-12 | 1756-OA16I | 10 | 7 | 10 | BC4506_COIL | O:115/12 | BC | BC 4506 RUN FUEL SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BC4506_COIL_IO | MCR1_R10:7:O.Data.10 | MCR1_R10:7:O.Data.10:=BC4506_COIL_IO; //BC 4506 RUN FUEL SYSTEM BELT CONVEYOR |  | _BC4506_M01 | P_VSD | PCmd_Start | 1 | Fuel_Handling_TaskC | Task_C | _BC4506_M01 | Fuel Handling
1283 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-13 | 1756-OA16I | 10 | 7 | 11 | BC4514_COIL | O:115/13 | BC | BC 4514 RUN FUEL SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BC4514_COIL_IO | MCR1_R10:7:O.Data.11 | MCR1_R10:7:O.Data.11:=BC4514_COIL_IO; //BC 4514 RUN FUEL SYSTEM BELT CONVEYOR |  | _BC4514_M01 | P_Motor | PCmd_Start | 1 | Fuel_Handling_TaskC | Task_C | _BC4514_M01 | Fuel Handling
1284 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-14 | 1756-OA16I | 10 | 7 | 12 | VF4504A_COIL | O:115/14 | VF | VF 4504-A RUN FUEL SYSTEM VIBRATING FEEDER | [10 empty] | MCR1_R10 | O.Data | OUTPUT | VF4504A_COIL_IO | MCR1_R10:7:O.Data.12 | MCR1_R10:7:O.Data.12:=VF4504A_COIL_IO; //VF 4504-A RUN FUEL SYSTEM VIBRATING FEEDER |  | _VF4504A_M01 | P_VSD | PCmd_StartFwd |  | Fuel_Handling_TaskC | Task_C | _VF4504A_M01
1285 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-15 | 1756-OA16I | 10 | 7 | 13 | VF4504B_COIL | O:115/15 | VF | VF 4504-B RUN FUEL SYSTEM VIBRATING FEEDER | [10 empty] | MCR1_R10 | O.Data | OUTPUT | VF4504B_COIL_IO | MCR1_R10:7:O.Data.13 | MCR1_R10:7:O.Data.13:=VF4504B_COIL_IO; //VF 4504-B RUN FUEL SYSTEM VIBRATING FEEDER |  | _VF4504B_M01 | P_VSD | PCmd_StartFwd |  | Fuel_Handling_TaskC | Task_C | _VF4504B_M01
1286 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-16 | 1756-OA16I | 10 | 7 | 14 | RC45051_COIL | O:115/16 | RC | RC 4505-1 RUN FUEL SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR1_R10 | O.Data | OUTPUT | RC45051_COIL_IO | MCR1_R10:7:O.Data.14 | MCR1_R10:7:O.Data.14:=RC45051_COIL_IO; //RC 4505-1 RUN FUEL SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC45051_M01 | P_Motor | PCmd_Start |  | Fuel_Handling_TaskC | Task_C | _RC45051_M01
1287 | MCR1 R11G5M- | 1771-ODD | 11 | 13 | L1-17 | 1756-OA16I | 10 | 7 | 15 | RC45052_COIL | O:115/17 | RC | RC 4505-2 RUN FUEL SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR1_R10 | O.Data | OUTPUT | RC45052_COIL_IO | MCR1_R10:7:O.Data.15 | MCR1_R10:7:O.Data.15:=RC45052_COIL_IO; //RC 4505-2 RUN FUEL SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC45052_M01 | P_Motor | PCmd_Start |  | Fuel_Handling_TaskC | Task_C | _RC45052_M01
1288 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-0 | 1756-OA16I | 10 | 8 | 0 |  | O:116/0 |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:8:O.Data.0 | // MCR1_R10:8:O.Data.0 SPARE | bar: Notes to EU
1289 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-1 | 1756-OA16I | 10 | 8 | 1 | HM44051_1_COIL | O:116/1 | HM | HM 4405-1 RUN BACK SYSTEM HAMMERMILL REVERSE | [10 empty] | MCR1_R10 | O.Data | OUTPUT | HM44051_1_COIL_IO | MCR1_R10:8:O.Data.1 | MCR1_R10:8:O.Data.1:=HM44051_1_COIL_IO; //HM 4405-1 RUN BACK SYSTEM HAMMERMILL REVERSE |  | _HM44051_1_COIL | P_Motor | PCmd_Start
1290 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-2 | 1756-OA16I | 10 | 8 | 2 | SC1613_COIL | O:116/2 | SC | SC 1613 RUN KILN 1 FUEL FEED SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC1613_COIL_IO | MCR1_R10:8:O.Data.2 | MCR1_R10:8:O.Data.2:=SC1613_COIL_IO; //SC 1613 RUN KILN 1 FUEL FEED SCREW CONVEYOR |  | _SC1613_M01 | P_Motor | PCmd_Start |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _SC1613_M01 | bar: Notes
1291 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-3 | 1756-OA16I | 10 | 8 | 3 | BM1602_YAY | O:116/3 |  | BM 1-602 START UP ALARM | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BM1602_YAY_IO | MCR1_R10:8:O.Data.3 | MCR1_R10:8:O.Data.3:=BM1602_YAY_IO; //BM 1-602 START UP ALARM |  | NA | NA | NA
1292 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-4 | 1756-OA16I | 10 | 8 | 4 | FN1605_YYS | O:116/4 |  | FN 1-605 VFD ENABLE KILN 1 MILL EXHAUST FAN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | FN1605_YYS_IO | MCR1_R10:8:O.Data.4 | MCR1_R10:8:O.Data.4:=FN1605_YYS_IO; //FN 1-605 VFD ENABLE KILN 1 MILL EXHAUST FAN |  | NA | NA | NA
1293 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-5 | 1756-OA16I | 10 | 8 | 5 | FN1605_2_COIL | O:116/5 | FN | FN 1-605 VFD RUN FWD KILN 1 MILL EXHAUST FAN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | FN1605_2_COIL_IO | MCR1_R10:8:O.Data.5 | MCR1_R10:8:O.Data.5:=FN1605_2_COIL_IO; //FN 1-605 VFD RUN FWD KILN 1 MILL EXHAUST FAN |  | _FN1605_M01 | P_VSD | PCmd_Start |  | Kiln1_Solid_Fuel_System_TaskC | Task_C | _FN1605_M01
1294 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-6 | 1756-OA16I | 10 | 8 | 6 | BC4504C_COIL | O:116/6 | BC | BC 4504-C RUN FUEL SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BC4504C_COIL_IO | MCR1_R10:8:O.Data.6 | MCR1_R10:8:O.Data.6:=BC4504C_COIL_IO; //BC 4504-C RUN FUEL SYSTEM BELT CONVEYOR |  | _BC4504C_M01 | P_VSD | PCmd_Start | 1 | Fuel_Handling_TaskC | Task_C | _BC4504C_M01 | Fuel Handling
1295 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-7 | 1756-OA16I | 10 | 8 | 7 | BM1602_LUBE_SV | O:116/7 |  | 1-602 BALL MILL LUBE SOLENOID VALVE | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BM1602_LUBE_SV_IO | MCR1_R10:8:O.Data.7 | MCR1_R10:8:O.Data.7:=BM1602_LUBE_SV_IO; //1-602 BALL MILL LUBE SOLENOID VALVE |  | NA | NA | NA | 0 | bar: Notes
1296 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-10 | 1756-OA16I | 10 | 8 | 8 |  | O:116/10 |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:8:O.Data.8 | // MCR1_R10:8:O.Data.8 SPARE
1297 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-11 | 1756-OA16I | 10 | 8 | 9 | BC4506_YAY | O:116/11 |  | BC 4506 & 4505-C ALARM HORN FUEL SYSTEM BELT CONVEYOR START WARNING | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BC4506_YAY_IO | MCR1_R10:8:O.Data.9 | MCR1_R10:8:O.Data.9:=BC4506_YAY_IO; //BC 4506 & 4505-C ALARM HORN FUEL SYSTEM BELT CONVEYOR START WARNING |  | _BC4506_YAY | P_Dout | PCmd_On | 1 | Fuel_Handling_TaskB | Task_B | _BC4506_YAY | Fuel Handling
1298 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-12 | 1756-OA16I | 10 | 8 | 10 | FN44141_COIL | O:116/12 | FN | FN 4414-1 RUN BACK SYSTEM DC FAN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | FN44141_COIL_IO | MCR1_R10:8:O.Data.10 | MCR1_R10:8:O.Data.10:=FN44141_COIL_IO; //FN 4414-1 RUN BACK SYSTEM DC FAN |  | _FN44141_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _FN44141_M01
1299 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-13 | 1756-OA16I | 10 | 8 | 11 | SC44142_COIL | O:116/13 | SC | SC 4414-2 RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC44142_COIL_IO | MCR1_R10:8:O.Data.11 | MCR1_R10:8:O.Data.11:=SC44142_COIL_IO; //SC 4414-2 RUN BACK SYSTEM SCREW CONVEYOR |  | _SC44142_M01 | P_Motor | PCmd_Start |  | Back_Handling2_TaskC | Task_C | _SC44142_M01
1300 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-14 | 1756-OA16I | 10 | 8 | 12 | SC4408_COIL | O:116/14 | SC | SC 4408 RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4408_COIL_IO | MCR1_R10:8:O.Data.12 | MCR1_R10:8:O.Data.12:=SC4408_COIL_IO; //SC 4408 RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4408_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4408_M01
1301 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-15 | 1756-OA16I | 10 | 8 | 13 | PM1602A1_COIL | O:116/15 | PM | PM 1-602-A1 RUN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | PM1602A1_COIL_IO | MCR1_R10:8:O.Data.13 | MCR1_R10:8:O.Data.13:=PM1602A1_COIL_IO; //PM 1-602-A1 RUN |  | _PM1602A1_M01 | P_Motor | PCmd_Start
1302 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-16 | 1756-OA16I | 10 | 8 | 14 | PM1602A2_COIL | O:116/16 | PM | PM 1-602-A2 RUN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | PM1602A2_COIL_IO | MCR1_R10:8:O.Data.14 | MCR1_R10:8:O.Data.14:=PM1602A2_COIL_IO; //PM 1-602-A2 RUN |  | _PM1602A2_M01 | P_Motor | PCmd_Start
1303 | MCR1 R11G6M- | 1771-ODD | 11 | 14 | L1-17 | 1756-OA16I | 10 | 8 | 15 | RA44144_COIL | O:116/17 | RA | RA 4414-4 RUN BACK SYSTEM ROTARY AIRLOCK | [10 empty] | MCR1_R10 | O.Data | OUTPUT | RA44144_COIL_IO | MCR1_R10:8:O.Data.15 | MCR1_R10:8:O.Data.15:=RA44144_COIL_IO; //RA 4414-4 RUN BACK SYSTEM ROTARY AIRLOCK |  | _RA44144_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _RA44144_M01
1304 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-0 | 1756-OA16I | 10 | 9 | 0 | BC4401_COIL | O:117/0 | BC | BC 4401 RUN BACK SYSTEM BELT CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BC4401_COIL_IO | MCR1_R10:9:O.Data.0 | MCR1_R10:9:O.Data.0:=BC4401_COIL_IO; //BC 4401 RUN BACK SYSTEM BELT CONVEYOR |  | _BC4401_M01 | P_Motor | PCmd_Start | 1 | Kiln1_Main_TaskC | Task_C | _BC4401_M01 | Back Handling
1305 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-1 | 1756-OA16I | 10 | 9 | 1 | BE4403_COIL | O:117/1 | BE | BE 4403 RUN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BE4403_COIL_IO | MCR1_R10:9:O.Data.1 | MCR1_R10:9:O.Data.1:=BE4403_COIL_IO; //BE 4403 RUN BACK SYSTEM BUCKET ELEVATOR |  | _BE4403_M01 | P_Motor | PCmd_Start | 1 | Back_Handling_TaskC | Task_C | _BE4403_M01 | Back LimeHandling
1306 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-2 | 1756-OA16I | 10 | 9 | 2 | SC4443_COIL | O:117/2 | SC | SC 4443 RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4443_COIL_IO | MCR1_R10:9:O.Data.2 | MCR1_R10:9:O.Data.2:=SC4443_COIL_IO; //SC 4443 RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4443_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4443_M01
1307 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-3 | 1756-OA16I | 10 | 9 | 3 | SC4445_COIL | O:117/3 | SC | SC 4445 RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4445_COIL_IO | MCR1_R10:9:O.Data.3 | MCR1_R10:9:O.Data.3:=SC4445_COIL_IO; //SC 4445 RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4445_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4445_M01
1308 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-4 | 1756-OA16I | 10 | 9 | 4 | RC44441_COIL | O:117/4 | RC | RC 4444-1 RUN BACK SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR1_R10 | O.Data | OUTPUT | RC44441_COIL_IO | MCR1_R10:9:O.Data.4 | MCR1_R10:9:O.Data.4:=RC44441_COIL_IO; //RC 4444-1 RUN BACK SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC44441_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _RC44441_M01
1309 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-5 | 1756-OA16I | 10 | 9 | 5 | RC44442_COIL | O:117/5 | RC | RC 4444-2 RUN BACK SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR1_R10 | O.Data | OUTPUT | RC44442_COIL_IO | MCR1_R10:9:O.Data.5 | MCR1_R10:9:O.Data.5:=RC44442_COIL_IO; //RC 4444-2 RUN BACK SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC44442_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _RC44442_M01
1310 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-6 | 1756-OA16I | 10 | 9 | 6 | BE4446_COIL | O:117/6 | BE | BE 4446 RUN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BE4446_COIL_IO | MCR1_R10:9:O.Data.6 | MCR1_R10:9:O.Data.6:=BE4446_COIL_IO; //BE 4446 RUN BACK SYSTEM BUCKET ELEVATOR |  | _BE4446_M01 | P_Motor | PCmd_Start | 1 | Back_Handling_TaskC | Task_C | _BE4446_M01 | Back LimeHandling
1311 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-7 | 1756-OA16I | 10 | 9 | 7 | VS4404_COIL | O:117/7 | VS | VS 4404 RUN BACK SYSTEM VIBRATING SCREEN | [10 empty] | MCR1_R10 | O.Data | OUTPUT | VS4404_COIL_IO | MCR1_R10:9:O.Data.7 | MCR1_R10:9:O.Data.7:=VS4404_COIL_IO; //VS 4404 RUN BACK SYSTEM VIBRATING SCREEN |  | _VS4404_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _VS4404_M01
1312 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-10 | 1756-OA16I | 10 | 9 | 8 | HM44051_2_COIL | O:117/10 | HM | HM 4405-1 RUN BACK SYSTEM HAMMERMILL | [10 empty] | MCR1_R10 | O.Data | OUTPUT | HM44051_2_COIL_IO | MCR1_R10:9:O.Data.8 | MCR1_R10:9:O.Data.8:=HM44051_2_COIL_IO; //HM 4405-1 RUN BACK SYSTEM HAMMERMILL |  | _HM44051_2_COIL | P_Motor | PCmd_Start
1313 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-11 | 1756-OA16I | 10 | 9 | 9 | SC4412_COIL | O:117/11 | SC | SC 4412 RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4412_COIL_IO | MCR1_R10:9:O.Data.9 | MCR1_R10:9:O.Data.9:=SC4412_COIL_IO; //SC 4412 RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4412_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4412_M01
1314 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-12 | 1756-OA16I | 10 | 9 | 10 | SC4447_COIL | O:117/12 | SC | SC 4447 RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4447_COIL_IO | MCR1_R10:9:O.Data.10 | MCR1_R10:9:O.Data.10:=SC4447_COIL_IO; //SC 4447 RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4447_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4447_M01
1315 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-13 | 1756-OA16I | 10 | 9 | 11 | BE4406W_COIL | O:117/13 | BE | BE 4406-W RUN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BE4406W_COIL_IO | MCR1_R10:9:O.Data.11 | MCR1_R10:9:O.Data.11:=BE4406W_COIL_IO; //BE 4406-W RUN BACK SYSTEM BUCKET ELEVATOR |  | _BE4406W_M01 | P_Motor | PCmd_Start | 1 | Back_Handling_TaskC | Task_C | _BE4406W_M01 | Back LimeHandling
1316 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-14 | 1756-OA16I | 10 | 9 | 12 | BE4406E_COIL | O:117/14 | BE | BE 4406-E RUN BACK SYSTEM BUCKET ELEVATOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | BE4406E_COIL_IO | MCR1_R10:9:O.Data.12 | MCR1_R10:9:O.Data.12:=BE4406E_COIL_IO; //BE 4406-E RUN BACK SYSTEM BUCKET ELEVATOR |  | _BE4406E_M01 | P_Motor | PCmd_Start | 1 | Back_Handling_TaskC | Task_C | _BE4406E_M01 | Back LimeHandling
1317 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-15 | 1756-OA16I | 10 | 9 | 13 | SC4408A_COIL | O:117/15 | SC | SC 4408-A RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4408A_COIL_IO | MCR1_R10:9:O.Data.13 | MCR1_R10:9:O.Data.13:=SC4408A_COIL_IO; //SC 4408-A RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4408A_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4408A_M01
1318 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-16 | 1756-OA16I | 10 | 9 | 14 | SC4408B_COIL | O:117/16 | SC | SC 4408-B RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4408B_COIL_IO | MCR1_R10:9:O.Data.14 | MCR1_R10:9:O.Data.14:=SC4408B_COIL_IO; //SC 4408-B RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4408B_M01 | P_Motor | PCmd_Start |  | Back_Handling_TaskC | Task_C | _SC4408B_M01
1319 | MCR1 R11G7M- | 1771-ODD | 11 | 15 | L1-17 | 1756-OA16I | 10 | 9 | 15 | SC4408C_COIL | O:117/17 | SC | SC 4408-C RUN BACK SYSTEM SCREW CONVEYOR | [10 empty] | MCR1_R10 | O.Data | OUTPUT | SC4408C_COIL_IO | MCR1_R10:9:O.Data.15 | MCR1_R10:9:O.Data.15:=SC4408C_COIL_IO; //SC 4408-C RUN BACK SYSTEM SCREW CONVEYOR |  | _SC4408C_M01 | P_Motor | PCmd_Start |  | Back_Handling2_TaskC | Task_C | _SC4408C_M01
1320 | BACK R12G0M- | 1771-IAD | 12 | 0 | 00 | 1756-IA16 | 12 | 0 | 00 | DG44421_ZS_BE4403 | I:120/0 |  | DG 4442-1 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4403 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44421_ZS_BE4403_IO | BackSystem_R12:0:I.Data.00 | DG44421_ZS_BE4403_IO:= BackSystem_R12:0:I.Data.00; //DG 4442-1 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4403 |  | _DG44421_ZS_BE4403 | P_DIn | Val | 0 | Back_Handling_TaskC | Task_C | _DG44421
1321 | BACK R12G0M- | 1771-IAD | 12 | 0 | 01 | 1756-IA16 | 12 | 0 | 01 | DG44421_ZS_DG4448 | I:120/1 |  | DG 4442-1 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4448 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44421_ZS_DG4448_IO | BackSystem_R12:0:I.Data.01 | DG44421_ZS_DG4448_IO:= BackSystem_R12:0:I.Data.01; //DG 4442-1 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4448 |  | _DG44421_ZS_DG4448 | P_DIn | Val | 0 | Back_Handling_TaskC | Task_C | _DG4448
1322 | BACK R12G0M- | 1771-IAD | 12 | 0 | 02 | 1756-IA16 | 12 | 0 | 02 | DG44422_ZS_SC4443 | I:120/2 |  | DG 4442-2 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4443 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44422_ZS_SC4443_IO | BackSystem_R12:0:I.Data.02 | DG44422_ZS_SC4443_IO:= BackSystem_R12:0:I.Data.02; //DG 4442-2 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4443 |  | _DG44422 | P_D4SD | Sts_St0 | 1 | Back_Handling_TaskC | Task_C | _DG44422 | Back LimeHandling
1323 | BACK R12G0M- | 1771-IAD | 12 | 0 | 03 | 1756-IA16 | 12 | 0 | 03 | DG4442_ZS_JUNK | I:120/3 |  | DG 4442-2 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO JUNK | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG4442_ZS_JUNK_IO | BackSystem_R12:0:I.Data.03 | DG4442_ZS_JUNK_IO:= BackSystem_R12:0:I.Data.03; //DG 4442-2 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO JUNK |  | _DG4442_ZS_JUNK | P_DIn | Val | 0
1324 | BACK R12G0M- | 1771-IAD | 12 | 0 | 04 | 1756-IA16 | 12 | 0 | 04 | DG4443_ZS_BE4406E | I:120/4 |  | DG 4442-3 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-E | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG4443_ZS_BE4406E_IO | BackSystem_R12:0:I.Data.04 | DG4443_ZS_BE4406E_IO:= BackSystem_R12:0:I.Data.04; //DG 4442-3 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-E |  | _DG4443 | P_D4SD | Sts_St1
1325 | BACK R12G0M- | 1771-IAD | 12 | 0 | 05 | 1756-IA16 | 12 | 0 | 05 | DG44423_ZS_BE4406W | I:120/5 |  | DG 4442-3 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-W | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44423_ZS_BE4406W_IO | BackSystem_R12:0:I.Data.05 | DG44423_ZS_BE4406W_IO:= BackSystem_R12:0:I.Data.05; //DG 4442-3 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-W |  | _DG44423 | P_D4SD | Sts_St1 | 1 | Back_Handling_TaskC | Task_C | _DG44423 | Back LimeHandling
1326 | BACK R12G0M- | 1771-IAD | 12 | 0 | 06 | 1756-IA16 | 12 | 0 | 06 | DG44424_ZS_BE4406W | I:120/6 |  | DG 4442-4 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-W | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44424_ZS_BE4406W_IO | BackSystem_R12:0:I.Data.06 | DG44424_ZS_BE4406W_IO:= BackSystem_R12:0:I.Data.06; //DG 4442-4 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-W |  | _DG44424 | P_D4SD | Sts_St0 | 1 | Back_Handling_TaskC | Task_C | _DG44424 | Back LimeHandling
1327 | BACK R12G0M- | 1771-IAD | 12 | 0 | 07 | 1756-IA16 | 12 | 0 | 07 | DG44424_ZS_BE4406E | I:120/7 |  | DG 4442-4 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-E | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44424_ZS_BE4406E_IO | BackSystem_R12:0:I.Data.07 | DG44424_ZS_BE4406E_IO:= BackSystem_R12:0:I.Data.07; //DG 4442-4 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-E |  | _DG44424 | P_D4SD | Sts_St1 | 1 | Back_Handling_TaskC | Task_C | _DG44424 | Back LimeHandling
1328 | BACK R12G0M- | 1771-IAD | 12 | 0 | 10 | 1756-IA16 | 12 | 0 | 08 | DG44425_ZS_SC4408 | I:120/10 |  | DG 4442-5 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44425_ZS_SC4408_IO | BackSystem_R12:0:I.Data.08 | DG44425_ZS_SC4408_IO:= BackSystem_R12:0:I.Data.08; //DG 4442-5 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408 |  | _DG44425 | P_D4SD | Sts_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44425 | Back LimeHandling
1329 | BACK R12G0M- | 1771-IAD | 12 | 0 | 11 | 1756-IA16 | 12 | 0 | 09 | DG44425_ZS_DG44426 | I:120/11 |  | DG 4442-5 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-6 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44425_ZS_DG44426_IO | BackSystem_R12:0:I.Data.09 | DG44425_ZS_DG44426_IO:= BackSystem_R12:0:I.Data.09; //DG 4442-5 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-6 |  | _DG44425 | P_D4SD | Sts_St0 | 1 | Back_Handling2_TaskC | Task_C | _DG44425 | Back LimeHandling
1330 | BACK R12G0M- | 1771-IAD | 12 | 0 | 12 | 1756-IA16 | 12 | 0 | 10 | DG44426_ZS_DG44429 | I:120/12 |  | DG 4442-6 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-9 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44426_ZS_DG44429_IO | BackSystem_R12:0:I.Data.10 | DG44426_ZS_DG44429_IO:= BackSystem_R12:0:I.Data.10; //DG 4442-6 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-9 |  | _DG44426 | P_D4SD | Sts_St0 | 1 | Back_Handling2_TaskC | Task_C | _DG44426 | Back LimeHandling
1331 | BACK R12G0M- | 1771-IAD | 12 | 0 | 13 | 1756-IA16 | 12 | 0 | 11 | DG44426_ZS_SC4408C | I:120/13 |  | DG 4442-6 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-C | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44426_ZS_SC4408C_IO | BackSystem_R12:0:I.Data.11 | DG44426_ZS_SC4408C_IO:= BackSystem_R12:0:I.Data.11; //DG 4442-6 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-C |  | _DG44426 | P_D4SD | Sts_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44426 | Back LimeHandling
1332 | BACK R12G0M- | 1771-IAD | 12 | 0 | 14 | 1756-IA16 | 12 | 0 | 12 | DG44427_ZS_DG44428 | I:120/14 |  | DG 4442-7 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-8 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44427_ZS_DG44428_IO | BackSystem_R12:0:I.Data.12 | DG44427_ZS_DG44428_IO:= BackSystem_R12:0:I.Data.12; //DG 4442-7 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-8 |  | _DG44427 | P_D4SD | Sts_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44427 | Back LimeHandling
1333 | BACK R12G0M- | 1771-IAD | 12 | 0 | 15 | 1756-IA16 | 12 | 0 | 13 | DG44427_ZS_SC4408 | I:120/15 |  | DG 4442-7 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44427_ZS_SC4408_IO | BackSystem_R12:0:I.Data.13 | DG44427_ZS_SC4408_IO:= BackSystem_R12:0:I.Data.13; //DG 4442-7 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408 |  | _DG44427 | P_D4SD | Sts_St0 | 1 | Back_Handling2_TaskC | Task_C | _DG44427 | Back LimeHandling
1334 | BACK R12G0M- | 1771-IAD | 12 | 0 | 16 | 1756-IA16 | 12 | 0 | 14 | DG44428_ZS_SC4408C | I:120/16 |  | DG 4442-8 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-C | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44428_ZS_SC4408C_IO | BackSystem_R12:0:I.Data.14 | DG44428_ZS_SC4408C_IO:= BackSystem_R12:0:I.Data.14; //DG 4442-8 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-C |  | _DG44428 | P_D4SD | Sts_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44428 | Back LimeHandling
1335 | BACK R12G0M- | 1771-IAD | 12 | 0 | 17 | 1756-IA16 | 12 | 0 | 15 | DG44428_ZS_DG44429 | I:120/17 |  | DG 4442-8 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-9 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44428_ZS_DG44429_IO | BackSystem_R12:0:I.Data.15 | DG44428_ZS_DG44429_IO:= BackSystem_R12:0:I.Data.15; //DG 4442-8 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO DG 4442-9 |  | _DG44428 | P_D4SD | Sts_St0 | 1 | Back_Handling2_TaskC | Task_C | _DG44428 | Back LimeHandling
1336 | BACK R12G1M- | 1771-IAD | 12 | 1 | 00 | 1756-IA16 | 12 | 1 | 00 | DG44429_ZS_SILO2 | I:121/0 |  | DG 4442-9 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SILO 2 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44429_ZS_SILO2_IO | BackSystem_R12:1:I.Data.00 | DG44429_ZS_SILO2_IO:= BackSystem_R12:1:I.Data.00; //DG 4442-9 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SILO 2 |  | _DG44429 | P_D4SD | Sts_St0 | 1 | Back_Handling2_TaskC | Task_C | _DG44429 | Back LimeHandling
1337 | BACK R12G1M- | 1771-IAD | 12 | 1 | 01 | 1756-IA16 | 12 | 1 | 01 | DG44429_ZS_SC4408B | I:121/1 |  | DG 4442-9 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-B | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG44429_ZS_SC4408B_IO | BackSystem_R12:1:I.Data.01 | DG44429_ZS_SC4408B_IO:= BackSystem_R12:1:I.Data.01; //DG 4442-9 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-B |  | _DG44429 | P_D4SD | Sts_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44429 | Back LimeHandling
1338 | BACK R12G1M- | 1771-IAD | 12 | 1 | 02 | 1756-IA16 | 12 | 1 | 02 | DG4449_ZS_SILO5 | I:121/2 |  | DG 4449 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SILO 5 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG4449_ZS_SILO5_IO | BackSystem_R12:1:I.Data.02 | DG4449_ZS_SILO5_IO:= BackSystem_R12:1:I.Data.02; //DG 4449 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SILO 5 |  | _DG4449 | P_D4SD | Sts_St1
1339 | BACK R12G1M- | 1771-IAD | 12 | 1 | 03 | 1756-IA16 | 12 | 1 | 03 | DG4449_ZS_SC4408A | I:121/3 |  | DG 4449 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-A | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG4449_ZS_SC4408A_IO | BackSystem_R12:1:I.Data.03 | DG4449_ZS_SC4408A_IO:= BackSystem_R12:1:I.Data.03; //DG 4449 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO SC 4408-A |  | _DG4449 | P_D4SD | Sts_St0
1340 | BACK R12G1M- | 1771-IAD | 12 | 1 | 04 | 1756-IA16 | 12 | 1 | 04 | DG4448_ZS_BE4406W | I:121/4 |  | DG 4448 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-W | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG4448_ZS_BE4406W_IO | BackSystem_R12:1:I.Data.04 | DG4448_ZS_BE4406W_IO:= BackSystem_R12:1:I.Data.04; //DG 4448 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-W |  | _DG4448 | P_D4SD | Sts_St1 |  | Back_Handling_TaskC | Task_C | _DG4448
1341 | BACK R12G1M- | 1771-IAD | 12 | 1 | 05 | 1756-IA16 | 12 | 1 | 05 | DG4448_ZS_BE4406E | I:121/5 |  | DG 4448 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-E | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG4448_ZS_BE4406E_IO | BackSystem_R12:1:I.Data.05 | DG4448_ZS_BE4406E_IO:= BackSystem_R12:1:I.Data.05; //DG 4448 LIMIT SWITCH BACK SYSTEM DIVERTER GATE TO BE 4406-E |  | _DG4448 | P_D4SD | Sts_St0 |  | Back_Handling_TaskC | Task_C | _DG4448
1342 | BACK R12G1M- | 1771-IAD | 12 | 1 | 06 | 1756-IA16 | 12 | 1 | 06 | SILO1_LAH | I:121/6 |  | ALARM BACK SYSTEM SILO 1 HIGH LEVEL | [10 empty] | BackSystem_R12 | I.Data | INPUT | SILO1_LAH_IO | BackSystem_R12:1:I.Data.06 | SILO1_LAH_IO:= BackSystem_R12:1:I.Data.06; //ALARM BACK SYSTEM SILO 1 HIGH LEVEL |  | _SILO1_LAH | P_DIn | Sts_PV
1343 | BACK R12G1M- | 1771-IAD | 12 | 1 | 07 | 1756-IA16 | 12 | 1 | 07 | SILO2_LAH | I:121/7 |  | ALARM BACK SYSTEM SILO 2 HIGH LEVEL | [10 empty] | BackSystem_R12 | I.Data | INPUT | SILO2_LAH_IO | BackSystem_R12:1:I.Data.07 | SILO2_LAH_IO:= BackSystem_R12:1:I.Data.07; //ALARM BACK SYSTEM SILO 2 HIGH LEVEL |  | _SILO2_LAH | P_DIn | Sts_PV
1344 | BACK R12G1M- | 1771-IAD | 12 | 1 | 10 | 1756-IA16 | 12 | 1 | 08 | SILO3_LAH | I:121/10 |  | ALARM BACK SYSTEM SILO 3 HIGH LEVEL | [10 empty] | BackSystem_R12 | I.Data | INPUT | SILO3_LAH_IO | BackSystem_R12:1:I.Data.08 | SILO3_LAH_IO:= BackSystem_R12:1:I.Data.08; //ALARM BACK SYSTEM SILO 3 HIGH LEVEL |  | _SILO3_LAH | P_DIn | Sts_PV
1345 | BACK R12G1M- | 1771-IAD | 12 | 1 | 11 | 1756-IA16 | 12 | 1 | 09 | SILO4_LAH | I:121/11 |  | ALARM BACK SYSTEM SILO 4 HIGH LEVEL | [10 empty] | BackSystem_R12 | I.Data | INPUT | SILO4_LAH_IO | BackSystem_R12:1:I.Data.09 | SILO4_LAH_IO:= BackSystem_R12:1:I.Data.09; //ALARM BACK SYSTEM SILO 4 HIGH LEVEL |  | _SILO4_LAH | P_DIn | Sts_PV
1346 | BACK R12G1M- | 1771-IAD | 12 | 1 | 12 | 1756-IA16 | 12 | 1 | 10 | SILO5_LAH | I:121/12 |  | ALARM BACK SYSTEM SILO 5 HIGH LEVEL | [10 empty] | BackSystem_R12 | I.Data | INPUT | SILO5_LAH_IO | BackSystem_R12:1:I.Data.10 | SILO5_LAH_IO:= BackSystem_R12:1:I.Data.10; //ALARM BACK SYSTEM SILO 5 HIGH LEVEL |  | _SILO5_LAH | P_DIn | Sts_PV
1347 | BACK R12G1M- | 1771-IAD | 12 | 1 | 13 | 1756-IA16 | 12 | 1 | 11 |  | I:121/13 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:1:I.Data.11 | // BackSystem_R12:1:I.Data.11 SPARE
1348 | BACK R12G1M- | 1771-IAD | 12 | 1 | 14 | 1756-IA16 | 12 | 1 | 12 | BC4401_PCD | I:121/14 |  | BC 4401 PLUGGED CHUTE DETECTOR | [10 empty] | BackSystem_R12 | I.Data | INPUT | BC4401_PCD_IO | BackSystem_R12:1:I.Data.12 | BC4401_PCD_IO:= BackSystem_R12:1:I.Data.12; //BC 4401 PLUGGED CHUTE DETECTOR |  | _BC4401_PCD | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BC4401_PCD | Back LimeHandling | bar: Notes
1349 | BACK R12G1M- | 1771-IAD | 12 | 1 | 15 | 1756-IA16 | 12 | 1 | 13 | DG444210_ZS_SC4408A | I:121/15 |  | DG 4442-10 TO SC 4408-A BACK SYSTEM DIVERTER GATE SILO 4 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG444210_ZS_SC4408A_IO | BackSystem_R12:1:I.Data.13 | DG444210_ZS_SC4408A_IO:= BackSystem_R12:1:I.Data.13; //DG 4442-10 TO SC 4408-A BACK SYSTEM DIVERTER GATE SILO 4 |  | _DG444210 | P_D4SD | Sts_St1 | 1 | Back_Handling_TaskC | Task_C | _DG444210 | Back LimeHandling
1350 | BACK R12G1M- | 1771-IAD | 12 | 1 | 16 | 1756-IA16 | 12 | 1 | 14 | DG444210_ZS_SC4408 | I:121/16 |  | DG 4442-10 TO SC 4408 BACK SYSTEM DIVERTER GATE SILO 1 | [10 empty] | BackSystem_R12 | I.Data | INPUT | DG444210_ZS_SC4408_IO | BackSystem_R12:1:I.Data.14 | DG444210_ZS_SC4408_IO:= BackSystem_R12:1:I.Data.14; //DG 4442-10 TO SC 4408 BACK SYSTEM DIVERTER GATE SILO 1 |  | _DG444210 | P_D4SD | Sts_St0 | 1 | Back_Handling_TaskC | Task_C | _DG444210 | Back LimeHandling
1351 | BACK R12G1M- | 1771-IAD | 12 | 1 | 17 | 1756-IA16 | 12 | 1 | 15 |  | I:121/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:1:I.Data.15 | // BackSystem_R12:1:I.Data.15 SPARE
1352 | BACK R12G2M- | 1771-IAD | 12 | 2 | 00 | 1756-IA16 | 12 | 2 | 00 |  | I:122/0 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.00 | // BackSystem_R12:2:I.Data.00
1353 | BACK R12G2M- | 1771-IAD | 12 | 2 | 01 | 1756-IA16 | 12 | 2 | 01 |  | I:122/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.01 | // BackSystem_R12:2:I.Data.01 SPARE | bar: Notes to EU
1354 | BACK R12G2M- | 1771-IAD | 12 | 2 | 02 | 1756-IA16 | 12 | 2 | 02 |  | I:122/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.02 | // BackSystem_R12:2:I.Data.02 SPARE | bar: Notes to EU
1355 | BACK R12G2M- | 1771-IAD | 12 | 2 | 03 | 1756-IA16 | 12 | 2 | 03 | BC4401_MS | I:122/3 | BC | BC 4401 MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | BC4401_MS_IO | BackSystem_R12:2:I.Data.03 | BC4401_MS_IO:= BackSystem_R12:2:I.Data.03; //BC 4401 MOTION SWITCH |  | _BC4401_MS | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BC4401_MS | Back LimeHandling
1356 | BACK R12G2M- | 1771-IAD | 12 | 2 | 04 | 1756-IA16 | 12 | 2 | 04 |  | I:122/4 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.04 | // BackSystem_R12:2:I.Data.04
1357 | BACK R12G2M- | 1771-IAD | 12 | 2 | 05 | 1756-IA16 | 12 | 2 | 05 |  | I:122/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.05 | // BackSystem_R12:2:I.Data.05 SPARE | bar: Notes to EU
1358 | BACK R12G2M- | 1771-IAD | 12 | 2 | 06 | 1756-IA16 | 12 | 2 | 06 |  | I:122/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.06 | // BackSystem_R12:2:I.Data.06 SPARE | bar: Notes to EU
1359 | BACK R12G2M- | 1771-IAD | 12 | 2 | 07 | 1756-IA16 | 12 | 2 | 07 | BE4403_MS | I:122/7 | BE | BE 4403 BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | BE4403_MS_IO | BackSystem_R12:2:I.Data.07 | BE4403_MS_IO:= BackSystem_R12:2:I.Data.07; //BE 4403 BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH |  | _BE4403_MS | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4403_MS | Back LimeHandling
1360 | BACK R12G2M- | 1771-IAD | 12 | 2 | 10 | 1756-IA16 | 12 | 2 | 08 |  | I:122/10 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.08 | // BackSystem_R12:2:I.Data.08
1361 | BACK R12G2M- | 1771-IAD | 12 | 2 | 11 | 1756-IA16 | 12 | 2 | 09 |  | I:122/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.09 | // BackSystem_R12:2:I.Data.09 SPARE | bar: Notes to EU
1362 | BACK R12G2M- | 1771-IAD | 12 | 2 | 12 | 1756-IA16 | 12 | 2 | 10 |  | I:122/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.10 | // BackSystem_R12:2:I.Data.10 SPARE | bar: Notes to EU
1363 | BACK R12G2M- | 1771-IAD | 12 | 2 | 13 | 1756-IA16 | 12 | 2 | 11 | SC4443_MS | I:122/13 | SC | SC 4443 ZERO SPEED SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4443_MS_IO | BackSystem_R12:2:I.Data.11 | SC4443_MS_IO:= BackSystem_R12:2:I.Data.11; //SC 4443 ZERO SPEED SWITCH |  | _SC4443_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4443_MS
1364 | BACK R12G2M- | 1771-IAD | 12 | 2 | 14 | 1756-IA16 | 12 | 2 | 12 |  | I:122/14 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.12 | // BackSystem_R12:2:I.Data.12 SPARE
1365 | BACK R12G2M- | 1771-IAD | 12 | 2 | 15 | 1756-IA16 | 12 | 2 | 13 |  | I:122/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.13 | // BackSystem_R12:2:I.Data.13 SPARE
1366 | BACK R12G2M- | 1771-IAD | 12 | 2 | 16 | 1756-IA16 | 12 | 2 | 14 |  | I:122/16 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.14 | // BackSystem_R12:2:I.Data.14 SPARE
1367 | BACK R12G2M- | 1771-IAD | 12 | 2 | 17 | 1756-IA16 | 12 | 2 | 15 |  | I:122/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:2:I.Data.15 | // BackSystem_R12:2:I.Data.15 SPARE
1368 | BACK R12G3M- | 1771-IAD | 12 | 3 | 00 | 1756-IA16 | 12 | 3 | 00 |  | I:123/0 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.00 | // BackSystem_R12:3:I.Data.00
1369 | BACK R12G3M- | 1771-IAD | 12 | 3 | 01 | 1756-IA16 | 12 | 3 | 01 |  | I:123/1 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.01 | // BackSystem_R12:3:I.Data.01
1370 | BACK R12G3M- | 1771-IAD | 12 | 3 | 02 | 1756-IA16 | 12 | 3 | 02 |  | I:123/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.02 | // BackSystem_R12:3:I.Data.02 SPARE | bar: Notes to EU
1371 | BACK R12G3M- | 1771-IAD | 12 | 3 | 03 | 1756-IA16 | 12 | 3 | 03 |  | I:123/3 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.03 | // BackSystem_R12:3:I.Data.03 SPARE | bar: Notes to EU
1372 | BACK R12G3M- | 1771-IAD | 12 | 3 | 04 | 1756-IA16 | 12 | 3 | 04 | RC44441_2_AUX | I:123/4 | RC | RC 4444-1 FDBK BACK SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | BackSystem_R12 | I.Data | INPUT | RC44441_2_AUX_IO | BackSystem_R12:3:I.Data.04 | RC44441_2_AUX_IO:= BackSystem_R12:3:I.Data.04; //RC 4444-1 FDBK BACK SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC44441_2_MS | P_DIn | Sts_PV
1373 | BACK R12G3M- | 1771-IAD | 12 | 3 | 05 | 1756-IA16 | 12 | 3 | 05 | RC44442_2_AUX | I:123/5 | RC | RC 4444-2 FDBK BACK SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | BackSystem_R12 | I.Data | INPUT | RC44442_2_AUX_IO | BackSystem_R12:3:I.Data.05 | RC44442_2_AUX_IO:= BackSystem_R12:3:I.Data.05; //RC 4444-2 FDBK BACK SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC44442_2_MS | P_DIn | Sts_PV
1374 | BACK R12G3M- | 1771-IAD | 12 | 3 | 06 | 1756-IA16 | 12 | 3 | 06 |  | I:123/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.06 | // BackSystem_R12:3:I.Data.06 SPARE | bar: Notes to EU
1375 | BACK R12G3M- | 1771-IAD | 12 | 3 | 07 | 1756-IA16 | 12 | 3 | 07 |  | I:123/7 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.07 | // BackSystem_R12:3:I.Data.07
1376 | BACK R12G3M- | 1771-IAD | 12 | 3 | 10 | 1756-IA16 | 12 | 3 | 08 |  | I:123/10 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.08 | // BackSystem_R12:3:I.Data.08 SPARE | bar: Notes to EU
1377 | BACK R12G3M- | 1771-IAD | 12 | 3 | 11 | 1756-IA16 | 12 | 3 | 09 |  | I:123/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.09 | // BackSystem_R12:3:I.Data.09 SPARE | bar: Notes to EU
1378 | BACK R12G3M- | 1771-IAD | 12 | 3 | 12 | 1756-IA16 | 12 | 3 | 10 | SC4445_MS | I:123/12 | SC | SC 4445 FDBK BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4445_MS_IO | BackSystem_R12:3:I.Data.10 | SC4445_MS_IO:= BackSystem_R12:3:I.Data.10; //SC 4445 FDBK BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4445_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4445_MS
1379 | BACK R12G3M- | 1771-IAD | 12 | 3 | 13 | 1756-IA16 | 12 | 3 | 11 |  | I:123/13 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.11 | // BackSystem_R12:3:I.Data.11
1380 | BACK R12G3M- | 1771-IAD | 12 | 3 | 14 | 1756-IA16 | 12 | 3 | 12 |  | I:123/14 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.12 | // BackSystem_R12:3:I.Data.12 SPARE
1381 | BACK R12G3M- | 1771-IAD | 12 | 3 | 15 | 1756-IA16 | 12 | 3 | 13 |  | I:123/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.13 | // BackSystem_R12:3:I.Data.13 SPARE
1382 | BACK R12G3M- | 1771-IAD | 12 | 3 | 16 | 1756-IA16 | 12 | 3 | 14 | BE4446_MS | I:123/16 | BE | BE 4446 FDBK BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | BE4446_MS_IO | BackSystem_R12:3:I.Data.14 | BE4446_MS_IO:= BackSystem_R12:3:I.Data.14; //BE 4446 FDBK BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH |  | _BE4446_MS | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4446_MS | Back LimeHandling
1383 | BACK R12G3M- | 1771-IAD | 12 | 3 | 17 | 1756-IA16 | 12 | 3 | 15 |  | I:123/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:3:I.Data.15 | // BackSystem_R12:3:I.Data.15 SPARE
1384 | BACK R12G4M- | 1771-IAD | 12 | 4 | 00 | 1756-IA16 | 12 | 4 | 00 |  | I:124/0 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.00 | // BackSystem_R12:4:I.Data.00 SPARE
1385 | BACK R12G4M- | 1771-IAD | 12 | 4 | 01 | 1756-IA16 | 12 | 4 | 01 |  | I:124/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.01 | // BackSystem_R12:4:I.Data.01 SPARE
1386 | BACK R12G4M- | 1771-IAD | 12 | 4 | 02 | 1756-IA16 | 12 | 4 | 02 |  | I:124/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.02 | // BackSystem_R12:4:I.Data.02 SPARE | bar: Notes to EU
1387 | BACK R12G4M- | 1771-IAD | 12 | 4 | 03 | 1756-IA16 | 12 | 4 | 03 |  | I:124/3 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.03 | // BackSystem_R12:4:I.Data.03 SPARE | bar: Notes to EU
1388 | BACK R12G4M- | 1771-IAD | 12 | 4 | 04 | 1756-IA16 | 12 | 4 | 04 |  | I:124/4 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.04 | // BackSystem_R12:4:I.Data.04 SPARE
1389 | BACK R12G4M- | 1771-IAD | 12 | 4 | 05 | 1756-IA16 | 12 | 4 | 05 |  | I:124/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.05 | // BackSystem_R12:4:I.Data.05 SPARE
1390 | BACK R12G4M- | 1771-IAD | 12 | 4 | 06 | 1756-IA16 | 12 | 4 | 06 |  | I:124/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.06 | // BackSystem_R12:4:I.Data.06 SPARE
1391 | BACK R12G4M- | 1771-IAD | 12 | 4 | 07 | 1756-IA16 | 12 | 4 | 07 |  | I:124/7 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.07 | // BackSystem_R12:4:I.Data.07
1392 | BACK R12G4M- | 1771-IAD | 12 | 4 | 10 | 1756-IA16 | 12 | 4 | 08 |  | I:124/10 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.08 | // BackSystem_R12:4:I.Data.08 SPARE | bar: Notes to EU
1393 | BACK R12G4M- | 1771-IAD | 12 | 4 | 11 | 1756-IA16 | 12 | 4 | 09 |  | I:124/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.09 | // BackSystem_R12:4:I.Data.09 SPARE | bar: Notes to EU
1394 | BACK R12G4M- | 1771-IAD | 12 | 4 | 12 | 1756-IA16 | 12 | 4 | 10 |  | I:124/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.10 | // BackSystem_R12:4:I.Data.10 SPARE
1395 | BACK R12G4M- | 1771-IAD | 12 | 4 | 13 | 1756-IA16 | 12 | 4 | 11 |  | I:124/13 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.11 | // BackSystem_R12:4:I.Data.11
1396 | BACK R12G4M- | 1771-IAD | 12 | 4 | 14 | 1756-IA16 | 12 | 4 | 12 |  | I:124/14 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.12 | // BackSystem_R12:4:I.Data.12 SPARE | bar: Notes to EU
1397 | BACK R12G4M- | 1771-IAD | 12 | 4 | 15 | 1756-IA16 | 12 | 4 | 13 |  | I:124/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.13 | // BackSystem_R12:4:I.Data.13 SPARE | bar: Notes to EU
1398 | BACK R12G4M- | 1771-IAD | 12 | 4 | 16 | 1756-IA16 | 12 | 4 | 14 | SC4447_MS | I:124/16 | TBD | SC 4447 BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4447_MS_IO | BackSystem_R12:4:I.Data.14 | SC4447_MS_IO:= BackSystem_R12:4:I.Data.14; //SC 4447 BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4447_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4447_MS
1399 | BACK R12G4M- | 1771-IAD | 12 | 4 | 17 | 1756-IA16 | 12 | 4 | 15 |  | I:124/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:4:I.Data.15 | // BackSystem_R12:4:I.Data.15 SPARE
1400 | BACK R12G5M- | 1771-IAD | 12 | 5 | 00 | 1756-IA16 | 12 | 5 | 00 |  | I:125/0 |  |  | PHYSICALLY VERIFY EIO TO RUN?? | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.00 | // BackSystem_R12:5:I.Data.00
1401 | BACK R12G5M- | 1771-IAD | 12 | 5 | 01 | 1756-IA16 | 12 | 5 | 01 |  | I:125/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.01 | // BackSystem_R12:5:I.Data.01 SPARE
1402 | BACK R12G5M- | 1771-IAD | 12 | 5 | 02 | 1756-IA16 | 12 | 5 | 02 |  | I:125/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.02 | // BackSystem_R12:5:I.Data.02 SPARE
1403 | BACK R12G5M- | 1771-IAD | 12 | 5 | 03 | 1756-IA16 | 12 | 5 | 03 | BE4406W_MS | I:125/3 | BE | BE 4406-W BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | BE4406W_MS_IO | BackSystem_R12:5:I.Data.03 | BE4406W_MS_IO:= BackSystem_R12:5:I.Data.03; //BE 4406-W BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH |  | _BE4406W_MS | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4406W_MS
1404 | BACK R12G5M- | 1771-IAD | 12 | 5 | 04 | 1756-IA16 | 12 | 5 | 04 |  | I:125/4 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.04 | // BackSystem_R12:5:I.Data.04 SPARE | bar: Notes to EU
1405 | BACK R12G5M- | 1771-IAD | 12 | 5 | 05 | 1756-IA16 | 12 | 5 | 05 |  | I:125/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.05 | // BackSystem_R12:5:I.Data.05 SPARE | bar: Notes to EU
1406 | BACK R12G5M- | 1771-IAD | 12 | 5 | 06 | 1756-IA16 | 12 | 5 | 06 |  | I:125/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.06 | // BackSystem_R12:5:I.Data.06 SPARE | bar: Notes to EU
1407 | BACK R12G5M- | 1771-IAD | 12 | 5 | 07 | 1756-IA16 | 12 | 5 | 07 | SC4408A_MS | I:125/7 | SC | SC 4408-A BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4408A_MS_IO | BackSystem_R12:5:I.Data.07 | SC4408A_MS_IO:= BackSystem_R12:5:I.Data.07; //SC 4408-A BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4408A_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4408A_MS
1408 | BACK R12G5M- | 1771-IAD | 12 | 5 | 10 | 1756-IA16 | 12 | 5 | 08 |  | I:125/10 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.08 | // BackSystem_R12:5:I.Data.08 SPARE | bar: Notes to EU
1409 | BACK R12G5M- | 1771-IAD | 12 | 5 | 11 | 1756-IA16 | 12 | 5 | 09 |  | I:125/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.09 | // BackSystem_R12:5:I.Data.09 SPARE | bar: Notes to EU
1410 | BACK R12G5M- | 1771-IAD | 12 | 5 | 12 | 1756-IA16 | 12 | 5 | 10 |  | I:125/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.10 | // BackSystem_R12:5:I.Data.10 SPARE | bar: Notes to EU
1411 | BACK R12G5M- | 1771-IAD | 12 | 5 | 13 | 1756-IA16 | 12 | 5 | 11 | SC4408B_MS | I:125/13 | SC | SC 4408-B BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4408B_MS_IO | BackSystem_R12:5:I.Data.11 | SC4408B_MS_IO:= BackSystem_R12:5:I.Data.11; //SC 4408-B BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4408B_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4408B_MS
1412 | BACK R12G5M- | 1771-IAD | 12 | 5 | 14 | 1756-IA16 | 12 | 5 | 12 |  | I:125/14 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.12 | // BackSystem_R12:5:I.Data.12
1413 | BACK R12G5M- | 1771-IAD | 12 | 5 | 15 | 1756-IA16 | 12 | 5 | 13 |  | I:125/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.13 | // BackSystem_R12:5:I.Data.13 SPARE | bar: EU
1414 | BACK R12G5M- | 1771-IAD | 12 | 5 | 16 | 1756-IA16 | 12 | 5 | 14 |  | I:125/16 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:5:I.Data.14 | // BackSystem_R12:5:I.Data.14 SPARE | bar: Notes to EU
1415 | BACK R12G5M- | 1771-IAD | 12 | 5 | 17 | 1756-IA16 | 12 | 5 | 15 | BE4406E_MS | I:125/17 | BE | BE 4406-E BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | BE4406E_MS_IO | BackSystem_R12:5:I.Data.15 | BE4406E_MS_IO:= BackSystem_R12:5:I.Data.15; //BE 4406-E BACK SYSTEM BUCKET ELEVATOR MOTION SWITCH |  | _BE4406E_MS | P_DIn | Sts_PV | 1 | Back_Handling_TaskB | Task_B | _BE4406E_MS | Back LimeHandling
1416 | BACK R12G6M- | 1771-IAD | 12 | 6 | 00 | 1756-IA16 | 12 | REMOVE | 00 |  | I:126/0 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.00 | // BackSystem_R12:REMOVE:I.Data.00 SPARE
1417 | BACK R12G6M- | 1771-IAD | 12 | 6 | 01 | 1756-IA16 | 12 | REMOVE | 01 |  | I:126/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.01 | // BackSystem_R12:REMOVE:I.Data.01 SPARE
1418 | BACK R12G6M- | 1771-IAD | 12 | 6 | 02 | 1756-IA16 | 12 | 6 | 02 |  | I:126/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.02 | // BackSystem_R12:6:I.Data.02 SPARE
1419 | BACK R12G6M- | 1771-IAD | 12 | 6 | 03 | 1756-IA16 | 12 | 6 | 03 | SC4408_MS | I:126/3 | SC | SC 4408 BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4408_MS_IO | BackSystem_R12:6:I.Data.03 | SC4408_MS_IO:= BackSystem_R12:6:I.Data.03; //SC 4408 BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4408_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4408_MS | Back LimeHandling
1420 | BACK R12G6M- | 1771-IAD | 12 | 6 | 04 | 1756-IA16 | 12 | 6 | 04 |  | I:126/4 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.04 | // BackSystem_R12:6:I.Data.04
1421 | BACK R12G6M- | 1771-IAD | 12 | 6 | 05 | 1756-IA16 | 12 | 6 | 05 |  | I:126/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.05 | // BackSystem_R12:6:I.Data.05 SPARE | bar: Notes to EU
1422 | BACK R12G6M- | 1771-IAD | 12 | 6 | 06 | 1756-IA16 | 12 | 6 | 06 |  | I:126/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.06 | // BackSystem_R12:6:I.Data.06 SPARE | bar: Notes to EU
1423 | BACK R12G6M- | 1771-IAD | 12 | 6 | 07 | 1756-IA16 | 12 | 6 | 07 | SC4408C_MS | I:126/7 | SC | SC 4408-C BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC4408C_MS_IO | BackSystem_R12:6:I.Data.07 | SC4408C_MS_IO:= BackSystem_R12:6:I.Data.07; //SC 4408-C BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4408C_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC4408C_MS
1424 | BACK R12G6M- | 1771-IAD | 12 | 6 | 10 | 1756-IA16 | 12 | 6 | 08 |  | I:126/10 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.08 | // BackSystem_R12:6:I.Data.08
1425 | BACK R12G6M- | 1771-IAD | 12 | 6 | 11 | 1756-IA16 | 12 | 6 | 09 |  | I:126/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.09 | // BackSystem_R12:6:I.Data.09 SPARE
1426 | BACK R12G6M- | 1771-IAD | 12 | 6 | 12 | 1756-IA16 | 12 | 6 | 10 |  | I:126/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.10 | // BackSystem_R12:6:I.Data.10 SPARE
1427 | BACK R12G6M- | 1771-IAD | 12 | 6 | 13 | 1756-IA16 | 12 | 6 | 11 |  | I:126/13 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.11 | // BackSystem_R12:6:I.Data.11 SPARE
1428 | BACK R12G6M- | 1771-IAD | 12 | 6 | 14 | 1756-IA16 | 12 | 6 | 12 |  | I:126/14 |  |  |  | Notes: Will remove wiring and logic | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.12 | // BackSystem_R12:6:I.Data.12
1429 | BACK R12G6M- | 1771-IAD | 12 | 6 | 15 | 1756-IA16 | 12 | 6 | 13 |  | I:126/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.13 | // BackSystem_R12:6:I.Data.13 SPARE | bar: EU
1430 | BACK R12G6M- | 1771-IAD | 12 | 6 | 16 | 1756-IA16 | 12 | 6 | 14 |  | I:126/16 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:6:I.Data.14 | // BackSystem_R12:6:I.Data.14 SPARE | bar: EU
1431 | BACK R12G6M- | 1771-IAD | 12 | 6 | 17 | 1756-IA16 | 12 | 6 | 15 | SC44122_MS | I:126/17 | SC | SC 4414-2 BACK SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | SC44122_MS_IO | BackSystem_R12:6:I.Data.15 | SC44122_MS_IO:= BackSystem_R12:6:I.Data.15; //SC 4414-2 BACK SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC44122_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _SC44122_MS
1432 | BACK R12G7M- | 1771-IAD | 12 | 7 | 00 | 1756-IA16 | 12 | REMOVE | 00 |  | I:127/0 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.00 | // BackSystem_R12:REMOVE:I.Data.00 SPARE
1433 | BACK R12G7M- | 1771-IAD | 12 | 7 | 01 | 1756-IA16 | 12 | REMOVE | 01 |  | I:127/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.01 | // BackSystem_R12:REMOVE:I.Data.01 SPARE
1434 | BACK R12G7M- | 1771-IAD | 12 | 7 | 02 | 1756-IA16 | 12 | REMOVE | 02 |  | I:127/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.02 | // BackSystem_R12:REMOVE:I.Data.02 SPARE
1435 | BACK R12G7M- | 1771-IAD | 12 | 7 | 03 | 1756-IA16 | 12 | REMOVE | 03 |  | I:127/3 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.03 | // BackSystem_R12:REMOVE:I.Data.03 SPARE
1436 | BACK R12G7M- | 1771-IAD | 12 | 7 | 04 | 1756-IA16 | 12 | REMOVE | 04 |  | I:127/4 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.04 | // BackSystem_R12:REMOVE:I.Data.04 SPARE
1437 | BACK R12G7M- | 1771-IAD | 12 | 7 | 05 | 1756-IA16 | 12 | REMOVE | 05 |  | I:127/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.05 | // BackSystem_R12:REMOVE:I.Data.05 SPARE
1438 | BACK R12G7M- | 1771-IAD | 12 | 7 | 06 | 1756-IA16 | 12 | REMOVE | 06 |  | I:127/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.06 | // BackSystem_R12:REMOVE:I.Data.06 SPARE
1439 | BACK R12G7M- | 1771-IAD | 12 | 7 | 07 | 1756-IA16 | 12 | REMOVE | 07 |  | I:127/7 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.07 | // BackSystem_R12:REMOVE:I.Data.07 SPARE
1440 | BACK R12G7M- | 1771-IAD | 12 | 7 | 10 | 1756-IA16 | 12 | REMOVE | 08 |  | I:127/10 | TBD | RA 4414-4 DISCONNECT BACK SYSTEM ROTARY AIRLOCK |  | Notes: RA4414_DISC -> 'PHYSICALLY VERIFY EIO TO RUN?? | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.08 | // BackSystem_R12:REMOVE:I.Data.08 RA 4414-4 DISCONNECT BACK SYSTEM ROTARY AIRLOCK
1441 | BACK R12G7M- | 1771-IAD | 12 | 7 | 11 | 1756-IA16 | 12 | REMOVE | 09 |  | I:127/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.09 | // BackSystem_R12:REMOVE:I.Data.09 SPARE | bar: Notes to EU
1442 | BACK R12G7M- | 1771-IAD | 12 | 7 | 12 | 1756-IA16 | 12 | REMOVE | 10 |  | I:127/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.10 | // BackSystem_R12:REMOVE:I.Data.10 SPARE | bar: Notes to EU
1443 | BACK R12G7M- | 1771-IAD | 12 | 7 | 13 | 1756-IA16 | 12 | 6 | 0 | RA44144_MS | I:127/13 | RA | RA 4414-4 BACK SYSTEM ROTARY AIRLOCK MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | RA44144_MS_IO | BackSystem_R12:6:I.Data.0 | RA44144_MS_IO:= BackSystem_R12:6:I.Data.0; //RA 4414-4 BACK SYSTEM ROTARY AIRLOCK MOTION SWITCH |  | _RA44144_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _RA44144_MS
1444 | BACK R12G7M- | 1771-IAD | 12 | 7 | 14 | 1756-IA16 | 12 | 6 | 1 | SILO6_LAH | I:127/14 |  | SILO 6 ALARM HYDRATE SYSTEM HIGH LEVEL | [10 empty] | BackSystem_R12 | I.Data | INPUT | SILO6_LAH_IO | BackSystem_R12:6:I.Data.1 | SILO6_LAH_IO:= BackSystem_R12:6:I.Data.1; //SILO 6 ALARM HYDRATE SYSTEM HIGH LEVEL |  | _SILO6_LAH | P_DIn | Sts_PV
1445 | BACK R12G7M- | 1771-IAD | 12 | 7 | 15 | 1756-IA16 | 12 | REMOVE | 13 |  | I:127/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.13 | // BackSystem_R12:REMOVE:I.Data.13 SPARE
1446 | BACK R12G7M- | 1771-IAD | 12 | 7 | 16 | 1756-IA16 | 12 | REMOVE | 14 |  | I:127/16 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.14 | // BackSystem_R12:REMOVE:I.Data.14 SPARE
1447 | BACK R12G7M- | 1771-IAD | 12 | 7 | 17 | 1756-IA16 | 12 | REMOVE | 15 |  | I:127/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.15 | // BackSystem_R12:REMOVE:I.Data.15 SPARE
1448 | BACK R13G0M- | 1771-IAD | 13 | 8 | 00 | 1756-IA16 | 12 | 7 | 00 |  | I:130/0 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.00 | // BackSystem_R12:7:I.Data.00 SPARE | bar: Notes to EU
1449 | BACK R13G0M- | 1771-IAD | 13 | 8 | 01 | 1756-IA16 | 12 | 7 | 01 |  | I:130/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.01 | // BackSystem_R12:7:I.Data.01 SPARE | bar: Notes to EU
1450 | BACK R13G0M- | 1771-IAD | 13 | 8 | 02 | 1756-IA16 | 12 | 7 | 02 |  | I:130/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.02 | // BackSystem_R12:7:I.Data.02 SPARE | bar: Notes to EU
1451 | BACK R13G0M- | 1771-IAD | 13 | 8 | 03 | 1756-IA16 | 12 | 7 | 03 |  | I:130/3 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.03 | // BackSystem_R12:7:I.Data.03 SPARE
1452 | BACK R13G0M- | 1771-IAD | 13 | 8 | 04 | 1756-IA16 | 12 | 7 | 04 |  | I:130/4 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.04 | // BackSystem_R12:7:I.Data.04 SPARE
1453 | BACK R13G0M- | 1771-IAD | 13 | 8 | 05 | 1756-IA16 | 12 | 7 | 05 |  | I:130/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.05 | // BackSystem_R12:7:I.Data.05 SPARE
1454 | BACK R13G0M- | 1771-IAD | 13 | 8 | 06 | 1756-IA16 | 12 | 7 | 06 |  | I:130/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.06 | // BackSystem_R12:7:I.Data.06 SPARE
1455 | BACK R13G0M- | 1771-IAD | 13 | 8 | 07 | 1756-IA16 | 12 | 7 | 07 | HM44022_MS | I:130/7 | HM | HM 4402-2 BACK SYSTEM HAMMERMILL MOTION SWITCH | [10 empty] | BackSystem_R12 | I.Data | INPUT | HM44022_MS_IO | BackSystem_R12:7:I.Data.07 | HM44022_MS_IO:= BackSystem_R12:7:I.Data.07; //HM 4402-2 BACK SYSTEM HAMMERMILL MOTION SWITCH |  | _HM44022_MS | P_DIn | Sts_PV |  | Back_Handling_TaskB | Task_B | _HM44022_MS
1456 | BACK R13G0M- | 1771-IAD | 13 | 8 | 10 | 1756-IA16 | 12 | 7 | 08 |  | I:130/10 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.08 | // BackSystem_R12:7:I.Data.08 SPARE
1457 | BACK R13G0M- | 1771-IAD | 13 | 8 | 11 | 1756-IA16 | 12 | 7 | 09 |  | I:130/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.09 | // BackSystem_R12:7:I.Data.09 SPARE
1458 | BACK R13G0M- | 1771-IAD | 13 | 8 | 12 | 1756-IA16 | 12 | 7 | 10 |  | I:130/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.10 | // BackSystem_R12:7:I.Data.10 SPARE
1459 | BACK R13G0M- | 1771-IAD | 13 | 8 | 13 | 1756-IA16 | 12 | 7 | 11 |  | I:130/13 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.11 | // BackSystem_R12:7:I.Data.11 SPARE
1460 | BACK R13G0M- | 1771-IAD | 13 | 8 | 14 | 1756-IA16 | 12 | 7 | 12 |  | I:130/14 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.12 | // BackSystem_R12:7:I.Data.12 SPARE
1461 | BACK R13G0M- | 1771-IAD | 13 | 8 | 15 | 1756-IA16 | 12 | 7 | 13 |  | I:130/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.13 | // BackSystem_R12:7:I.Data.13 SPARE
1462 | BACK R13G0M- | 1771-IAD | 13 | 8 | 16 | 1756-IA16 | 12 | 7 | 14 |  | I:130/16 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.14 | // BackSystem_R12:7:I.Data.14 SPARE
1463 | BACK R13G0M- | 1771-IAD | 13 | 8 | 17 | 1756-IA16 | 12 | 7 | 15 |  | I:130/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:7:I.Data.15 | // BackSystem_R12:7:I.Data.15 SPARE
1464 | BACK R13G1M- | 1771-IAD | 13 | 9 | 00 | 1756-IA16 | 12 | REMOVE | 00 |  | I:131/0 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.00 | // BackSystem_R12:REMOVE:I.Data.00 SPARE
1465 | BACK R13G1M- | 1771-IAD | 13 | 9 | 01 | 1756-IA16 | 12 | REMOVE | 01 |  | I:131/1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.01 | // BackSystem_R12:REMOVE:I.Data.01 SPARE
1466 | BACK R13G1M- | 1771-IAD | 13 | 9 | 02 | 1756-IA16 | 12 | REMOVE | 02 |  | I:131/2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.02 | // BackSystem_R12:REMOVE:I.Data.02 SPARE
1467 | BACK R13G1M- | 1771-IAD | 13 | 9 | 03 | 1756-IA16 | 12 | REMOVE | 03 |  | I:131/3 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.03 | // BackSystem_R12:REMOVE:I.Data.03 SPARE
1468 | BACK R13G1M- | 1771-IAD | 13 | 9 | 04 | 1756-IA16 | 12 | REMOVE | 04 |  | I:131/4 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.04 | // BackSystem_R12:REMOVE:I.Data.04 SPARE
1469 | BACK R13G1M- | 1771-IAD | 13 | 9 | 05 | 1756-IA16 | 12 | REMOVE | 05 |  | I:131/5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.05 | // BackSystem_R12:REMOVE:I.Data.05 SPARE
1470 | BACK R13G1M- | 1771-IAD | 13 | 9 | 06 | 1756-IA16 | 12 | REMOVE | 06 |  | I:131/6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.06 | // BackSystem_R12:REMOVE:I.Data.06 SPARE
1471 | BACK R13G1M- | 1771-IAD | 13 | 9 | 07 | 1756-IA16 | 12 | REMOVE | 07 |  | I:131/7 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.07 | // BackSystem_R12:REMOVE:I.Data.07 SPARE
1472 | BACK R13G1M- | 1771-IAD | 13 | 9 | 10 | 1756-IA16 | 12 | REMOVE | 08 |  | I:131/10 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.08 | // BackSystem_R12:REMOVE:I.Data.08 SPARE
1473 | BACK R13G1M- | 1771-IAD | 13 | 9 | 11 | 1756-IA16 | 12 | REMOVE | 09 |  | I:131/11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.09 | // BackSystem_R12:REMOVE:I.Data.09 SPARE
1474 | BACK R13G1M- | 1771-IAD | 13 | 9 | 12 | 1756-IA16 | 12 | REMOVE | 10 |  | I:131/12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.10 | // BackSystem_R12:REMOVE:I.Data.10 SPARE
1475 | BACK R13G1M- | 1771-IAD | 13 | 9 | 13 | 1756-IA16 | 12 | REMOVE | 11 |  | I:131/13 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.11 | // BackSystem_R12:REMOVE:I.Data.11 SPARE
1476 | BACK R13G1M- | 1771-IAD | 13 | 9 | 14 | 1756-IA16 | 12 | REMOVE | 12 |  | I:131/14 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.12 | // BackSystem_R12:REMOVE:I.Data.12 SPARE
1477 | BACK R13G1M- | 1771-IAD | 13 | 9 | 15 | 1756-IA16 | 12 | REMOVE | 13 |  | I:131/15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.13 | // BackSystem_R12:REMOVE:I.Data.13 SPARE
1478 | BACK R13G1M- | 1771-IAD | 13 | 9 | 16 | 1756-IA16 | 12 | REMOVE | 14 |  | I:131/16 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.14 | // BackSystem_R12:REMOVE:I.Data.14 SPARE
1479 | BACK R13G1M- | 1771-IAD | 13 | 9 | 17 | 1756-IA16 | 12 | REMOVE | 15 |  | I:131/17 |  | SPARE | [10 empty] | BackSystem_R12 | I.Data | INPUT |  | BackSystem_R12:REMOVE:I.Data.15 | // BackSystem_R12:REMOVE:I.Data.15 SPARE
1480 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-0 | 1756-OA16I | 12 | 8 | 0 |  | O:132/0 | [12 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.0 | // BackSystem_R12:8:O.Data.0
1481 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-1 | 1756-OA16I | 12 | 8 | 1 | DG44422_SV | O:132/1 | DG | DG 4442-2 RUN BACK SYSTEM SOLENOID TO JUNK | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG44422_SV_IO | BackSystem_R12:8:O.Data.1 | BackSystem_R12:8:O.Data.1:=DG44422_SV_IO; //DG 4442-2 RUN BACK SYSTEM SOLENOID TO JUNK |  | _DG44422 | P_D4SD | PCmd_St1 | 1 | Back_Handling_TaskC | Task_C | _DG44422 | Back Lime Handling
1482 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-2 | 1756-OA16I | 12 | 8 | 2 | DG44423_SV | O:132/2 | DG | DG 4442-3 RUN BACK SYSTEM SOLENOID TO BE 4406-W | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG44423_SV_IO | BackSystem_R12:8:O.Data.2 | BackSystem_R12:8:O.Data.2:=DG44423_SV_IO; //DG 4442-3 RUN BACK SYSTEM SOLENOID TO BE 4406-W |  | _DG44423 | P_D4SD | PCmd_St1 | 1 | Back_Handling_TaskC | Task_C | _DG44423 | Back Lime Handling
1483 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-3 | 1756-OA16I | 12 | 8 | 3 | DG44424_SV | O:132/3 | DG | DG 4442-4 RUN BACK SYSTEM SOLENOID TO BE 4406-E | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG44424_SV_IO | BackSystem_R12:8:O.Data.3 | BackSystem_R12:8:O.Data.3:=DG44424_SV_IO; //DG 4442-4 RUN BACK SYSTEM SOLENOID TO BE 4406-E |  | _DG44424 | P_D4SD | PCmd_St1 | 1 | Back_Handling_TaskC | Task_C | _DG44424 | Back Lime Handling
1484 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-4 | 1756-OA16I | 12 | 8 | 4 |  | O:132/4 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.4 | // BackSystem_R12:8:O.Data.4 SPARE
1485 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-5 | 1756-OA16I | 12 | 8 | 5 | DG44426_SV | O:132/5 | DG | DG 4442-6 RUN BACK SYSTEM SOLENOID TO SC 4408-C | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG44426_SV_IO | BackSystem_R12:8:O.Data.5 | BackSystem_R12:8:O.Data.5:=DG44426_SV_IO; //DG 4442-6 RUN BACK SYSTEM SOLENOID TO SC 4408-C |  | _DG44426 | P_D4SD | PCmd_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44426 | Back Lime Handling
1486 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-6 | 1756-OA16I | 12 | 8 | 6 | DG44427_SV | O:132/6 | DG | DG 4442-7 RUN BACK SYSTEM SOLENOID TO DG 4442-8 | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG44427_SV_IO | BackSystem_R12:8:O.Data.6 | BackSystem_R12:8:O.Data.6:=DG44427_SV_IO; //DG 4442-7 RUN BACK SYSTEM SOLENOID TO DG 4442-8 |  | _DG44427 | P_D4SD | PCmd_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44427 | Back Lime Handling
1487 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-7 | 1756-OA16I | 12 | 8 | 7 |  | O:132/7 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.7 | // BackSystem_R12:8:O.Data.7 SPARE
1488 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-10 | 1756-OA16I | 12 | 8 | 8 | DG44429_SV | O:132/10 | DG | DG 4442-9 RUN BACK SYSTEM SOLENOID TO SC 4408-B | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG44429_SV_IO | BackSystem_R12:8:O.Data.8 | BackSystem_R12:8:O.Data.8:=DG44429_SV_IO; //DG 4442-9 RUN BACK SYSTEM SOLENOID TO SC 4408-B |  | _DG44429 | P_D4SD | PCmd_St1 | 1 | Back_Handling2_TaskC | Task_C | _DG44429 | Back Lime Handling
1489 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-11 | 1756-OA16I | 12 | 8 | 9 |  | O:132/11 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.9 | // BackSystem_R12:8:O.Data.9 SPARE
1490 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-12 | 1756-OA16I | 12 | 8 | 10 | HM44022_COIL | O:132/12 | HM | HM 4402-2 RUN BACK SYSTEM HAMMERMILL | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | HM44022_COIL_IO | BackSystem_R12:8:O.Data.10 | BackSystem_R12:8:O.Data.10:=HM44022_COIL_IO; //HM 4402-2 RUN BACK SYSTEM HAMMERMILL |  | _HM44022_M01 | P_AOut | PCmd_Start |  | Back_Handling_TaskC | Task_C | _HM44022_M01
1491 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-13 | 1756-OA16I | 12 | 8 | 11 | DG444210_SV | O:132/13 | DG | DG 4442-10 RUN BACK SYSTEM SOLENOID TO SC 4408-A | [10 empty] | BackSystem_R12 | O.Data | OUTPUT | DG444210_SV_IO | BackSystem_R12:8:O.Data.11 | BackSystem_R12:8:O.Data.11:=DG444210_SV_IO; //DG 4442-10 RUN BACK SYSTEM SOLENOID TO SC 4408-A |  | _DG444210 | P_D4SD | PCmd_St1 | 1 | Back_Handling_TaskC | Task_C | _DG444210 | Back Lime Handling
1492 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-14 | 1756-OA16I | 12 | 8 | 12 |  | O:132/14 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.12 | // BackSystem_R12:8:O.Data.12 SPARE
1493 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-15 | 1756-OA16I | 12 | 8 | 13 |  | O:132/15 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.13 | // BackSystem_R12:8:O.Data.13 SPARE
1494 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-16 | 1756-OA16I | 12 | 8 | 14 |  | O:132/16 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.14 | // BackSystem_R12:8:O.Data.14 SPARE
1495 | BACK R13G2M- | 1771-ODD | 13 | 10 | L1-17 | 1756-OA16I | 12 | 8 | 15 |  | O:132/17 |  | SPARE | [10 empty] | BackSystem_R12 | O.Data | OUTPUT |  | BackSystem_R12:8:O.Data.15 | // BackSystem_R12:8:O.Data.15 SPARE
1496 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH1 | 1756-IF16 | 12 | 9 | 0 |  | N54:0 |  | SPARE (SILO 1 LEVEL BACK SYSTEM RAMSEY C-LEVEL) | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch0Data | // BackSystem_R12:9:I.Ch0Data SPARE (SILO 1 LEVEL BACK SYSTEM RAMSEY C-LEVEL)
1497 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH2 | 1756-IF16 | 12 | 9 | 1 |  | N54:1 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch1Data | // BackSystem_R12:9:I.Ch1Data SPARE
1498 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH3 | 1756-IF16 | 12 | 9 | 2 |  | N54:2 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch2Data | // BackSystem_R12:9:I.Ch2Data SPARE
1499 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH4 | 1756-IF16 | 12 | 9 | 3 |  | N54:3 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch3Data | // BackSystem_R12:9:I.Ch3Data SPARE
1500 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH5 | 1756-IF16 | 12 | 9 | 4 |  | N54:4 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch4Data | // BackSystem_R12:9:I.Ch4Data SPARE
1501 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH6 | 1756-IF16 | 12 | 9 | 5 |  | N54:5 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch5Data | // BackSystem_R12:9:I.Ch5Data SPARE
1502 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH7 | 1756-IF16 | 12 | 9 | 6 |  | N54:6 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch6Data | // BackSystem_R12:9:I.Ch6Data SPARE
1503 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH8 | 1756-IF16 | 12 | 9 | 7 |  | N54:7 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch7Data | // BackSystem_R12:9:I.Ch7Data SPARE
1504 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH9 | 1756-IF16 | 12 | 9 | 8 |  | N54:8 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch8Data | // BackSystem_R12:9:I.Ch8Data SPARE
1505 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH10 | 1756-IF16 | 12 | 9 | 9 |  | N54:9 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch9Data | // BackSystem_R12:9:I.Ch9Data SPARE
1506 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH11 | 1756-IF16 | 12 | 9 | 10 |  | N54:10 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch10Data | // BackSystem_R12:9:I.Ch10Data SPARE
1507 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH12 | 1756-IF16 | 12 | 9 | 11 |  | N54:11 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch11Data | // BackSystem_R12:9:I.Ch11Data SPARE
1508 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH13 | 1756-IF16 | 12 | 9 | 12 |  | N54:12 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch12Data | // BackSystem_R12:9:I.Ch12Data SPARE
1509 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH14 | 1756-IF16 | 12 | 9 | 13 |  | N54:13 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch13Data | // BackSystem_R12:9:I.Ch13Data SPARE
1510 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH15 | 1756-IF16 | 12 | 9 | 14 |  | N54:14 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch14Data | // BackSystem_R12:9:I.Ch14Data SPARE
1511 | BACK R13G7M- | 1771-IFE | 13 | 15 | CH16 | 1756-IF16 | 12 | 9 | 15 |  | N54:15 |  | SPARE | [10 empty] | BackSystem_R12 | I.Ch | INPUT |  | BackSystem_R12:9:I.Ch15Data | // BackSystem_R12:9:I.Ch15Data SPARE
1512 | CAP R20G0M- | 1771-IAD | 20 | 0 | 00 | 1756-IA16 | 20 | 0 | 00 | DA2313MOD1_ZSO_INLET | I:200/0 |  | MODULE 1 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD1_ZSO_INLET_IO | MCR5B_R20:0:I.Data.00 | DA2313MOD1_ZSO_INLET_IO:= MCR5B_R20:0:I.Data.00; //MODULE 1 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1513 | CAP R20G0M- | 1771-IAD | 20 | 0 | 01 | 1756-IA16 | 20 | 0 | 01 | DA2313MOD1_ZSC_INLET | I:200/1 |  | MODULE 1 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD1_ZSC_INLET_IO | MCR5B_R20:0:I.Data.01 | DA2313MOD1_ZSC_INLET_IO:= MCR5B_R20:0:I.Data.01; //MODULE 1 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1514 | CAP R20G0M- | 1771-IAD | 20 | 0 | 02 | 1756-IA16 | 20 | 0 | 02 | DA2313MOD1_ZSO_OUTLET | I:200/2 |  | MODULE 1 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD1_ZSO_OUTLET_IO | MCR5B_R20:0:I.Data.02 | DA2313MOD1_ZSO_OUTLET_IO:= MCR5B_R20:0:I.Data.02; //MODULE 1 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1515 | CAP R20G0M- | 1771-IAD | 20 | 0 | 03 | 1756-IA16 | 20 | 0 | 03 | DA2313MOD1_ZSC_OUTLET | I:200/3 |  | MODULE 1 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD1_ZSC_OUTLET_IO | MCR5B_R20:0:I.Data.03 | DA2313MOD1_ZSC_OUTLET_IO:= MCR5B_R20:0:I.Data.03; //MODULE 1 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1516 | CAP R20G0M- | 1771-IAD | 20 | 0 | 04 | 1756-IA16 | 20 | 0 | 04 | KN2313MOD1_SEQ | I:200/4 |  | MODULE 1 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD1_SEQ_IO | MCR5B_R20:0:I.Data.04 | KN2313MOD1_SEQ_IO:= MCR5B_R20:0:I.Data.04; //MODULE 1 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1517 | CAP R20G0M- | 1771-IAD | 20 | 0 | 05 | 1756-IA16 | 20 | 0 | 05 | KN2313MOD1_SEQ_ADVANCE | I:200/5 |  | MODULE 1 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD1_SEQ_ADVANCE_IO | MCR5B_R20:0:I.Data.05 | KN2313MOD1_SEQ_ADVANCE_IO:= MCR5B_R20:0:I.Data.05; //MODULE 1 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1518 | CAP R20G0M- | 1771-IAD | 20 | 0 | 06 | 1756-IA16 | 20 | 0 | 06 | RA23131_AUX | I:200/6 | RA | RA 2313-1 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23131_AUX_IO | MCR5B_R20:0:I.Data.06 | RA23131_AUX_IO:= MCR5B_R20:0:I.Data.06; //RA 2313-1 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23131_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23131_M01
1519 | CAP R20G0M- | 1771-IAD | 20 | 0 | 07 | 1756-IA16 | 20 | 0 | 07 | RA23131_MS | I:200/7 | RA | RA 2313-1 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23131_MS_IO | MCR5B_R20:0:I.Data.07 | RA23131_MS_IO:= MCR5B_R20:0:I.Data.07; //RA 2313-1 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23131_MS | P_DIn | Sts_PV
1520 | CAP R20G0M- | 1771-IAD | 20 | 0 | 10 | 1756-IA16 | 20 | 0 | 08 | DA2313MOD2_ZSO_INLET | I:200/10 |  | MODULE 2 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD2_ZSO_INLET_IO | MCR5B_R20:0:I.Data.08 | DA2313MOD2_ZSO_INLET_IO:= MCR5B_R20:0:I.Data.08; //MODULE 2 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1521 | CAP R20G0M- | 1771-IAD | 20 | 0 | 11 | 1756-IA16 | 20 | 0 | 09 | DA2313MOD2_ZSC_INLET | I:200/11 |  | MODULE 2 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD2_ZSC_INLET_IO | MCR5B_R20:0:I.Data.09 | DA2313MOD2_ZSC_INLET_IO:= MCR5B_R20:0:I.Data.09; //MODULE 2 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1522 | CAP R20G0M- | 1771-IAD | 20 | 0 | 12 | 1756-IA16 | 20 | 0 | 10 | DA2313MOD2_ZSO_OUTLET | I:200/12 |  | MODULE 2 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD2_ZSO_OUTLET_IO | MCR5B_R20:0:I.Data.10 | DA2313MOD2_ZSO_OUTLET_IO:= MCR5B_R20:0:I.Data.10; //MODULE 2 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1523 | CAP R20G0M- | 1771-IAD | 20 | 0 | 13 | 1756-IA16 | 20 | 0 | 11 | DA2313MOD2_ZSC_OUTLET | I:200/13 |  | MODULE 2 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD2_ZSC_OUTLET_IO | MCR5B_R20:0:I.Data.11 | DA2313MOD2_ZSC_OUTLET_IO:= MCR5B_R20:0:I.Data.11; //MODULE 2 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1524 | CAP R20G0M- | 1771-IAD | 20 | 0 | 14 | 1756-IA16 | 20 | 0 | 12 | KN2313MOD2_SEQ | I:200/14 |  | MODULE 2 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD2_SEQ_IO | MCR5B_R20:0:I.Data.12 | KN2313MOD2_SEQ_IO:= MCR5B_R20:0:I.Data.12; //MODULE 2 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1525 | CAP R20G0M- | 1771-IAD | 20 | 0 | 15 | 1756-IA16 | 20 | 0 | 13 | KN2313MOD2_SEQ_ADVANCE | I:200/15 |  | MODULE 2 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD2_SEQ_ADVANCE_IO | MCR5B_R20:0:I.Data.13 | KN2313MOD2_SEQ_ADVANCE_IO:= MCR5B_R20:0:I.Data.13; //MODULE 2 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1526 | CAP R20G0M- | 1771-IAD | 20 | 0 | 16 | 1756-IA16 | 20 | 0 | 14 | RA23132_AUX | I:200/16 | RA | RA 2313-2 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23132_AUX_IO | MCR5B_R20:0:I.Data.14 | RA23132_AUX_IO:= MCR5B_R20:0:I.Data.14; //RA 2313-2 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23132_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23132_M01
1527 | CAP R20G0M- | 1771-IAD | 20 | 0 | 17 | 1756-IA16 | 20 | 0 | 15 | RA23132_MS | I:200/17 | RA | RA 2313-2 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23132_MS_IO | MCR5B_R20:0:I.Data.15 | RA23132_MS_IO:= MCR5B_R20:0:I.Data.15; //RA 2313-2 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23132_MS | P_DIn | Sts_PV
1528 | CAP R20G1M- | 1771-IAD | 20 | 1 | 00 | 1756-IA16 | 20 | 1 | 00 | DA2313MOD3_ZSO_INLET | I:201/0 |  | MODULE 3 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD3_ZSO_INLET_IO | MCR5B_R20:1:I.Data.00 | DA2313MOD3_ZSO_INLET_IO:= MCR5B_R20:1:I.Data.00; //MODULE 3 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1529 | CAP R20G1M- | 1771-IAD | 20 | 1 | 01 | 1756-IA16 | 20 | 1 | 01 | DA2313MOD3_ZSC_INLET | I:201/1 |  | MODULE 3 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD3_ZSC_INLET_IO | MCR5B_R20:1:I.Data.01 | DA2313MOD3_ZSC_INLET_IO:= MCR5B_R20:1:I.Data.01; //MODULE 3 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1530 | CAP R20G1M- | 1771-IAD | 20 | 1 | 02 | 1756-IA16 | 20 | 1 | 02 | DA2313MOD3_ZSO_OUTLET | I:201/2 |  | MODULE 3 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD3_ZSO_OUTLET_IO | MCR5B_R20:1:I.Data.02 | DA2313MOD3_ZSO_OUTLET_IO:= MCR5B_R20:1:I.Data.02; //MODULE 3 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1531 | CAP R20G1M- | 1771-IAD | 20 | 1 | 03 | 1756-IA16 | 20 | 1 | 03 | DA2313MOD3_ZSC_OUTLET | I:201/3 |  | MODULE 3 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD3_ZSC_OUTLET_IO | MCR5B_R20:1:I.Data.03 | DA2313MOD3_ZSC_OUTLET_IO:= MCR5B_R20:1:I.Data.03; //MODULE 3 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1532 | CAP R20G1M- | 1771-IAD | 20 | 1 | 04 | 1756-IA16 | 20 | 1 | 04 | KN2313MOD3_SEQ | I:201/4 |  | MODULE 3 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD3_SEQ_IO | MCR5B_R20:1:I.Data.04 | KN2313MOD3_SEQ_IO:= MCR5B_R20:1:I.Data.04; //MODULE 3 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1533 | CAP R20G1M- | 1771-IAD | 20 | 1 | 05 | 1756-IA16 | 20 | 1 | 05 | KN2313MOD3_SEQ_ADVANCE | I:201/5 |  | MODULE 3 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD3_SEQ_ADVANCE_IO | MCR5B_R20:1:I.Data.05 | KN2313MOD3_SEQ_ADVANCE_IO:= MCR5B_R20:1:I.Data.05; //MODULE 3 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1534 | CAP R20G1M- | 1771-IAD | 20 | 1 | 06 | 1756-IA16 | 20 | 1 | 06 | RA23133_AUX | I:201/6 | RA | RA 2313-3 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23133_AUX_IO | MCR5B_R20:1:I.Data.06 | RA23133_AUX_IO:= MCR5B_R20:1:I.Data.06; //RA 2313-3 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23133_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23133_M01
1535 | CAP R20G1M- | 1771-IAD | 20 | 1 | 07 | 1756-IA16 | 20 | 1 | 07 | RA23133_MS | I:201/7 | RA | RA 2313-3 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23133_MS_IO | MCR5B_R20:1:I.Data.07 | RA23133_MS_IO:= MCR5B_R20:1:I.Data.07; //RA 2313-3 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23133_MS | P_DIn | Sts_PV
1536 | CAP R20G1M- | 1771-IAD | 20 | 1 | 10 | 1756-IA16 | 20 | 1 | 08 | DA2313MOD4_ZSO_INLET | I:201/10 |  | MODULE 4 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD4_ZSO_INLET_IO | MCR5B_R20:1:I.Data.08 | DA2313MOD4_ZSO_INLET_IO:= MCR5B_R20:1:I.Data.08; //MODULE 4 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1537 | CAP R20G1M- | 1771-IAD | 20 | 1 | 11 | 1756-IA16 | 20 | 1 | 09 | DA2313MOD4_ZSC_INLET | I:201/11 |  | MODULE 4 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD4_ZSC_INLET_IO | MCR5B_R20:1:I.Data.09 | DA2313MOD4_ZSC_INLET_IO:= MCR5B_R20:1:I.Data.09; //MODULE 4 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1538 | CAP R20G1M- | 1771-IAD | 20 | 1 | 12 | 1756-IA16 | 20 | 1 | 10 | DA2313MOD4_ZSO_OUTLET | I:201/12 |  | MODULE 4 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD4_ZSO_OUTLET_IO | MCR5B_R20:1:I.Data.10 | DA2313MOD4_ZSO_OUTLET_IO:= MCR5B_R20:1:I.Data.10; //MODULE 4 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1539 | CAP R20G1M- | 1771-IAD | 20 | 1 | 13 | 1756-IA16 | 20 | 1 | 11 | DA2313MOD4_ZSC_OUTLET | I:201/13 |  | MODULE 4 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD4_ZSC_OUTLET_IO | MCR5B_R20:1:I.Data.11 | DA2313MOD4_ZSC_OUTLET_IO:= MCR5B_R20:1:I.Data.11; //MODULE 4 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1540 | CAP R20G1M- | 1771-IAD | 20 | 1 | 14 | 1756-IA16 | 20 | 1 | 12 | KN2313MOD4_SEQ | I:201/14 |  | MODULE 4 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD4_SEQ_IO | MCR5B_R20:1:I.Data.12 | KN2313MOD4_SEQ_IO:= MCR5B_R20:1:I.Data.12; //MODULE 4 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1541 | CAP R20G1M- | 1771-IAD | 20 | 1 | 15 | 1756-IA16 | 20 | 1 | 13 | KN2313MOD4_SEQ_ADVANCE | I:201/15 |  | MODULE 4 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD4_SEQ_ADVANCE_IO | MCR5B_R20:1:I.Data.13 | KN2313MOD4_SEQ_ADVANCE_IO:= MCR5B_R20:1:I.Data.13; //MODULE 4 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1542 | CAP R20G1M- | 1771-IAD | 20 | 1 | 16 | 1756-IA16 | 20 | 1 | 14 | RA23134_AUX | I:201/16 | RA | RA 2313-4 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23134_AUX_IO | MCR5B_R20:1:I.Data.14 | RA23134_AUX_IO:= MCR5B_R20:1:I.Data.14; //RA 2313-4 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23134_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23134_M01
1543 | CAP R20G1M- | 1771-IAD | 20 | 1 | 17 | 1756-IA16 | 20 | 1 | 15 | RA23134_MS | I:201/17 | RA | RA 2313-4 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23134_MS_IO | MCR5B_R20:1:I.Data.15 | RA23134_MS_IO:= MCR5B_R20:1:I.Data.15; //RA 2313-4 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23134_MS | P_DIn | Sts_PV
1544 | CAP R20G2M- | 1771-IAD | 20 | 2 | 00 | 1756-IA16 | 20 | 2 | 00 | DA2313MOD5_ZSO_INLET | I:202/0 |  | MODULE 5 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD5_ZSO_INLET_IO | MCR5B_R20:2:I.Data.00 | DA2313MOD5_ZSO_INLET_IO:= MCR5B_R20:2:I.Data.00; //MODULE 5 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1545 | CAP R20G2M- | 1771-IAD | 20 | 2 | 01 | 1756-IA16 | 20 | 2 | 01 | DA2313MOD5_ZSC_INLET | I:202/1 |  | MODULE 5 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD5_ZSC_INLET_IO | MCR5B_R20:2:I.Data.01 | DA2313MOD5_ZSC_INLET_IO:= MCR5B_R20:2:I.Data.01; //MODULE 5 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1546 | CAP R20G2M- | 1771-IAD | 20 | 2 | 02 | 1756-IA16 | 20 | 2 | 02 | DA2313MOD5_ZSO_OUTLET | I:202/2 |  | MODULE 5 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD5_ZSO_OUTLET_IO | MCR5B_R20:2:I.Data.02 | DA2313MOD5_ZSO_OUTLET_IO:= MCR5B_R20:2:I.Data.02; //MODULE 5 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1547 | CAP R20G2M- | 1771-IAD | 20 | 2 | 03 | 1756-IA16 | 20 | 2 | 03 | DA2313MOD5_ZSC_OUTLET | I:202/3 |  | MODULE 5 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD5_ZSC_OUTLET_IO | MCR5B_R20:2:I.Data.03 | DA2313MOD5_ZSC_OUTLET_IO:= MCR5B_R20:2:I.Data.03; //MODULE 5 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1548 | CAP R20G2M- | 1771-IAD | 20 | 2 | 04 | 1756-IA16 | 20 | 2 | 04 | KN2313MOD5_SEQ | I:202/4 |  | MODULE 5 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD5_SEQ_IO | MCR5B_R20:2:I.Data.04 | KN2313MOD5_SEQ_IO:= MCR5B_R20:2:I.Data.04; //MODULE 5 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1549 | CAP R20G2M- | 1771-IAD | 20 | 2 | 05 | 1756-IA16 | 20 | 2 | 05 | KN2313MOD5_SEQ_ADVANCE | I:202/5 |  | MODULE 5 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD5_SEQ_ADVANCE_IO | MCR5B_R20:2:I.Data.05 | KN2313MOD5_SEQ_ADVANCE_IO:= MCR5B_R20:2:I.Data.05; //MODULE 5 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1550 | CAP R20G2M- | 1771-IAD | 20 | 2 | 06 | 1756-IA16 | 20 | 2 | 06 | RA23135_AUX | I:202/6 | RA | RA 2313-5 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23135_AUX_IO | MCR5B_R20:2:I.Data.06 | RA23135_AUX_IO:= MCR5B_R20:2:I.Data.06; //RA 2313-5 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23135_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23135_M01
1551 | CAP R20G2M- | 1771-IAD | 20 | 2 | 07 | 1756-IA16 | 20 | 2 | 07 | RA23135_MS | I:202/7 | RA | RA 2313-5 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23135_MS_IO | MCR5B_R20:2:I.Data.07 | RA23135_MS_IO:= MCR5B_R20:2:I.Data.07; //RA 2313-5 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23135_MS | P_DIn | Sts_PV
1552 | CAP R20G2M- | 1771-IAD | 20 | 2 | 10 | 1756-IA16 | 20 | 2 | 08 | DA2313MOD6_ZSO_INLET | I:202/10 |  | MODULE 6 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD6_ZSO_INLET_IO | MCR5B_R20:2:I.Data.08 | DA2313MOD6_ZSO_INLET_IO:= MCR5B_R20:2:I.Data.08; //MODULE 6 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1553 | CAP R20G2M- | 1771-IAD | 20 | 2 | 11 | 1756-IA16 | 20 | 2 | 09 | DA2313MOD6_ZSC_INLET | I:202/11 |  | MODULE 6 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD6_ZSC_INLET_IO | MCR5B_R20:2:I.Data.09 | DA2313MOD6_ZSC_INLET_IO:= MCR5B_R20:2:I.Data.09; //MODULE 6 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1554 | CAP R20G2M- | 1771-IAD | 20 | 2 | 12 | 1756-IA16 | 20 | 2 | 10 | DA2313MOD6_ZSO_OUTLET | I:202/12 |  | MODULE 6 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD6_ZSO_OUTLET_IO | MCR5B_R20:2:I.Data.10 | DA2313MOD6_ZSO_OUTLET_IO:= MCR5B_R20:2:I.Data.10; //MODULE 6 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1555 | CAP R20G2M- | 1771-IAD | 20 | 2 | 13 | 1756-IA16 | 20 | 2 | 11 | DA2313MOD6_ZSC_OUTLET | I:202/13 |  | MODULE 6 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD6_ZSC_OUTLET_IO | MCR5B_R20:2:I.Data.11 | DA2313MOD6_ZSC_OUTLET_IO:= MCR5B_R20:2:I.Data.11; //MODULE 6 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1556 | CAP R20G2M- | 1771-IAD | 20 | 2 | 14 | 1756-IA16 | 20 | 2 | 12 | KN2313MOD6_SEQ | I:202/14 |  | MODULE 6 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD6_SEQ_IO | MCR5B_R20:2:I.Data.12 | KN2313MOD6_SEQ_IO:= MCR5B_R20:2:I.Data.12; //MODULE 6 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1557 | CAP R20G2M- | 1771-IAD | 20 | 2 | 15 | 1756-IA16 | 20 | 2 | 13 | KN2313MOD6_SEQ_ADVANCE | I:202/15 |  | MODULE 6 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD6_SEQ_ADVANCE_IO | MCR5B_R20:2:I.Data.13 | KN2313MOD6_SEQ_ADVANCE_IO:= MCR5B_R20:2:I.Data.13; //MODULE 6 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1558 | CAP R20G2M- | 1771-IAD | 20 | 2 | 16 | 1756-IA16 | 20 | 2 | 14 | RA23136_AUX | I:202/16 | RA | RA 2313-6 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23136_AUX_IO | MCR5B_R20:2:I.Data.14 | RA23136_AUX_IO:= MCR5B_R20:2:I.Data.14; //RA 2313-6 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23136_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23136_M01
1559 | CAP R20G2M- | 1771-IAD | 20 | 2 | 17 | 1756-IA16 | 20 | 2 | 15 | RA23136_MS | I:202/17 | RA | RA 2313-6 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23136_MS_IO | MCR5B_R20:2:I.Data.15 | RA23136_MS_IO:= MCR5B_R20:2:I.Data.15; //RA 2313-6 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23136_MS | P_DIn | Sts_PV
1560 | CAP R20G3M- | 1771-IAD | 20 | 3 | 00 | 1756-IA16 | 20 | 3 | 00 | DA2313MOD7_ZSO_INLET | I:203/0 |  | MODULE 7 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD7_ZSO_INLET_IO | MCR5B_R20:3:I.Data.00 | DA2313MOD7_ZSO_INLET_IO:= MCR5B_R20:3:I.Data.00; //MODULE 7 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1561 | CAP R20G3M- | 1771-IAD | 20 | 3 | 01 | 1756-IA16 | 20 | 3 | 01 | DA2313MOD7_ZSC_INLET | I:203/1 |  | MODULE 7 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD7_ZSC_INLET_IO | MCR5B_R20:3:I.Data.01 | DA2313MOD7_ZSC_INLET_IO:= MCR5B_R20:3:I.Data.01; //MODULE 7 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1562 | CAP R20G3M- | 1771-IAD | 20 | 3 | 02 | 1756-IA16 | 20 | 3 | 02 | DA2313MOD7_ZSO_OUTLET | I:203/2 |  | MODULE 7 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD7_ZSO_OUTLET_IO | MCR5B_R20:3:I.Data.02 | DA2313MOD7_ZSO_OUTLET_IO:= MCR5B_R20:3:I.Data.02; //MODULE 7 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1563 | CAP R20G3M- | 1771-IAD | 20 | 3 | 03 | 1756-IA16 | 20 | 3 | 03 | DA2313MOD7_ZSC_OUTLET | I:203/3 |  | MODULE 7 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD7_ZSC_OUTLET_IO | MCR5B_R20:3:I.Data.03 | DA2313MOD7_ZSC_OUTLET_IO:= MCR5B_R20:3:I.Data.03; //MODULE 7 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1564 | CAP R20G3M- | 1771-IAD | 20 | 3 | 04 | 1756-IA16 | 20 | 3 | 04 | KN2313MOD7_SEQ | I:203/4 |  | MODULE 7 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD7_SEQ_IO | MCR5B_R20:3:I.Data.04 | KN2313MOD7_SEQ_IO:= MCR5B_R20:3:I.Data.04; //MODULE 7 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1565 | CAP R20G3M- | 1771-IAD | 20 | 3 | 05 | 1756-IA16 | 20 | 3 | 05 | KN2313MOD7_SEQ_ADVANCE | I:203/5 |  | MODULE 7 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD7_SEQ_ADVANCE_IO | MCR5B_R20:3:I.Data.05 | KN2313MOD7_SEQ_ADVANCE_IO:= MCR5B_R20:3:I.Data.05; //MODULE 7 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1566 | CAP R20G3M- | 1771-IAD | 20 | 3 | 06 | 1756-IA16 | 20 | 3 | 06 | RA23137_AUX | I:203/6 | RA | RA 2313-7 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23137_AUX_IO | MCR5B_R20:3:I.Data.06 | RA23137_AUX_IO:= MCR5B_R20:3:I.Data.06; //RA 2313-7 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23137_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23137_M01
1567 | CAP R20G3M- | 1771-IAD | 20 | 3 | 07 | 1756-IA16 | 20 | 3 | 07 | RA23137_MS | I:203/7 | RA | RA 2313-7 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23137_MS_IO | MCR5B_R20:3:I.Data.07 | RA23137_MS_IO:= MCR5B_R20:3:I.Data.07; //RA 2313-7 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23137_MS | P_DIn | Sts_PV
1568 | CAP R20G3M- | 1771-IAD | 20 | 3 | 10 | 1756-IA16 | 20 | 3 | 08 | DA2313MOD8_ZSO_INLET | I:203/10 |  | MODULE 8 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD8_ZSO_INLET_IO | MCR5B_R20:3:I.Data.08 | DA2313MOD8_ZSO_INLET_IO:= MCR5B_R20:3:I.Data.08; //MODULE 8 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1569 | CAP R20G3M- | 1771-IAD | 20 | 3 | 11 | 1756-IA16 | 20 | 3 | 09 | DA2313MOD8_ZSC_INLET | I:203/11 |  | MODULE 8 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD8_ZSC_INLET_IO | MCR5B_R20:3:I.Data.09 | DA2313MOD8_ZSC_INLET_IO:= MCR5B_R20:3:I.Data.09; //MODULE 8 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1570 | CAP R20G3M- | 1771-IAD | 20 | 3 | 12 | 1756-IA16 | 20 | 3 | 10 | DA2313MOD8_ZSO_OUTLET | I:203/12 |  | MODULE 8 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD8_ZSO_OUTLET_IO | MCR5B_R20:3:I.Data.10 | DA2313MOD8_ZSO_OUTLET_IO:= MCR5B_R20:3:I.Data.10; //MODULE 8 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1571 | CAP R20G3M- | 1771-IAD | 20 | 3 | 13 | 1756-IA16 | 20 | 3 | 11 | DA2313MOD8_ZSC_OUTLET | I:203/13 |  | MODULE 8 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD8_ZSC_OUTLET_IO | MCR5B_R20:3:I.Data.11 | DA2313MOD8_ZSC_OUTLET_IO:= MCR5B_R20:3:I.Data.11; //MODULE 8 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1572 | CAP R20G3M- | 1771-IAD | 20 | 3 | 14 | 1756-IA16 | 20 | 3 | 12 | KN2313MOD8_SEQ | I:203/14 |  | MODULE 8 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD8_SEQ_IO | MCR5B_R20:3:I.Data.12 | KN2313MOD8_SEQ_IO:= MCR5B_R20:3:I.Data.12; //MODULE 8 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1573 | CAP R20G3M- | 1771-IAD | 20 | 3 | 15 | 1756-IA16 | 20 | 3 | 13 | KN2313MOD8_SEQ_ADVANCE | I:203/15 |  | MODULE 8 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD8_SEQ_ADVANCE_IO | MCR5B_R20:3:I.Data.13 | KN2313MOD8_SEQ_ADVANCE_IO:= MCR5B_R20:3:I.Data.13; //MODULE 8 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1574 | CAP R20G3M- | 1771-IAD | 20 | 3 | 16 | 1756-IA16 | 20 | 3 | 14 | RA23138_AUX | I:203/16 | RA | RA 2313-8 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23138_AUX_IO | MCR5B_R20:3:I.Data.14 | RA23138_AUX_IO:= MCR5B_R20:3:I.Data.14; //RA 2313-8 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23138_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23138_M01
1575 | CAP R20G3M- | 1771-IAD | 20 | 3 | 17 | 1756-IA16 | 20 | 3 | 15 | RA23138_MS | I:203/17 | RA | RA 2313-8 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23138_MS_IO | MCR5B_R20:3:I.Data.15 | RA23138_MS_IO:= MCR5B_R20:3:I.Data.15; //RA 2313-8 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23138_MS | P_DIn | Sts_PV
1576 | CAP R20G4M- | 1771-IAD | 20 | 4 | 00 | 1756-IA16 | 20 | 4 | 00 | DA2313MOD9_ZSO_INLET | I:204/0 |  | MODULE 9 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD9_ZSO_INLET_IO | MCR5B_R20:4:I.Data.00 | DA2313MOD9_ZSO_INLET_IO:= MCR5B_R20:4:I.Data.00; //MODULE 9 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1577 | CAP R20G4M- | 1771-IAD | 20 | 4 | 01 | 1756-IA16 | 20 | 4 | 01 | DA2313MOD9_ZSC_INLET | I:204/1 |  | MODULE 9 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD9_ZSC_INLET_IO | MCR5B_R20:4:I.Data.01 | DA2313MOD9_ZSC_INLET_IO:= MCR5B_R20:4:I.Data.01; //MODULE 9 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1578 | CAP R20G4M- | 1771-IAD | 20 | 4 | 02 | 1756-IA16 | 20 | 4 | 02 | DA2313MOD9_ZSO_OUTLET | I:204/2 |  | MODULE 9 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD9_ZSO_OUTLET_IO | MCR5B_R20:4:I.Data.02 | DA2313MOD9_ZSO_OUTLET_IO:= MCR5B_R20:4:I.Data.02; //MODULE 9 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1579 | CAP R20G4M- | 1771-IAD | 20 | 4 | 03 | 1756-IA16 | 20 | 4 | 03 | DA2313MOD9_ZSC_OUTLET | I:204/3 |  | MODULE 9 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD9_ZSC_OUTLET_IO | MCR5B_R20:4:I.Data.03 | DA2313MOD9_ZSC_OUTLET_IO:= MCR5B_R20:4:I.Data.03; //MODULE 9 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1580 | CAP R20G4M- | 1771-IAD | 20 | 4 | 04 | 1756-IA16 | 20 | 4 | 04 | KN2313MOD9_SEQ | I:204/4 |  | MODULE 9 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD9_SEQ_IO | MCR5B_R20:4:I.Data.04 | KN2313MOD9_SEQ_IO:= MCR5B_R20:4:I.Data.04; //MODULE 9 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1581 | CAP R20G4M- | 1771-IAD | 20 | 4 | 05 | 1756-IA16 | 20 | 4 | 05 | KN2313MOD9_SEQ_ADVANCE | I:204/5 |  | MODULE 9 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD9_SEQ_ADVANCE_IO | MCR5B_R20:4:I.Data.05 | KN2313MOD9_SEQ_ADVANCE_IO:= MCR5B_R20:4:I.Data.05; //MODULE 9 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1582 | CAP R20G4M- | 1771-IAD | 20 | 4 | 06 | 1756-IA16 | 20 | 4 | 06 | RA23139_AUX | I:204/6 | RA | RA 2313-9 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23139_AUX_IO | MCR5B_R20:4:I.Data.06 | RA23139_AUX_IO:= MCR5B_R20:4:I.Data.06; //RA 2313-9 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA23139_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23139_M01
1583 | CAP R20G4M- | 1771-IAD | 20 | 4 | 07 | 1756-IA16 | 20 | 4 | 07 | RA23139_MS | I:204/7 | RA | RA 2313-9 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23139_MS_IO | MCR5B_R20:4:I.Data.07 | RA23139_MS_IO:= MCR5B_R20:4:I.Data.07; //RA 2313-9 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA23139_MS | P_DIn | Sts_PV
1584 | CAP R20G4M- | 1771-IAD | 20 | 4 | 10 | 1756-IA16 | 20 | 4 | 08 | DA2313MOD10_ZSO_INLET | I:204/10 |  | MODULE 10 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD10_ZSO_INLET_IO | MCR5B_R20:4:I.Data.08 | DA2313MOD10_ZSO_INLET_IO:= MCR5B_R20:4:I.Data.08; //MODULE 10 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1585 | CAP R20G4M- | 1771-IAD | 20 | 4 | 11 | 1756-IA16 | 20 | 4 | 09 | DA2313MOD10_ZSC_INLET | I:204/11 |  | MODULE 10 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | DA2313MOD10_ZSC_INLET_IO | MCR5B_R20:4:I.Data.09 | DA2313MOD10_ZSC_INLET_IO:= MCR5B_R20:4:I.Data.09; //MODULE 10 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER |  | NA | NA | NA
1586 | CAP R20G4M- | 1771-IAD | 20 | 4 | 12 | 1756-IA16 | 20 | 4 | 10 | DA2313MOD10_ZSO_OUTLET | I:204/12 |  | MODULE 10 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD10_ZSO_OUTLET_IO | MCR5B_R20:4:I.Data.10 | DA2313MOD10_ZSO_OUTLET_IO:= MCR5B_R20:4:I.Data.10; //MODULE 10 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1587 | CAP R20G4M- | 1771-IAD | 20 | 4 | 13 | 1756-IA16 | 20 | 4 | 11 | DA2313MOD10_ZSC_OUTLET | I:204/13 |  | MODULE 10 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313MOD10_ZSC_OUTLET_IO | MCR5B_R20:4:I.Data.11 | DA2313MOD10_ZSC_OUTLET_IO:= MCR5B_R20:4:I.Data.11; //MODULE 10 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER |  | NA | NA | NA
1588 | CAP R20G4M- | 1771-IAD | 20 | 4 | 14 | 1756-IA16 | 20 | 4 | 12 | KN2313MOD10_SEQ | I:204/14 |  | MODULE 10 SEQUENCER KILN 2 BAGHOUSE |  | Notes: No software or logic needed. Just physical wiring for future use | MCR5B_R20 | I.Data | INPUT | KN2313MOD10_SEQ_IO | MCR5B_R20:4:I.Data.12 | KN2313MOD10_SEQ_IO:= MCR5B_R20:4:I.Data.12; //MODULE 10 SEQUENCER KILN 2 BAGHOUSE |  | NA | NA | NA
1589 | CAP R20G4M- | 1771-IAD | 20 | 4 | 15 | 1756-IA16 | 20 | 4 | 13 | KN2313MOD10_SEQ_ADVANCE | I:204/15 |  | MODULE 10 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | [10 empty] | MCR5B_R20 | I.Data | INPUT | KN2313MOD10_SEQ_ADVANCE_IO | MCR5B_R20:4:I.Data.13 | KN2313MOD10_SEQ_ADVANCE_IO:= MCR5B_R20:4:I.Data.13; //MODULE 10 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION |  | NA | NA | NA
1590 | CAP R20G4M- | 1771-IAD | 20 | 4 | 16 | 1756-IA16 | 20 | 4 | 14 | RA231310_AUX | I:204/16 | RA | RA 2313-10 AUX FDBK KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA231310_AUX_IO | MCR5B_R20:4:I.Data.14 | RA231310_AUX_IO:= MCR5B_R20:4:I.Data.14; //RA 2313-10 AUX FDBK KILN 2 ROTARY AIRLOCK |  | _RA231310_M01 | P_Motor | Sts_Running |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA231310_M01
1591 | CAP R20G4M- | 1771-IAD | 20 | 4 | 17 | 1756-IA16 | 20 | 4 | 15 | RA231310_MS | I:204/17 | RA | RA 2313-10 KILN 2 ROTARY AIRLOCK MOTION SWITCH | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA231310_MS_IO | MCR5B_R20:4:I.Data.15 | RA231310_MS_IO:= MCR5B_R20:4:I.Data.15; //RA 2313-10 KILN 2 ROTARY AIRLOCK MOTION SWITCH |  | _RA231310_MS | P_DIn | Sts_PV
1592 | CAP R20G5M- | 1771-IAD | 20 | 5 | 00 | 1756-IA16 | 20 | 5 | 00 |  | I:205/0 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:5:I.Data.00 | // MCR5B_R20:5:I.Data.00 SPARE
1593 | CAP R20G5M- | 1771-IAD | 20 | 5 | 01 | 1756-IA16 | 20 | 5 | 01 | RA23131_HS | I:205/1 |  | RA 2313-1 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23131_HS_IO | MCR5B_R20:5:I.Data.01 | RA23131_HS_IO:= MCR5B_R20:5:I.Data.01; //RA 2313-1 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23131_HS | P_DIn | Sts_PV
1594 | CAP R20G5M- | 1771-IAD | 20 | 5 | 02 | 1756-IA16 | 20 | 5 | 02 | RA23132_HS | I:205/2 |  | RA 2313-2 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23132_HS_IO | MCR5B_R20:5:I.Data.02 | RA23132_HS_IO:= MCR5B_R20:5:I.Data.02; //RA 2313-2 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23132_HS | P_DIn | Sts_PV
1595 | CAP R20G5M- | 1771-IAD | 20 | 5 | 03 | 1756-IA16 | 20 | 5 | 03 | RA23133_HS | I:205/3 |  | RA 2313-3 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23133_HS_IO | MCR5B_R20:5:I.Data.03 | RA23133_HS_IO:= MCR5B_R20:5:I.Data.03; //RA 2313-3 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23133_HS | P_DIn | Sts_PV
1596 | CAP R20G5M- | 1771-IAD | 20 | 5 | 04 | 1756-IA16 | 20 | 5 | 04 | RA23134_HS | I:205/4 |  | RA 2313-4 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23134_HS_IO | MCR5B_R20:5:I.Data.04 | RA23134_HS_IO:= MCR5B_R20:5:I.Data.04; //RA 2313-4 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23134_HS | P_DIn | Sts_PV
1597 | CAP R20G5M- | 1771-IAD | 20 | 5 | 05 | 1756-IA16 | 20 | 5 | 05 | RA23135_HS | I:205/5 |  | RA 2313-5 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23135_HS_IO | MCR5B_R20:5:I.Data.05 | RA23135_HS_IO:= MCR5B_R20:5:I.Data.05; //RA 2313-5 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23135_HS | P_DIn | Sts_PV
1598 | CAP R20G5M- | 1771-IAD | 20 | 5 | 06 | 1756-IA16 | 20 | 5 | 06 | RA23136_HS | I:205/6 |  | RA 2313-6 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23136_HS_IO | MCR5B_R20:5:I.Data.06 | RA23136_HS_IO:= MCR5B_R20:5:I.Data.06; //RA 2313-6 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23136_HS | P_DIn | Sts_PV
1599 | CAP R20G5M- | 1771-IAD | 20 | 5 | 07 | 1756-IA16 | 20 | 5 | 07 | RA23137_HS | I:205/7 |  | RA 2313- 7 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23137_HS_IO | MCR5B_R20:5:I.Data.07 | RA23137_HS_IO:= MCR5B_R20:5:I.Data.07; //RA 2313- 7 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23137_HS | P_DIn | Sts_PV
1600 | CAP R20G5M- | 1771-IAD | 20 | 5 | 10 | 1756-IA16 | 20 | 5 | 08 | RA23138_HS | I:205/10 |  | RA 2313-8 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23138_HS_IO | MCR5B_R20:5:I.Data.08 | RA23138_HS_IO:= MCR5B_R20:5:I.Data.08; //RA 2313-8 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23138_HS | P_DIn | Sts_PV
1601 | CAP R20G5M- | 1771-IAD | 20 | 5 | 11 | 1756-IA16 | 20 | 5 | 09 | RA23139_HS | I:205/11 |  | RA 2313-9 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA23139_HS_IO | MCR5B_R20:5:I.Data.09 | RA23139_HS_IO:= MCR5B_R20:5:I.Data.09; //RA 2313-9 AUTO KILN 2 ROTARY AIRLOCK |  | _RA23139_HS | P_DIn | Sts_PV
1602 | CAP R20G5M- | 1771-IAD | 20 | 5 | 12 | 1756-IA16 | 20 | 5 | 10 | RA231310_HS | I:205/12 |  | RA 2313-10 AUTO KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | I.Data | INPUT | RA231310_HS_IO | MCR5B_R20:5:I.Data.10 | RA231310_HS_IO:= MCR5B_R20:5:I.Data.10; //RA 2313-10 AUTO KILN 2 ROTARY AIRLOCK |  | _RA231310_HS | P_DIn | Sts_PV
1603 | CAP R20G5M- | 1771-IAD | 20 | 5 | 13 | 1756-IA16 | 20 | 5 | 11 | SC2316G_HS | I:205/13 |  | SC 2316-G AUTO KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316G_HS_IO | MCR5B_R20:5:I.Data.11 | SC2316G_HS_IO:= MCR5B_R20:5:I.Data.11; //SC 2316-G AUTO KILN 2 SCREW CONVEYOR |  | _SC2316G_HS | P_DIn | Sts_PV
1604 | CAP R20G5M- | 1771-IAD | 20 | 5 | 14 | 1756-IA16 | 20 | 5 | 12 | SC2316F_HS | I:205/14 |  | SC 2316-F AUTO KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316F_HS_IO | MCR5B_R20:5:I.Data.12 | SC2316F_HS_IO:= MCR5B_R20:5:I.Data.12; //SC 2316-F AUTO KILN 2 SCREW CONVEYOR |  | _SC2316F_HS | P_DIn | Sts_PV
1605 | CAP R20G5M- | 1771-IAD | 20 | 5 | 15 | 1756-IA16 | 20 | 5 | 13 | SC2316E_HS | I:205/15 |  | SC 2316-E AUTO KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316E_HS_IO | MCR5B_R20:5:I.Data.13 | SC2316E_HS_IO:= MCR5B_R20:5:I.Data.13; //SC 2316-E AUTO KILN 2 SCREW CONVEYOR |  | _SC2316E_HS | P_DIn | Sts_PV
1606 | CAP R20G5M- | 1771-IAD | 20 | 5 | 16 | 1756-IA16 | 20 | 5 | 14 | SC2316D_HS | I:205/16 |  | SC 2316-D AUTO KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316D_HS_IO | MCR5B_R20:5:I.Data.14 | SC2316D_HS_IO:= MCR5B_R20:5:I.Data.14; //SC 2316-D AUTO KILN 2 SCREW CONVEYOR |  | _SC2316D_HS | P_DIn | Sts_PV
1607 | CAP R20G5M- | 1771-IAD | 20 | 5 | 17 | 1756-IA16 | 20 | 5 | 15 |  | I:205/17 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:5:I.Data.15 | // MCR5B_R20:5:I.Data.15 SPARE
1608 | CAP R20G6M- | 1771-IAD | 20 | 6 | 00 | 1756-IA16 | 20 | 6 | 00 | SC2316G_1_AUX | I:206/0 | SC | SC 2316-G FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316G_1_AUX_IO | MCR5B_R20:6:I.Data.00 | SC2316G_1_AUX_IO:= MCR5B_R20:6:I.Data.00; //SC 2316-G FDBK KILN 2 SCREW CONVEYOR |  | _SC2316G_1_AUX | P_DIn | Sts_PV
1609 | CAP R20G6M- | 1771-IAD | 20 | 6 | 01 | 1756-IA16 | 20 | 6 | 01 | SC2316F_1_AUX | I:206/1 | SC | SC 2316-F FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316F_1_AUX_IO | MCR5B_R20:6:I.Data.01 | SC2316F_1_AUX_IO:= MCR5B_R20:6:I.Data.01; //SC 2316-F FDBK KILN 2 SCREW CONVEYOR |  | _SC2316F_1_AUX | P_DIn | Sts_PV
1610 | CAP R20G6M- | 1771-IAD | 20 | 6 | 02 | 1756-IA16 | 20 | 6 | 02 | SC2316E_1_AUX | I:206/2 | SC | SC 2316-E FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316E_1_AUX_IO | MCR5B_R20:6:I.Data.02 | SC2316E_1_AUX_IO:= MCR5B_R20:6:I.Data.02; //SC 2316-E FDBK KILN 2 SCREW CONVEYOR |  | _SC2316E_1_AUX | P_DIn | Sts_PV
1611 | CAP R20G6M- | 1771-IAD | 20 | 6 | 03 | 1756-IA16 | 20 | 6 | 03 | SC2316D_1_AUX | I:206/3 | SC | SC 2316-D FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316D_1_AUX_IO | MCR5B_R20:6:I.Data.03 | SC2316D_1_AUX_IO:= MCR5B_R20:6:I.Data.03; //SC 2316-D FDBK KILN 2 SCREW CONVEYOR |  | _SC2316D_1_AUX | P_DIn | Sts_PV
1612 | CAP R20G6M- | 1771-IAD | 20 | 6 | 04 | 1756-IA16 | 20 | 6 | 04 | SC2316G_2_AUX | I:206/4 | SC | SC 2316-G AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316G_2_AUX_IO | MCR5B_R20:6:I.Data.04 | SC2316G_2_AUX_IO:= MCR5B_R20:6:I.Data.04; //SC 2316-G AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316G_2_AUX | P_Motor | Sts_Running
1613 | CAP R20G6M- | 1771-IAD | 20 | 6 | 05 | 1756-IA16 | 20 | 6 | 05 | SC2316F_2_AUX | I:206/5 | SC | SC 2316-F AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316F_2_AUX_IO | MCR5B_R20:6:I.Data.05 | SC2316F_2_AUX_IO:= MCR5B_R20:6:I.Data.05; //SC 2316-F AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316F_2_AUX | P_Motor | Sts_Running
1614 | CAP R20G6M- | 1771-IAD | 20 | 6 | 06 | 1756-IA16 | 20 | 6 | 06 | SC2316E_2_AUX | I:206/6 | SC | SC 2316-E AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316E_2_AUX_IO | MCR5B_R20:6:I.Data.06 | SC2316E_2_AUX_IO:= MCR5B_R20:6:I.Data.06; //SC 2316-E AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316E_2_AUX | P_Motor | Sts_Running
1615 | CAP R20G6M- | 1771-IAD | 20 | 6 | 07 | 1756-IA16 | 20 | 6 | 07 | SC2316D_2_AUX | I:206/7 | SC | SC 2316-D AUX FDBK KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | I.Data | INPUT | SC2316D_2_AUX_IO | MCR5B_R20:6:I.Data.07 | SC2316D_2_AUX_IO:= MCR5B_R20:6:I.Data.07; //SC 2316-D AUX FDBK KILN 2 SCREW CONVEYOR |  | _SC2316D_2_AUX | P_Motor | Sts_Running
1616 | CAP R20G6M- | 1771-IAD | 20 | 6 | 10 | 1756-IA16 | 20 | 6 | 08 | DA2313E_ZSO | I:206/10 |  | DA 2313-E OPEN KILN 2 BAGHOUSE INLET EMERGENCY DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313E_ZSO_IO | MCR5B_R20:6:I.Data.08 | DA2313E_ZSO_IO:= MCR5B_R20:6:I.Data.08; //DA 2313-E OPEN KILN 2 BAGHOUSE INLET EMERGENCY DAMPER |  | _DA2313E | P_D4SD | Sts_St0 | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _DA2313E | Kiln 2 Dust collection
1617 | CAP R20G6M- | 1771-IAD | 20 | 6 | 11 | 1756-IA16 | 20 | 6 | 09 | DA2313E_ZSC | I:206/11 |  | DA 2313-E CLOSED KILN 2 BAGHOUSE INLET EMERGENCY DAMPER | [10 empty] | MCR5B_R20 | I.Data | INPUT | DA2313E_ZSC_IO | MCR5B_R20:6:I.Data.09 | DA2313E_ZSC_IO:= MCR5B_R20:6:I.Data.09; //DA 2313-E CLOSED KILN 2 BAGHOUSE INLET EMERGENCY DAMPER |  | _DA2313E | P_D4SD | Sts_St1 | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _DA2313E | Kiln 2 Dust Collection
1618 | CAP R20G6M- | 1771-IAD | 20 | 6 | 12 | 1756-IA16 | 20 | 6 | 10 |  | I:206/12 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:6:I.Data.10 | // MCR5B_R20:6:I.Data.10 SPARE | bar: Notes to EU
1619 | CAP R20G6M- | 1771-IAD | 20 | 6 | 13 | 1756-IA16 | 20 | 6 | 11 |  | I:206/13 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:6:I.Data.11 | // MCR5B_R20:6:I.Data.11 SPARE | bar: Notes to EU
1620 | CAP R20G6M- | 1771-IAD | 20 | 6 | 14 | 1756-IA16 | 20 | 6 | 12 |  | I:206/14 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:6:I.Data.12 | // MCR5B_R20:6:I.Data.12 SPARE | bar: Notes to EU
1621 | CAP R20G6M- | 1771-IAD | 20 | 6 | 15 | 1756-IA16 | 20 | 6 | 13 |  | I:206/15 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:6:I.Data.13 | // MCR5B_R20:6:I.Data.13 SPARE | bar: Notes to EU
1622 | CAP R20G6M- | 1771-IAD | 20 | 6 | 16 | 1756-IA16 | 20 | 6 | 14 |  | I:206/16 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:6:I.Data.14 | // MCR5B_R20:6:I.Data.14 SPARE
1623 | CAP R20G6M- | 1771-IAD | 20 | 6 | 17 | 1756-IA16 | 20 | 6 | 15 |  | I:206/17 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:6:I.Data.15 | // MCR5B_R20:6:I.Data.15 SPARE
1624 | CAP R20G7M- | 1771-IAD | 20 | 7 | 00 | 1756-IA16 | 20 | 7 | 00 |  | I:207/0 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.00 | // MCR5B_R20:7:I.Data.00 SPARE
1625 | CAP R20G7M- | 1771-IAD | 20 | 7 | 01 | 1756-IA16 | 20 | 7 | 01 |  | I:207/1 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.01 | // MCR5B_R20:7:I.Data.01 SPARE
1626 | CAP R20G7M- | 1771-IAD | 20 | 7 | 02 | 1756-IA16 | 20 | 7 | 02 |  | I:207/2 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.02 | // MCR5B_R20:7:I.Data.02 SPARE
1627 | CAP R20G7M- | 1771-IAD | 20 | 7 | 03 | 1756-IA16 | 20 | 7 | 03 |  | I:207/3 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.03 | // MCR5B_R20:7:I.Data.03 SPARE
1628 | CAP R20G7M- | 1771-IAD | 20 | 7 | 04 | 1756-IA16 | 20 | 7 | 04 |  | I:207/4 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.04 | // MCR5B_R20:7:I.Data.04 SPARE
1629 | CAP R20G7M- | 1771-IAD | 20 | 7 | 05 | 1756-IA16 | 20 | 7 | 05 |  | I:207/5 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.05 | // MCR5B_R20:7:I.Data.05 SPARE
1630 | CAP R20G7M- | 1771-IAD | 20 | 7 | 06 | 1756-IA16 | 20 | 7 | 06 |  | I:207/6 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.06 | // MCR5B_R20:7:I.Data.06 SPARE
1631 | CAP R20G7M- | 1771-IAD | 20 | 7 | 07 | 1756-IA16 | 20 | 7 | 07 |  | I:207/7 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.07 | // MCR5B_R20:7:I.Data.07 SPARE
1632 | CAP R20G7M- | 1771-IAD | 20 | 7 | 10 | 1756-IA16 | 20 | 7 | 08 |  | I:207/10 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.08 | // MCR5B_R20:7:I.Data.08 SPARE
1633 | CAP R20G7M- | 1771-IAD | 20 | 7 | 11 | 1756-IA16 | 20 | 7 | 09 |  | I:207/11 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.09 | // MCR5B_R20:7:I.Data.09 SPARE
1634 | CAP R20G7M- | 1771-IAD | 20 | 7 | 12 | 1756-IA16 | 20 | 7 | 10 |  | I:207/12 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.10 | // MCR5B_R20:7:I.Data.10 SPARE
1635 | CAP R20G7M- | 1771-IAD | 20 | 7 | 13 | 1756-IA16 | 20 | 7 | 11 |  | I:207/13 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.11 | // MCR5B_R20:7:I.Data.11 SPARE
1636 | CAP R20G7M- | 1771-IAD | 20 | 7 | 14 | 1756-IA16 | 20 | 7 | 12 |  | I:207/14 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.12 | // MCR5B_R20:7:I.Data.12 SPARE
1637 | CAP R20G7M- | 1771-IAD | 20 | 7 | 15 | 1756-IA16 | 20 | 7 | 13 |  | I:207/15 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.13 | // MCR5B_R20:7:I.Data.13 SPARE
1638 | CAP R20G7M- | 1771-IAD | 20 | 7 | 16 | 1756-IA16 | 20 | 7 | 14 |  | I:207/16 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.14 | // MCR5B_R20:7:I.Data.14 SPARE
1639 | CAP R20G7M- | 1771-IAD | 20 | 7 | 17 | 1756-IA16 | 20 | 7 | 15 |  | I:207/17 |  | SPARE | [10 empty] | MCR5B_R20 | I.Data | INPUT |  | MCR5B_R20:7:I.Data.15 | // MCR5B_R20:7:I.Data.15 SPARE
1640 | CAP R21G0M- | 1771-OAD | 21 | 8 | 00 | 1756-OA16 | 20 | 8 | 0 | MD231301_SV | O:210/0 | SV | MODULE 1 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231301_SV_IO | MCR5B_R20:8:O.Data.0 | MCR5B_R20:8:O.Data.0:=MD231301_SV_IO; //MODULE 1 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1641 | CAP R21G0M- | 1771-OAD | 21 | 8 | 01 | 1756-OA16 | 20 | 8 | 1 | MD231301_KS | O:210/1 | KS | MODULE 1 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231301_KS_IO | MCR5B_R20:8:O.Data.1 | MCR5B_R20:8:O.Data.1:=MD231301_KS_IO; //MODULE 1 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1642 | CAP R21G0M- | 1771-OAD | 21 | 8 | 02 | 1756-OA16 | 20 | 8 | 2 | MD231302_SV | O:210/2 | SV | MODULE 2 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231302_SV_IO | MCR5B_R20:8:O.Data.2 | MCR5B_R20:8:O.Data.2:=MD231302_SV_IO; //MODULE 2 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1643 | CAP R21G0M- | 1771-OAD | 21 | 8 | 03 | 1756-OA16 | 20 | 8 | 3 | MD231302_KS | O:210/3 | KS | MODULE 2 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231302_KS_IO | MCR5B_R20:8:O.Data.3 | MCR5B_R20:8:O.Data.3:=MD231302_KS_IO; //MODULE 2 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1644 | CAP R21G0M- | 1771-OAD | 21 | 8 | 04 | 1756-OA16 | 20 | 8 | 4 | MD231303_SV | O:210/4 | SV | MODULE 3 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231303_SV_IO | MCR5B_R20:8:O.Data.4 | MCR5B_R20:8:O.Data.4:=MD231303_SV_IO; //MODULE 3 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1645 | CAP R21G0M- | 1771-OAD | 21 | 8 | 05 | 1756-OA16 | 20 | 8 | 5 | MD231303_KS | O:210/5 | KS | MODULE 3 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231303_KS_IO | MCR5B_R20:8:O.Data.5 | MCR5B_R20:8:O.Data.5:=MD231303_KS_IO; //MODULE 3 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1646 | CAP R21G0M- | 1771-OAD | 21 | 8 | 06 | 1756-OA16 | 20 | 8 | 6 | MD231304_SV | O:210/6 | SV | MODULE 4 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231304_SV_IO | MCR5B_R20:8:O.Data.6 | MCR5B_R20:8:O.Data.6:=MD231304_SV_IO; //MODULE 4 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1647 | CAP R21G0M- | 1771-OAD | 21 | 8 | 07 | 1756-OA16 | 20 | 8 | 7 | MD231304_KS | O:210/7 | KS | MODULE 4 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231304_KS_IO | MCR5B_R20:8:O.Data.7 | MCR5B_R20:8:O.Data.7:=MD231304_KS_IO; //MODULE 4 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1648 | CAP R21G0M- | 1771-OAD | 21 | 8 | 10 | 1756-OA16 | 20 | 8 | 8 | MD231305_SV | O:210/10 | SV | MODULE 5 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231305_SV_IO | MCR5B_R20:8:O.Data.8 | MCR5B_R20:8:O.Data.8:=MD231305_SV_IO; //MODULE 5 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1649 | CAP R21G0M- | 1771-OAD | 21 | 8 | 11 | 1756-OA16 | 20 | 8 | 9 | MD231305_KS | O:210/11 | KS | MODULE 5 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231305_KS_IO | MCR5B_R20:8:O.Data.9 | MCR5B_R20:8:O.Data.9:=MD231305_KS_IO; //MODULE 5 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1650 | CAP R21G0M- | 1771-OAD | 21 | 8 | 12 | 1756-OA16 | 20 | 8 | 10 | MD231306_SV | O:210/12 | SV | MODULE 6 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231306_SV_IO | MCR5B_R20:8:O.Data.10 | MCR5B_R20:8:O.Data.10:=MD231306_SV_IO; //MODULE 6 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1651 | CAP R21G0M- | 1771-OAD | 21 | 8 | 13 | 1756-OA16 | 20 | 8 | 11 | MD231306_KS | O:210/13 | KS | MODULE 6 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231306_KS_IO | MCR5B_R20:8:O.Data.11 | MCR5B_R20:8:O.Data.11:=MD231306_KS_IO; //MODULE 6 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1652 | CAP R21G0M- | 1771-OAD | 21 | 8 | 14 | 1756-OA16 | 20 | 8 | 12 | MD231307_SV | O:210/14 | SV | MODULE 7 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231307_SV_IO | MCR5B_R20:8:O.Data.12 | MCR5B_R20:8:O.Data.12:=MD231307_SV_IO; //MODULE 7 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1653 | CAP R21G0M- | 1771-OAD | 21 | 8 | 15 | 1756-OA16 | 20 | 8 | 13 | MD231307_KS | O:210/15 | KS | MODULE 7 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231307_KS_IO | MCR5B_R20:8:O.Data.13 | MCR5B_R20:8:O.Data.13:=MD231307_KS_IO; //MODULE 7 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1654 | CAP R21G0M- | 1771-OAD | 21 | 8 | 16 | 1756-OA16 | 20 | 8 | 14 | MD231308_SV | O:210/16 | SV | MODULE 8 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231308_SV_IO | MCR5B_R20:8:O.Data.14 | MCR5B_R20:8:O.Data.14:=MD231308_SV_IO; //MODULE 8 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1655 | CAP R21G0M- | 1771-OAD | 21 | 8 | 17 | 1756-OA16 | 20 | 8 | 15 | MD231308_KS | O:210/17 | KS | MODULE 8 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231308_KS_IO | MCR5B_R20:8:O.Data.15 | MCR5B_R20:8:O.Data.15:=MD231308_KS_IO; //MODULE 8 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1656 | CAP R21G1M- | 1771-OAD | 21 | 9 | 00 | 1756-OA16 | 20 | 9 | 0 | MD231309_SV | O:211/0 | SV | MODULE 9 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231309_SV_IO | MCR5B_R20:9:O.Data.0 | MCR5B_R20:9:O.Data.0:=MD231309_SV_IO; //MODULE 9 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1657 | CAP R21G1M- | 1771-OAD | 21 | 9 | 01 | 1756-OA16 | 20 | 9 | 1 | MD231309_KS | O:211/1 | KS | MODULE 9 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231309_KS_IO | MCR5B_R20:9:O.Data.1 | MCR5B_R20:9:O.Data.1:=MD231309_KS_IO; //MODULE 9 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1658 | CAP R21G1M- | 1771-OAD | 21 | 9 | 02 | 1756-OA16 | 20 | 9 | 2 | MD231310_SV | O:211/2 | SV | MODULE 10 CLOSE KILN 2 BAGHOUSE OUTLET POPPET | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231310_SV_IO | MCR5B_R20:9:O.Data.2 | MCR5B_R20:9:O.Data.2:=MD231310_SV_IO; //MODULE 10 CLOSE KILN 2 BAGHOUSE OUTLET POPPET |  | NA | NA | NA
1659 | CAP R21G1M- | 1771-OAD | 21 | 9 | 03 | 1756-OA16 | 20 | 9 | 3 | MD231310_KS | O:211/3 | KS | MODULE 10 RUN KILN 2 BAGHOUSE SEQUENCER | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | MD231310_KS_IO | MCR5B_R20:9:O.Data.3 | MCR5B_R20:9:O.Data.3:=MD231310_KS_IO; //MODULE 10 RUN KILN 2 BAGHOUSE SEQUENCER |  | NA | NA | NA
1660 | CAP R21G1M- | 1771-OAD | 21 | 9 | 04 | 1756-OA16 | 20 | 9 | 4 | DA2313E_XY_A | O:211/4 |  | DA 2313-E OPEN KILN 2 BAGHOUSE INLET EMERGENCY DAMPER | ANDCO DRESSER MODEL# 3112A | [9 empty] | MCR5B_R20 | O.Data | OUTPUT | DA2313E_XY_A_IO | MCR5B_R20:9:O.Data.4 | MCR5B_R20:9:O.Data.4:=DA2313E_XY_A_IO; //DA 2313-E OPEN KILN 2 BAGHOUSE INLET EMERGENCY DAMPER |  | _DA2313E | P_D4SD | PCmd_St0 | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _DA2313E | Kiln 2 Dust Collection
1661 | CAP R21G1M- | 1771-OAD | 21 | 9 | 05 | 1756-OA16 | 20 | 9 | 5 | DA2313E_XY_B | O:211/5 |  | DA 2313-E CLOSE KILN 2 BAGHOUSE INLET EMERGENCY DAMPER | ANDCO DRESSER MODEL# 3112A | [9 empty] | MCR5B_R20 | O.Data | OUTPUT | DA2313E_XY_B_IO | MCR5B_R20:9:O.Data.5 | MCR5B_R20:9:O.Data.5:=DA2313E_XY_B_IO; //DA 2313-E CLOSE KILN 2 BAGHOUSE INLET EMERGENCY DAMPER |  | _DA2313E | P_D4SD | PCmd_St1 | 1 | Kiln2_Dust_Collection_TaskC | Task_C | _DA2313E | Kiln 2 Dust Collection
1662 | CAP R21G1M- | 1771-OAD | 21 | 9 | 06 | 1756-OA16 | 20 | 9 | 6 |  | O:211/6 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.6 | // MCR5B_R20:9:O.Data.6 SPARE
1663 | CAP R21G1M- | 1771-OAD | 21 | 9 | 07 | 1756-OA16 | 20 | 9 | 7 |  | O:211/7 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.7 | // MCR5B_R20:9:O.Data.7 SPARE
1664 | CAP R21G1M- | 1771-OAD | 21 | 9 | 10 | 1756-OA16 | 20 | 9 | 8 |  | O:211/10 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.8 | // MCR5B_R20:9:O.Data.8 SPARE
1665 | CAP R21G1M- | 1771-OAD | 21 | 9 | 11 | 1756-OA16 | 20 | 9 | 9 |  | O:211/11 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.9 | // MCR5B_R20:9:O.Data.9 SPARE
1666 | CAP R21G1M- | 1771-OAD | 21 | 9 | 12 | 1756-OA16 | 20 | 9 | 10 |  | O:211/12 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.10 | // MCR5B_R20:9:O.Data.10 SPARE
1667 | CAP R21G1M- | 1771-OAD | 21 | 9 | 13 | 1756-OA16 | 20 | 9 | 11 |  | O:211/13 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.11 | // MCR5B_R20:9:O.Data.11 SPARE
1668 | CAP R21G1M- | 1771-OAD | 21 | 9 | 14 | 1756-OA16 | 20 | 9 | 12 |  | O:211/14 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.12 | // MCR5B_R20:9:O.Data.12 SPARE
1669 | CAP R21G1M- | 1771-OAD | 21 | 9 | 15 | 1756-OA16 | 20 | 9 | 13 |  | O:211/15 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.13 | // MCR5B_R20:9:O.Data.13 SPARE
1670 | CAP R21G1M- | 1771-OAD | 21 | 9 | 16 | 1756-OA16 | 20 | 9 | 14 |  | O:211/16 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.14 | // MCR5B_R20:9:O.Data.14 SPARE
1671 | CAP R21G1M- | 1771-OAD | 21 | 9 | 17 | 1756-OA16 | 20 | 9 | 15 |  | O:211/17 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:9:O.Data.15 | // MCR5B_R20:9:O.Data.15 SPARE
1672 | CAP R21G2M- | 1771-OAD | 21 | 10 | 00 | 1756-OA16I | 20 | 10 | 0 | RA23131_COIL | O:212/0 | RA | RA 2313-1 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23131_COIL_IO | MCR5B_R20:10:O.Data.0 | MCR5B_R20:10:O.Data.0:=RA23131_COIL_IO; //RA 2313-1 RUN KILN 2 ROTARY AIRLOCK |  | _RA23131_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23131_M01
1673 | CAP R21G2M- | 1771-OAD | 21 | 10 | 01 | 1756-OA16I | 20 | 10 | 1 | RA23132_COIL | O:212/1 | RA | RA 2313-2 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23132_COIL_IO | MCR5B_R20:10:O.Data.1 | MCR5B_R20:10:O.Data.1:=RA23132_COIL_IO; //RA 2313-2 RUN KILN 2 ROTARY AIRLOCK |  | _RA23132_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23132_M01
1674 | CAP R21G2M- | 1771-OAD | 21 | 10 | 02 | 1756-OA16I | 20 | 10 | 2 | RA23133_COIL | O:212/2 | RA | RA 2313-3 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23133_COIL_IO | MCR5B_R20:10:O.Data.2 | MCR5B_R20:10:O.Data.2:=RA23133_COIL_IO; //RA 2313-3 RUN KILN 2 ROTARY AIRLOCK |  | _RA23133_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23133_M01
1675 | CAP R21G2M- | 1771-OAD | 21 | 10 | 03 | 1756-OA16I | 20 | 10 | 3 | RA23134_COIL | O:212/3 | RA | RA 2313-4 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23134_COIL_IO | MCR5B_R20:10:O.Data.3 | MCR5B_R20:10:O.Data.3:=RA23134_COIL_IO; //RA 2313-4 RUN KILN 2 ROTARY AIRLOCK |  | _RA23134_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23134_M01
1676 | CAP R21G2M- | 1771-OAD | 21 | 10 | 04 | 1756-OA16I | 20 | 10 | 4 | RA23135_COIL | O:212/4 | RA | RA 2313-5 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23135_COIL_IO | MCR5B_R20:10:O.Data.4 | MCR5B_R20:10:O.Data.4:=RA23135_COIL_IO; //RA 2313-5 RUN KILN 2 ROTARY AIRLOCK |  | _RA23135_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23135_M01
1677 | CAP R21G2M- | 1771-OAD | 21 | 10 | 05 | 1756-OA16I | 20 | 10 | 5 | RA23136_COIL | O:212/5 | RA | RA 2313-6 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23136_COIL_IO | MCR5B_R20:10:O.Data.5 | MCR5B_R20:10:O.Data.5:=RA23136_COIL_IO; //RA 2313-6 RUN KILN 2 ROTARY AIRLOCK |  | _RA23136_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23136_M01
1678 | CAP R21G2M- | 1771-OAD | 21 | 10 | 06 | 1756-OA16I | 20 | 10 | 6 | RA23137_COIL | O:212/6 | RA | RA 2313-7 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23137_COIL_IO | MCR5B_R20:10:O.Data.6 | MCR5B_R20:10:O.Data.6:=RA23137_COIL_IO; //RA 2313-7 RUN KILN 2 ROTARY AIRLOCK |  | _RA23137_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23137_M01
1679 | CAP R21G2M- | 1771-OAD | 21 | 10 | 07 | 1756-OA16I | 20 | 10 | 7 | RA23138_COIL | O:212/7 | RA | RA 2313-8 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23138_COIL_IO | MCR5B_R20:10:O.Data.7 | MCR5B_R20:10:O.Data.7:=RA23138_COIL_IO; //RA 2313-8 RUN KILN 2 ROTARY AIRLOCK |  | _RA23138_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23138_M01
1680 | CAP R21G2M- | 1771-OAD | 21 | 10 | 10 | 1756-OA16I | 20 | 10 | 8 | RA23139_COIL | O:212/10 | RA | RA 2313-9 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA23139_COIL_IO | MCR5B_R20:10:O.Data.8 | MCR5B_R20:10:O.Data.8:=RA23139_COIL_IO; //RA 2313-9 RUN KILN 2 ROTARY AIRLOCK |  | _RA23139_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA23139_M01
1681 | CAP R21G2M- | 1771-OAD | 21 | 10 | 11 | 1756-OA16I | 20 | 10 | 9 | RA231310_COIL | O:212/11 | RA | RA 2313-10 RUN KILN 2 ROTARY AIRLOCK | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | RA231310_COIL_IO | MCR5B_R20:10:O.Data.9 | MCR5B_R20:10:O.Data.9:=RA231310_COIL_IO; //RA 2313-10 RUN KILN 2 ROTARY AIRLOCK |  | _RA231310_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _RA231310_M01
1682 | CAP R21G2M- | 1771-OAD | 21 | 10 | 12 | 1756-OA16I | 20 | 10 | 10 | SC2316G_COIL | O:212/12 | SC | SC 2316-G RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | SC2316G_COIL_IO | MCR5B_R20:10:O.Data.10 | MCR5B_R20:10:O.Data.10:=SC2316G_COIL_IO; //SC 2316-G RUN KILN 2 SCREW CONVEYOR |  | _SC2316G_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316G_M01
1683 | CAP R21G2M- | 1771-OAD | 21 | 10 | 13 | 1756-OA16I | 20 | 10 | 11 | SC2316F_COIL | O:212/13 | SC | SC 2316-F RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | SC2316F_COIL_IO | MCR5B_R20:10:O.Data.11 | MCR5B_R20:10:O.Data.11:=SC2316F_COIL_IO; //SC 2316-F RUN KILN 2 SCREW CONVEYOR |  | _SC2316F_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316F_M01
1684 | CAP R21G2M- | 1771-OAD | 21 | 10 | 14 | 1756-OA16I | 20 | 10 | 12 | SC2316E_COIL | O:212/14 | SC | SC 2316-E RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | SC2316E_COIL_IO | MCR5B_R20:10:O.Data.12 | MCR5B_R20:10:O.Data.12:=SC2316E_COIL_IO; //SC 2316-E RUN KILN 2 SCREW CONVEYOR |  | _SC2316E_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316E_M01
1685 | CAP R21G2M- | 1771-OAD | 21 | 10 | 15 | 1756-OA16I | 20 | 10 | 13 | SC2316D_COIL | O:212/15 | SC | SC 2316-D RUN KILN 2 SCREW CONVEYOR | [10 empty] | MCR5B_R20 | O.Data | OUTPUT | SC2316D_COIL_IO | MCR5B_R20:10:O.Data.13 | MCR5B_R20:10:O.Data.13:=SC2316D_COIL_IO; //SC 2316-D RUN KILN 2 SCREW CONVEYOR |  | _SC2316D_M01 | P_Motor | PCmd_Start |  | Kiln2_Dust_Collection_TaskC | Task_C | _SC2316D_M01
1686 | CAP R21G2M- | 1771-OAD | 21 | 10 | 16 | 1756-OA16I | 20 | 10 | 14 |  | O:212/16 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:10:O.Data.14 | // MCR5B_R20:10:O.Data.14 SPARE
1687 | CAP R21G2M- | 1771-OAD | 21 | 10 | 17 | 1756-OA16I | 20 | 10 | 15 |  | O:212/17 |  | SPARE | [10 empty] | MCR5B_R20 | O.Data | OUTPUT |  | MCR5B_R20:10:O.Data.15 | // MCR5B_R20:10:O.Data.15 SPARE
1688 | CAP R21G5M- | 1771-OFE | 21 | 13 | CH1+ | 1756-OF8I | 20 | 12 | 0 | FV2319_ZT | N62:0 |  | FV 2319 DAMPER POSITION KILN 2 BLEED AIR DAMPER |  | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR5B_R20 | O.Ch[ | OUTPUT | FV2319_ZT_IO | MCR5B_R20:12:O.Ch[0].Data | MCR5B_R20:12:O.Ch[0].Data:=FV2319_ZT_IO; //FV 2319 DAMPER POSITION KILN 2 BLEED AIR DAMPER |  | _FV2319_ZT | P_AIn | Val
1689 | CAP R21G5M- | 1771-OFE | 21 | 13 | CH2+ | 1756-OF8I | 20 | 12 | 1 |  | N62:1 |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[1].Data | // MCR5B_R20:12:O.Ch[1].Data SPARE
1690 | CAP R21G5M- | 1771-OFE | 21 | 13 | CH3+ | 1756-OF8I | 20 | 12 | 2 |  | N62:2 |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[2].Data | // MCR5B_R20:12:O.Ch[2].Data SPARE
1691 | CAP R21G5M- | 1771-OFE | 21 | 13 | CH4+ | 1756-OF8I | 20 | 12 | 3 |  | N62:3 |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[3].Data | // MCR5B_R20:12:O.Ch[3].Data SPARE
1692 | [5 empty] | 1756-OF8I | 20 | 12 | 4 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[4].Data | // MCR5B_R20:12:O.Ch[4].Data SPARE
1693 | [5 empty] | 1756-OF8I | 20 | 12 | 5 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[5].Data | // MCR5B_R20:12:O.Ch[5].Data SPARE
1694 | [5 empty] | 1756-OF8I | 20 | 12 | 6 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[6].Data | // MCR5B_R20:12:O.Ch[6].Data SPARE
1695 | [5 empty] | 1756-OF8I | 20 | 12 | 7 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | O.Ch[ | OUTPUT |  | MCR5B_R20:12:O.Ch[7].Data | // MCR5B_R20:12:O.Ch[7].Data SPARE
1696 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH1+ | 1756-IF16 | 20 | 11 | 0 | K22300_PIT | N63:4 |  | K2 BAG HOUSE AIR PSI 0-150 (4-20mA) |  | EU: PSI; V.MIN: 0; V.MAX: 150 | MCR5B_R20 | I.Ch | INPUT | K22300_PIT_IO | MCR5B_R20:11:I.Ch0Data | K22300_PIT_IO:= MCR5B_R20:11:I.Ch0Data; //K2 BAG HOUSE AIR PSI 0-150 (4-20mA) |  | _K22300_PIT | P_AIn | Val
1697 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH2+ | 1756-IF16 | 20 | 11 | 1 | FV2313_ZT | N63:5 |  | FV 2313 DAMPER POSITION KILN 2 BLEED AIR |  | EU: % Position; V.MIN: 0; V.MAX: 100 | MCR5B_R20 | I.Ch | INPUT | FV2313_ZT_IO | MCR5B_R20:11:I.Ch1Data | FV2313_ZT_IO:= MCR5B_R20:11:I.Ch1Data; //FV 2313 DAMPER POSITION KILN 2 BLEED AIR |  | _FV2313_ZT | P_AIn | Val
1698 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH3+ | 1756-IF16 | 20 | 11 | 2 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch | INPUT |  | MCR5B_R20:11:I.Ch2Data | // MCR5B_R20:11:I.Ch2Data SPARE
1699 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH4+ | 1756-IF16 | 20 | 11 | 3 | FN2314_VT_A | N63:6 |  | FN 2314 VIBRATION KILN 2 ID FAN |  | Notes: IN HMI ONLY; EU: IPS; V.MIN: 0; V.MAX: 1 | MCR5B_R20 | I.Ch | INPUT | FN2314_VT_A_IO | MCR5B_R20:11:I.Ch3Data | FN2314_VT_A_IO:= MCR5B_R20:11:I.Ch3Data; //FN 2314 VIBRATION KILN 2 ID FAN |  | _FN2314_VT_A | P_AIn | Val
1700 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH5+ | 1756-IF16 | 20 | 11 | 4 | FN2314_VT_B | NOT FOUND |  | FN 2314 VIBRATION KILN 2 ID FAN |  | Notes: IN HMI ONLY; EU: IPS; V.MIN: 0; V.MAX: 1 | MCR5B_R20 | I.Ch | INPUT | FN2314_VT_B_IO | MCR5B_R20:11:I.Ch4Data | FN2314_VT_B_IO:= MCR5B_R20:11:I.Ch4Data; //FN 2314 VIBRATION KILN 2 ID FAN |  | _FN2314_VT_B | P_AIn | Val
1701 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH6+ | 1756-IF16 | 20 | 11 | 5 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch | INPUT |  | MCR5B_R20:11:I.Ch5Data | // MCR5B_R20:11:I.Ch5Data SPARE
1702 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH7+ | 1756-IF16 | 20 | 11 | 6 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch | INPUT |  | MCR5B_R20:11:I.Ch6Data | // MCR5B_R20:11:I.Ch6Data SPARE
1703 | CAP R21G6M- | 1771-IFE | 21 | 14 | CH8+ | 1756-IF16 | 20 | 11 | 7 |  |  |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch | INPUT |  | MCR5B_R20:11:I.Ch7Data | // MCR5B_R20:11:I.Ch7Data SPARE
1704 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH1+ | 1756-IRT8I | 20 | 13 | 0 | DC2313BH_TE_INLET | N64:3 | DC | DC 2313 TEMPERATURE KILN 2 BAGHOUSE INLET | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR5B_R20 | I.Ch[ | INPUT | DC2313BH_TE_INLET_IO | MCR5B_R20:13:I.Ch[0].Data | DC2313BH_TE_INLET_IO:= MCR5B_R20:13:I.Ch[0].Data; //DC 2313 TEMPERATURE KILN 2 BAGHOUSE INLET |  | _DC2313BH_TE_INLET | P_AIn | Val | 0
1705 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH2+ | 1756-IRT8I | 20 | 13 | 1 | DC2313BK_TE_INLET | N64:4 | DC | DC 2313 TEMPERATURE KILN 2 BAGHOUSE BACK-UP INLET | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR5B_R20 | I.Ch[ | INPUT | DC2313BK_TE_INLET_IO | MCR5B_R20:13:I.Ch[1].Data | DC2313BK_TE_INLET_IO:= MCR5B_R20:13:I.Ch[1].Data; //DC 2313 TEMPERATURE KILN 2 BAGHOUSE BACK-UP INLET |  | _DC2313BK_TE_INLET | P_AIn | Val | 0
1706 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH3+ | 1756-IRT8I | 20 | 13 | 2 | DC2313BH_TE_OUTLET | N64:5 | DC | DC 2313 TEMPERATURE KILN 2 BAGHOUSE OUTLET | TC Type J | EU: °F; V.MIN: 0; V.MAX: 1000 | MCR5B_R20 | I.Ch[ | INPUT | DC2313BH_TE_OUTLET_IO | MCR5B_R20:13:I.Ch[2].Data | DC2313BH_TE_OUTLET_IO:= MCR5B_R20:13:I.Ch[2].Data; //DC 2313 TEMPERATURE KILN 2 BAGHOUSE OUTLET |  | _DC2313BH_TE_OUTLET | P_AIn | Val | 0
1707 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH4+ | 1756-IRT8I | 20 | 13 | 3 |  | N64:6 |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch[ | INPUT |  | MCR5B_R20:13:I.Ch[3].Data | // MCR5B_R20:13:I.Ch[3].Data SPARE
1708 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH5+ | 1756-IRT8I | 20 | 13 | 4 |  | N64:7 |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch[ | INPUT |  | MCR5B_R20:13:I.Ch[4].Data | // MCR5B_R20:13:I.Ch[4].Data SPARE
1709 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH6+ | 1756-IRT8I | 20 | 13 | 5 |  | N64:10 |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch[ | INPUT |  | MCR5B_R20:13:I.Ch[5].Data | // MCR5B_R20:13:I.Ch[5].Data SPARE
1710 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH7+ | 1756-IRT8I | 20 | 13 | 6 |  | N64:11 |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch[ | INPUT |  | MCR5B_R20:13:I.Ch[6].Data | // MCR5B_R20:13:I.Ch[6].Data SPARE
1711 | CAP R21G7M- | 1771-IXE TYPE J | 21 | 15 | CH8+ | 1756-IRT8I | 20 | 13 | 7 |  | N64:12 |  | SPARE | [10 empty] | MCR5B_R20 | I.Ch[ | INPUT |  | MCR5B_R20:13:I.Ch[7].Data | // MCR5B_R20:13:I.Ch[7].Data SPARE
1712 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 00 | 1756-IA16 | 22 | 0 | 00 | FN4437A_AUX | I:220/0 | FN | FN 4437-A AUX FDBK FRONT SYSTEM DC FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN4437A_AUX_IO | MCR4_R22:0:I.Data.00 | FN4437A_AUX_IO:=MCR4_R22:0:I.Data.00; //FN 4437-A AUX FDBK FRONT SYSTEM DC FAN |  | NA | NA | NA | 1
1713 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 01 | 1756-IA16 | 22 | 0 | 01 | BE44241_PB_JOG | I:220/1 | BE | BE 4424-1 JOG FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE44241_PB_JOG_IO | MCR4_R22:0:I.Data.01 | BE44241_PB_JOG_IO:=MCR4_R22:0:I.Data.01; //BE 4424-1 JOG FRONT SYSTEM BUCKET ELEVATOR |  | _BE44241_M01 | P_Motor | Sts_Jogging | 0 | Front_Handling_TaskC | Task_C | _BE44241_M01
1714 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 02 | 1756-IA16 | 22 | 0 | 02 | BE44242_JOG_SET | I:220/2 | BE | BE 4424-2 JOG PLUG IN FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE44242_JOG_SET_IO | MCR4_R22:0:I.Data.02 | BE44242_JOG_SET_IO:=MCR4_R22:0:I.Data.02; //BE 4424-2 JOG PLUG IN FRONT SYSTEM BUCKET ELEVATOR |  | _BE44242_M01 | P_Motor | Sts_Ext | 0 | Front_Handling_TaskC | Task_C | _BE44242_M01
1715 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 03 | 1756-IA16 | 22 | 0 | 03 | BE44242_PB_JOG | I:220/3 | BE | BE 4424-2 JOG FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE44242_PB_JOG_IO | MCR4_R22:0:I.Data.03 | BE44242_PB_JOG_IO:=MCR4_R22:0:I.Data.03; //BE 4424-2 JOG FRONT SYSTEM BUCKET ELEVATOR |  | _BE44242_M01 | P_Motor | Sts_Jogging | 0 | Front_Handling_TaskC | Task_C | _BE44242_M01
1716 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 04 | 1756-IA16 | 22 | 0 | 04 | FN4437C_AUX | I:220/4 | FN | FN 4437-C AUX FDBK FRONT SYSTEM DC FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN4437C_AUX_IO | MCR4_R22:0:I.Data.04 | FN4437C_AUX_IO:=MCR4_R22:0:I.Data.04; //FN 4437-C AUX FDBK FRONT SYSTEM DC FAN |  | NA | NA | NA
1717 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 05 | 1756-IA16 | 22 | 0 | 05 | RA4437B_AUX | I:220/5 | RA | RA 4437-B AUX FDBK FRONT SYSTEM ROTARY AIRLOCK | [10 empty] | MCR4_R22 | I.Data | INPUT | RA4437B_AUX_IO | MCR4_R22:0:I.Data.05 | RA4437B_AUX_IO:=MCR4_R22:0:I.Data.05; //RA 4437-B AUX FDBK FRONT SYSTEM ROTARY AIRLOCK |  | _RA4437B_M01 | P_Motor | Sts_Running
1718 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 06 | 1756-IA16 | 22 | 0 | 06 | FN4437D_AUX | I:220/6 | FN | FN 4437-D AUX FDBK FRONT SYSTEM DC FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN4437D_AUX_IO | MCR4_R22:0:I.Data.06 | FN4437D_AUX_IO:=MCR4_R22:0:I.Data.06; //FN 4437-D AUX FDBK FRONT SYSTEM DC FAN |  | NA | NA | NA
1719 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 07 | 1756-IA16 | 22 | 0 | 07 | BE4424_1_JOG_SET | I:220/7 | BE | BE 4424-1 JOG FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE4424_1_JOG_SET_IO | MCR4_R22:0:I.Data.07 | BE4424_1_JOG_SET_IO:=MCR4_R22:0:I.Data.07; //BE 4424-1 JOG FRONT SYSTEM BUCKET ELEVATOR |  | _BE44241_M01 | P_Motor | Sts_Ext | 0 | Front_Handling_TaskC | Task_C | _BE44241_M01
1720 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 10 | 1756-IA16 | 22 | 0 | 08 | BE4423_JOG_SET | I:220/10 | BE | BE 4423 JOG PLUG IN FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE4423_JOG_SET_IO | MCR4_R22:0:I.Data.08 | BE4423_JOG_SET_IO:=MCR4_R22:0:I.Data.08; //BE 4423 JOG PLUG IN FRONT SYSTEM BUCKET ELEVATOR |  | _BE4423_M01 | P_Motor | Sts_Ext | 1 | Silo1A_Recycle_TaskC | Task_C | _BE4423_M01 | Front Handling
1721 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 11 | 1756-IA16 | 22 | 0 | 09 | BE4423_PB_JOG | I:220/11 | BE | BE 4423 JOG FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE4423_PB_JOG_IO | MCR4_R22:0:I.Data.09 | BE4423_PB_JOG_IO:=MCR4_R22:0:I.Data.09; //BE 4423 JOG FRONT SYSTEM BUCKET ELEVATOR |  | _BE4423_M01 | P_Motor | Sts_Jogging | 0 | Silo1A_Recycle_TaskC | Task_C | _BE4423_M01
1722 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 12 | 1756-IA16 | 22 | 0 | 10 | RA47621_AUX | I:220/12 | RA | RA 4762-1 AUX FDBK LIMEHANDLING DC ROTARY AIRLOCK | [10 empty] | MCR4_R22 | I.Data | INPUT | RA47621_AUX_IO | MCR4_R22:0:I.Data.10 | RA47621_AUX_IO:=MCR4_R22:0:I.Data.10; //RA 4762-1 AUX FDBK LIMEHANDLING DC ROTARY AIRLOCK |  | _RA47621_M01 | P_Motor | Sts_Running
1723 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 13 | 1756-IA16 | 22 | 0 | 11 | FN4437E_AUX | I:220/13 | FN | FN 4437-E AUX FDBK FRONT SYSTEM DC FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN4437E_AUX_IO | MCR4_R22:0:I.Data.11 | FN4437E_AUX_IO:=MCR4_R22:0:I.Data.11; //FN 4437-E AUX FDBK FRONT SYSTEM DC FAN |  | NA | NA | NA
1724 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 14 | 1756-IA16 | 22 | 0 | 12 | FN4527_AUX | I:220/14 | FN | FN 4527 FDBK COAL SYSTEM DUST COLLECTOR FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN4527_AUX_IO | MCR4_R22:0:I.Data.12 | FN4527_AUX_IO:=MCR4_R22:0:I.Data.12; //FN 4527 FDBK COAL SYSTEM DUST COLLECTOR FAN |  | _FN4527_M01 | P_Motor | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _FN4527_M01
1725 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 15 | 1756-IA16 | 22 | 0 | 13 | FN4437F_AUX | I:220/15 | FN | FN 4437-F AUX FDBK FRONT SYSTEM DC FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN4437F_AUX_IO | MCR4_R22:0:I.Data.13 | FN4437F_AUX_IO:=MCR4_R22:0:I.Data.13; //FN 4437-F AUX FDBK FRONT SYSTEM DC FAN |  | NA | NA | NA
1726 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 16 | 1756-IA16 | 22 | 0 | 14 | RA4527_AUX | I:220/16 | RA | RA 4527 FDBK COAL SYSTEM DUST COLLECTOR ROTARY AIRLOCK | [10 empty] | MCR4_R22 | I.Data | INPUT | RA4527_AUX_IO | MCR4_R22:0:I.Data.14 | RA4527_AUX_IO:=MCR4_R22:0:I.Data.14; //RA 4527 FDBK COAL SYSTEM DUST COLLECTOR ROTARY AIRLOCK |  | _RA4527_M01 | P_Motor | Sts_Running | 1 | Fuel_Handling_TaskC | Task_C | _RA4527_M01 | Fuel Handling
1727 | MCR4 R22G0M- | 1771-IAD | 22 | 0 | 17 | 1756-IA16 | 22 | 0 | 15 | COAL_BIN_LSH | I:220/17 | BN | ALARM KILN 1 FUEL BIN HIGH LEVEL | [10 empty] | MCR4_R22 | I.Data | INPUT | COAL_BIN_LSH_IO | MCR4_R22:0:I.Data.15 | COAL_BIN_LSH_IO:=MCR4_R22:0:I.Data.15; //ALARM KILN 1 FUEL BIN HIGH LEVEL |  | _COAL_BIN_LSH | P_DIn | Sts_PV | 1 | Kiln1_Preheater_TaskB | Task_B | _COAL_BIN_LSH | Kiln 1
1728 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 00 | 1756-IA16 | 22 | 1 | 00 | DG4514_ZS_BC4514 | I:221/0 |  | DG 4514 LIMIT SWITCH COAL SYSTEM DIVERTER GATE TO BC 4514 | [10 empty] | MCR4_R22 | I.Data | INPUT | DG4514_ZS_BC4514_IO | MCR4_R22:1:I.Data.00 | DG4514_ZS_BC4514_IO:=MCR4_R22:1:I.Data.00; //DG 4514 LIMIT SWITCH COAL SYSTEM DIVERTER GATE TO BC 4514 |  | _DG4514 | P_D4SD | Sts_St1 |  | Fuel_Handling_TaskC | Task_C | _DG4514
1729 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 01 | 1756-IA16 | 22 | 1 | 01 | DG4514_ZS_RC4522 | I:221/1 |  | DG 4514 LIMIT SWITCH COAL SYSTEM DIVERTER GATE TO RC 4522 | [10 empty] | MCR4_R22 | I.Data | INPUT | DG4514_ZS_RC4522_IO | MCR4_R22:1:I.Data.01 | DG4514_ZS_RC4522_IO:=MCR4_R22:1:I.Data.01; //DG 4514 LIMIT SWITCH COAL SYSTEM DIVERTER GATE TO RC 4522 |  | _DG4514 | P_D4SD | Sts_St0 |  | Fuel_Handling_TaskC | Task_C | _DG4514
1730 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 02 | 1756-IA16 | 22 | 1 | 02 | BV2518_AUX | I:221/2 | BV | BV 2518 AUX FDBK KILN 2 FUEL BIN VIBRATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BV2518_AUX_IO | MCR4_R22:1:I.Data.02 | BV2518_AUX_IO:=MCR4_R22:1:I.Data.02; //BV 2518 AUX FDBK KILN 2 FUEL BIN VIBRATOR |  | _BV2518_M01 | P_Motor | Sts_Running | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _BV2518_M01 | Kiln 2 Solid Fuel System
1731 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 03 | 1756-IA16 | 22 | 1 | 03 | FN2605_ATSPD_DI | I:221/3 |  | FN 2605 VFD AT SPEED KILN 2 MILL EXHAUST FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN2605_ATSPD_DI_IO | MCR4_R22:1:I.Data.03 | FN2605_ATSPD_DI_IO:=MCR4_R22:1:I.Data.03; //FN 2605 VFD AT SPEED KILN 2 MILL EXHAUST FAN |  | _FN2605_M01 | P_VSD | Sts_AtSpeed
1732 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 04 | 1756-IA16 | 22 | 1 | 04 | FN2605_FLT_DI | I:221/4 |  | FN 2605 VFD FAULT KILN 2 MILL EXHAUST FAN | [10 empty] | MCR4_R22 | I.Data | INPUT | FN2605_FLT_DI_IO | MCR4_R22:1:I.Data.04 | FN2605_FLT_DI_IO:=MCR4_R22:1:I.Data.04; //FN 2605 VFD FAULT KILN 2 MILL EXHAUST FAN |  | _FN2605_M01 | P_VSD | Sts_DriveFault
1733 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 05 | 1756-IA16 | 22 | 1 | 05 | RC45221_AUX | I:221/5 | RC | RC 4522-1 FDBK COAL SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR4_R22 | I.Data | INPUT | RC45221_AUX_IO | MCR4_R22:1:I.Data.05 | RC45221_AUX_IO:=MCR4_R22:1:I.Data.05; //RC 4522-1 FDBK COAL SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC45221_M01 | P_Motor | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _RC45221_M01
1734 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 06 | 1756-IA16 | 22 | 1 | 06 | HP260212_PSH | I:221/6 |  | 2-602-1&2 HIGH PRESSURE SWITCHES | [10 empty] | MCR4_R22 | I.Data | INPUT | HP260212_PSH_IO | MCR4_R22:1:I.Data.06 | HP260212_PSH_IO:=MCR4_R22:1:I.Data.06; //2-602-1&2 HIGH PRESSURE SWITCHES |  | _HP260212_PSH | P_DIn | Sts_PV
1735 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 07 | 1756-IA16 | 22 | 1 | 07 | RC45222_AUX | I:221/7 | RC | RC 4522-2 FDBK COAL SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR4_R22 | I.Data | INPUT | RC45222_AUX_IO | MCR4_R22:1:I.Data.07 | RC45222_AUX_IO:=MCR4_R22:1:I.Data.07; //RC 4522-2 FDBK COAL SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC45222_M01 | P_Motor | Sts_Running |  | Fuel_Handling_TaskC | Task_C | _RC45222_M01
1736 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 10 | 1756-IA16 | 22 | 1 | 08 | SPARE | I:221/10 |  | SPARE | [10 empty] | MCR4_R22 | I.Data | INPUT | SPARE_IO | MCR4_R22:1:I.Data.08 | SPARE_IO:=MCR4_R22:1:I.Data.08; //SPARE |  | _SPARE
1737 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 11 | 1756-IA16 | 22 | 1 | 09 | BE4521_AUX | I:221/11 | BE | BE 4521 AUX FDBK COAL SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BE4521_AUX_IO | MCR4_R22:1:I.Data.09 | BE4521_AUX_IO:=MCR4_R22:1:I.Data.09; //BE 4521 AUX FDBK COAL SYSTEM BUCKET ELEVATOR |  | _BE4521_M01 | P_Motor | Sts_Running | 1 | Fuel_Handling_TaskC | Task_C | _BE4521_M01 | Fuel Handling
1738 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 12 | 1756-IA16 | 22 | 1 | 10 | SPARE | I:221/12 |  | SPARE | [10 empty] | MCR4_R22 | I.Data | INPUT | SPARE_IO | MCR4_R22:1:I.Data.10 | SPARE_IO:=MCR4_R22:1:I.Data.10; //SPARE
1739 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 13 | 1756-IA16 | 22 | 1 | 11 | BC4516_AUX | I:221/13 | BC | BC 4516 FDBK COAL SYSTEM BELT CONVEYOR | [10 empty] | MCR4_R22 | I.Data | INPUT | BC4516_AUX_IO | MCR4_R22:1:I.Data.11 | BC4516_AUX_IO:=MCR4_R22:1:I.Data.11; //BC 4516 FDBK COAL SYSTEM BELT CONVEYOR |  | _BC4516_M01 | P_Motor | Sts_Running | 1 | Fuel_Handling_TaskC | Task_C | _BC4516_M01 | Fuel Handling
1740 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 14 | 1756-IA16 | 22 | 1 | 12 | SPARE | I:221/14 |  | SPARE | [10 empty] | MCR4_R22 | I.Data | INPUT | SPARE_IO | MCR4_R22:1:I.Data.12 | SPARE_IO:=MCR4_R22:1:I.Data.12; //SPARE |  | _SPARE
1741 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 15 | 1756-IA16 | 22 | 1 | 13 | BM2602_FSE_DI | I:221/15 |  | BM 2-602 RECIRCULATION LUBE PUMP FLOW SWITCH EAST | [10 empty] | MCR4_R22 | I.Data | INPUT | BM2602_FSE_DI_IO | MCR4_R22:1:I.Data.13 | BM2602_FSE_DI_IO:=MCR4_R22:1:I.Data.13; //BM 2-602 RECIRCULATION LUBE PUMP FLOW SWITCH EAST |  | _BM2602_FSE_DI | P_DIn | Sts_PV | 0
1742 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 16 | 1756-IA16 | 22 | 1 | 14 | BM2602_FSW_DI | I:221/16 |  | BM 2-602 RECIRCULATION LUBE PUMP FLOW SWITCH WEST | [10 empty] | MCR4_R22 | I.Data | INPUT | BM2602_FSW_DI_IO | MCR4_R22:1:I.Data.14 | BM2602_FSW_DI_IO:=MCR4_R22:1:I.Data.14; //BM 2-602 RECIRCULATION LUBE PUMP FLOW SWITCH WEST |  | _BM2602_FSW_DI | P_DIn | Sts_PV | 0
1743 | MCR4 R22G1M- | 1771-IAD | 22 | 1 | 17 | 1756-IA16 | 22 | 1 | 15 | COKEBIN_LSH | I:221/17 |  | ALARM KILN 2 FUEL BIN HIGH LEVEL | [10 empty] | MCR4_R22 | I.Data | INPUT | COKEBIN_LSH_IO | MCR4_R22:1:I.Data.15 | COKEBIN_LSH_IO:=MCR4_R22:1:I.Data.15; //ALARM KILN 2 FUEL BIN HIGH LEVEL |  | _COKEBIN_LSH | P_DIn | Sts_PV | 1 |  |  |  | Kiln 2
1744 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-0 | 1756-OA16I | 22 | 2 | 0 |  | O:222/0 |  | SPARE | [10 empty] | MCR4_R22 | O.Data | OUTPUT |  | MCR4_R22:2:O.Data.0 | //MCR4_R22:2:O.Data.0 SPARE
1745 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-1 | 1756-OA16I | 22 | 2 | 1 |  | O:222/1 |  | SPARE | [10 empty] | MCR4_R22 | O.Data | OUTPUT |  | MCR4_R22:2:O.Data.1 | //MCR4_R22:2:O.Data.1 SPARE
1746 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-2 | 1756-OA16I | 22 | 2 | 2 |  | O:222/2 |  | SPARE | [10 empty] | MCR4_R22 | O.Data | OUTPUT |  | MCR4_R22:2:O.Data.2 | //MCR4_R22:2:O.Data.2 SPARE
1747 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-3 | 1756-OA16I | 22 | 2 | 3 |  | O:222/3 |  | SPARE | [10 empty] | MCR4_R22 | O.Data | OUTPUT |  | MCR4_R22:2:O.Data.3 | //MCR4_R22:2:O.Data.3 SPARE
1748 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-4 | 1756-OA16I | 22 | 2 | 4 |  | O:222/4 |  | SPARE | [10 empty] | MCR4_R22 | O.Data | OUTPUT |  | MCR4_R22:2:O.Data.4 | //MCR4_R22:2:O.Data.4 SPARE
1749 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-5 | 1756-OA16I | 22 | 2 | 5 | FN4527_COIL | O:222/5 | FN | FN 4527 RUN COAL SYSTEM DUST COLLECTOR FAN | [10 empty] | MCR4_R22 | O.Data | OUTPUT | FN4527_COIL_IO | MCR4_R22:2:O.Data.5 | MCR4_R22:2:O.Data.5:=FN4527_COIL_IO; //FN 4527 RUN COAL SYSTEM DUST COLLECTOR FAN |  | _FN4527_M01 | P_Motor | PCmd_Start |  | Fuel_Handling_TaskC | Task_C | _FN4527_M01
1750 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-6 | 1756-OA16I | 22 | 2 | 6 | RA47621_COIL | O:222/6 | RA | RA 4762-1 RUN LIMEHANDLING DC ROTARY AIRLOCK | [10 empty] | MCR4_R22 | O.Data | OUTPUT | RA47621_COIL_IO | MCR4_R22:2:O.Data.6 | MCR4_R22:2:O.Data.6:=RA47621_COIL_IO; //RA 4762-1 RUN LIMEHANDLING DC ROTARY AIRLOCK |  | _RA47621_M01 | P_Motor | PCmd_Start
1751 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-7 | 1756-OA16I | 22 | 2 | 7 | DG4514_COIL | O:222/7 | DG | DG 4514 RUN COAL SYSTEM SOLENOID TO BC 4514 | [10 empty] | MCR4_R22 | O.Data | OUTPUT | DG4514_COIL_IO | MCR4_R22:2:O.Data.7 | MCR4_R22:2:O.Data.7:=DG4514_COIL_IO; //DG 4514 RUN COAL SYSTEM SOLENOID TO BC 4514 |  | _DG4514 | P_D4SD | PCmd_St1 |  | Fuel_Handling_TaskC | Task_C | _DG4514
1752 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-10 | 1756-OA16I | 22 | 2 | 8 | BV2518_COIL | O:222/10 | BV | BV 2518 RUN KILN 2 FUEL BIN VIBRATOR | [10 empty] | MCR4_R22 | O.Data | OUTPUT | BV2518_COIL_IO | MCR4_R22:2:O.Data.8 | MCR4_R22:2:O.Data.8:=BV2518_COIL_IO; //BV 2518 RUN KILN 2 FUEL BIN VIBRATOR |  | _BV2518_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Solid_Fuel_System_TaskC | Task_C | _BV2518_M01 | Kiln 2
1753 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-11 | 1756-OA16I | 22 | 2 | 9 | RC45221_COIL | O:222/11 | RC | RC 4522-1 RUN COAL SYSTEM ROLL CRUSHER MOTOR #1 | [10 empty] | MCR4_R22 | O.Data | OUTPUT | RC45221_COIL_IO | MCR4_R22:2:O.Data.9 | MCR4_R22:2:O.Data.9:=RC45221_COIL_IO; //RC 4522-1 RUN COAL SYSTEM ROLL CRUSHER MOTOR #1 |  | _RC45221_M01 | P_Motor | PCmd_Start |  | Fuel_Handling_TaskC | Task_C | _RC45221_M01
1754 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-12 | 1756-OA16I | 22 | 2 | 10 | RC45222_COIL | O:222/12 | RC | RC 4522-2 RUN COAL SYSTEM ROLL CRUSHER MOTOR #2 | [10 empty] | MCR4_R22 | O.Data | OUTPUT | RC45222_COIL_IO | MCR4_R22:2:O.Data.10 | MCR4_R22:2:O.Data.10:=RC45222_COIL_IO; //RC 4522-2 RUN COAL SYSTEM ROLL CRUSHER MOTOR #2 |  | _RC45222_M01 | P_Motor | PCmd_Start |  | Fuel_Handling_TaskC | Task_C | _RC45222_M01
1755 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-13 | 1756-OA16I | 22 | 2 | 11 | BE4521_COIL | O:222/13 | BE | BE 4521 RUN COAL SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R22 | O.Data | OUTPUT | BE4521_COIL_IO | MCR4_R22:2:O.Data.11 | MCR4_R22:2:O.Data.11:=BE4521_COIL_IO; //BE 4521 RUN COAL SYSTEM BUCKET ELEVATOR |  | _BE4521_M01 | P_Motor | PCmd_Start | 1 | Fuel_Handling_TaskC | Task_C | _BE4521_M01 | Fuel Handling
1756 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-14 | 1756-OA16I | 22 | 2 | 12 | BC4516_COIL | O:222/14 | BC | BC 4516 RUN COAL SYSTEM BELT CONVEYOR | [10 empty] | MCR4_R22 | O.Data | OUTPUT | BC4516_COIL_IO | MCR4_R22:2:O.Data.12 | MCR4_R22:2:O.Data.12:=BC4516_COIL_IO; //BC 4516 RUN COAL SYSTEM BELT CONVEYOR |  | _BC4516_M01 | P_Motor | PCmd_Start | 1 | Fuel_Handling_TaskC | Task_C | _BC4516_M01 | Fuel Handling
1757 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-15 | 1756-OA16I | 22 | 2 | 13 | FN2605_YYS | O:222/15 |  | FN 2605 VFD ENABLE KILN 2 MILL EXHAUST FAN | [10 empty] | MCR4_R22 | O.Data | OUTPUT | FN2605_YYS_IO | MCR4_R22:2:O.Data.13 | MCR4_R22:2:O.Data.13:=FN2605_YYS_IO; //FN 2605 VFD ENABLE KILN 2 MILL EXHAUST FAN |  | NA | NA | NA
1758 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-16 | 1756-OA16I | 22 | 2 | 14 | FN2605_2_COIL | O:222/16 |  | FN 2605 VFD RUN FORWARD KILN 2 MILL EXHAUST FAN | [10 empty] | MCR4_R22 | O.Data | OUTPUT | FN2605_2_COIL_IO | MCR4_R22:2:O.Data.14 | MCR4_R22:2:O.Data.14:=FN2605_2_COIL_IO; //FN 2605 VFD RUN FORWARD KILN 2 MILL EXHAUST FAN |  | _FN2605_M01 | P_VSD | PCmd_StartFwd | 1 |  |  |  | Kiln 2
1759 | MCR 4 R22G2M- | 1771-ODD | 22 | 2 | L1-17 | 1756-OA16I | 22 | 2 | 15 | FN2605_UY | O:222/17 |  | FN 2605 VFD RESET KILN 2 MILL EXHAUST FAN | [10 empty] | MCR4_R22 | O.Data | OUTPUT | FN2605_UY_IO | MCR4_R22:2:O.Data.15 | MCR4_R22:2:O.Data.15:=FN2605_UY_IO; //FN 2605 VFD RESET KILN 2 MILL EXHAUST FAN |  | _FN2605_M01 | P_VSD | Out_ClearFault
1760 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH1 | 1756-IF16 | 22 | 3 | 0 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch0Data | //MCR4_R22:3:I.Ch0Data SPARE | bar: EU to HH
1761 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH2 | 1756-IF16 | 22 | 3 | 1 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch1Data | //MCR4_R22:3:I.Ch1Data SPARE
1762 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH3 | 1756-IF16 | 22 | 3 | 2 | SILO3A_LT | N83:6 |  | SILO 3A % LEVEL FRONT SYSTEM 48" - 200' |  | EU: % Level; V.MIN: 48; V.MAX: 200 | MCR4_R22 | I.Ch | INPUT | SILO3A_LT_IO | MCR4_R22:3:I.Ch2Data | SILO3A_LT_IO:=MCR4_R22:3:I.Ch2Data; //SILO 3A % LEVEL FRONT SYSTEM 48" - 200' |  | _SILO3A_LT | P_AIn | Val
1763 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH4 | 1756-IF16 | 22 | 3 | 3 | BE4424C_IT | N83:7 | BE | BE 4424-C AMPS FRONT SYSTEM BUCKET ELEVATOR |  | EU: Ampers; V.MIN: 0; V.MAX: 65 | MCR4_R22 | I.Ch | INPUT | BE4424C_IT_IO | MCR4_R22:3:I.Ch3Data | BE4424C_IT_IO:=MCR4_R22:3:I.Ch3Data; //BE 4424-C AMPS FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_IT | P_AIn | Val | 1 | Front_Handling_TaskD | Task_D | _BE4424C_IT | Front Handling
1764 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH5 | 1756-IF16 | 22 | 3 | 4 | SC4428_IT | N83:8 | SC | SC 4428 AMPS FRONT SYSTEM SCREW CONVEYOR |  | EU: Ampers; V.MIN: 0; V.MAX: 65 | MCR4_R22 | I.Ch | INPUT | SC4428_IT_IO | MCR4_R22:3:I.Ch4Data | SC4428_IT_IO:=MCR4_R22:3:I.Ch4Data; //SC 4428 AMPS FRONT SYSTEM SCREW CONVEYOR |  | _SC4428_IT | P_AIn | Val | 1 | Front_Handling_TaskD | Task_D | _SC4428_IT | Front Handling
1765 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH6 | 1756-IF16 | 22 | 3 | 5 | HM4422_IT | N83:9 | HM | HM 4422 AMPS FRONT SYSTEM HAMMERMILL |  | EU: Ampers; V.MIN: 0; V.MAX: 250 | MCR4_R22 | I.Ch | INPUT | HM4422_IT_IO | MCR4_R22:3:I.Ch5Data | HM4422_IT_IO:=MCR4_R22:3:I.Ch5Data; //HM 4422 AMPS FRONT SYSTEM HAMMERMILL |  | _HM4422_IT | P_AIn |  | 1 | Front_Handling_TaskD | Task_D | _HM4422_IT | Front Handling
1766 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH7 | 1756-IF16 | 22 | 3 | 6 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch6Data | //MCR4_R22:3:I.Ch6Data SPARE
1767 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH8 | 1756-IF16 | 22 | 3 | 7 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch7Data | //MCR4_R22:3:I.Ch7Data SPARE
1768 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH9 | 1756-IF16 | 22 | 3 | 8 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch8Data | //MCR4_R22:3:I.Ch8Data SPARE
1769 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH10 | 1756-IF16 | 22 | 3 | 9 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch9Data | //MCR4_R22:3:I.Ch9Data SPARE
1770 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH11 | 1756-IF16 | 22 | 3 | 10 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch10Data | //MCR4_R22:3:I.Ch10Data SPARE
1771 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH12 | 1756-IF16 | 22 | 3 | 11 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch11Data | //MCR4_R22:3:I.Ch11Data SPARE
1772 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH13 | 1756-IF16 | 22 | 3 | 12 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch12Data | //MCR4_R22:3:I.Ch12Data SPARE
1773 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH14 | 1756-IF16 | 22 | 3 | 13 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch13Data | //MCR4_R22:3:I.Ch13Data SPARE
1774 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH15 | 1756-IF16 | 22 | 3 | 14 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch14Data | //MCR4_R22:3:I.Ch14Data SPARE
1775 | MCR 4 R22G3M- | 1771-IFE | 22 | 3 | CH16 | 1756-IF16 | 22 | 3 | 15 |  |  |  | SPARE | [10 empty] | MCR4_R22 | I.Ch | INPUT |  | MCR4_R22:3:I.Ch15Data | //MCR4_R22:3:I.Ch15Data SPARE
1776 | MCR4 R23G0M4 | 1771-IAD | 23 | 0 | 00 | 1756-IA16 | 23 | 0 | 00 | BE4424C_MS | I:230/0 | BE | BE 4424-C FRONT SYSTEM BUCKET ELEVATOR MOTION SWITCH | [10 empty] | MCR4_R23 | I.Data | INPUT | BE4424C_MS_IO | MCR4_R23:0:I.Data.00 | BE4424C_MS_IO:=MCR4_R23:0:I.Data.00; //BE 4424-C FRONT SYSTEM BUCKET ELEVATOR MOTION SWITCH |  | _BE4424C_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _BE4424C_MS | Front Handling
1777 | MCR4 R23G0M5 | 1771-IAD | 23 | 0 | 01 | 1756-IA16 | 23 | 0 | 01 | BE4424C_SSA | I:230/1 | BE | BE 4424-C AUTO FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | I.Data | INPUT | BE4424C_SSA_IO | MCR4_R23:0:I.Data.01 | BE4424C_SSA_IO:=MCR4_R23:0:I.Data.01; //BE 4424-C AUTO FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_AUTO | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _BE4424C_AUTO | Front Handling
1778 | MCR4 R23G0M6 | 1771-IAD | 23 | 0 | 02 | 1756-IA16 | 23 | 0 | 02 | BE4424C_AUX | I:230/2 | BE | BE 4424-C AUX FDBK FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | I.Data | INPUT | BE4424C_AUX_IO | MCR4_R23:0:I.Data.02 | BE4424C_AUX_IO:=MCR4_R23:0:I.Data.02; //BE 4424-C AUX FDBK FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _BE4424C_M01 | Front Handling
1779 | MCR4 R23G0M7 | 1771-IAD | 23 | 0 | 03 | 1756-IA16 | 23 | 0 | 03 | BE4424C_YS | I:230/3 | BE | BE 4424-C STARTER DISCONNECT FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | I.Data | INPUT | BE4424C_YS_IO | MCR4_R23:0:I.Data.03 | BE4424C_YS_IO:=MCR4_R23:0:I.Data.03; //BE 4424-C STARTER DISCONNECT FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_DISC | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _BE4424C_DISC | Front Handling
1780 | MCR4 R23G0M8 | 1771-IAD | 23 | 0 | 04 | 1756-IA16 | 23 | 0 | 04 |  | I:230/4 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:0:I.Data.04 | //MCR4_R23:0:I.Data.04 SPARE
1781 | MCR4 R23G0M9 | 1771-IAD | 23 | 0 | 05 | 1756-IA16 | 23 | 0 | 05 | SC4428_MS | I:230/5 | SC | SC 4428 FRONT SYSTEM SCREW CONVEYOR MOTION SWITCH | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4428_MS_IO | MCR4_R23:0:I.Data.05 | SC4428_MS_IO:=MCR4_R23:0:I.Data.05; //SC 4428 FRONT SYSTEM SCREW CONVEYOR MOTION SWITCH |  | _SC4428_MS | P_DIn | Sts_PV |  | Front_Handling_TaskB | Task_B | _SC4428_MS
1782 | MCR4 R23G0M10 | 1771-IAD | 23 | 0 | 06 | 1756-IA16 | 23 | 0 | 06 | SC4428_SSA | I:230/6 | SCS | SC 4428 AUTO FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4428_SSA_IO | MCR4_R23:0:I.Data.06 | SC4428_SSA_IO:=MCR4_R23:0:I.Data.06; //SC 4428 AUTO FRONT SYSTEM SCREW CONVEYOR |  | _SC4428_SSA | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _SC4428_SSA | Front Handling
1783 | MCR4 R23G0M11 | 1771-IAD | 23 | 0 | 07 | 1756-IA16 | 23 | 0 | 07 | SC4428_AUX | I:230/7 | SC | SC 4428 AUX FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4428_AUX_IO | MCR4_R23:0:I.Data.07 | SC4428_AUX_IO:=MCR4_R23:0:I.Data.07; //SC 4428 AUX FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4428_M01 | P_Motor | Sts_Running |  | Front_Handling_TaskC | Task_C | _SC4428_M01
1784 | MCR4 R23G0M12 | 1771-IAD | 23 | 0 | 10 | 1756-IA16 | 23 | 0 | 08 | SC4428_YS | I:230/10 | SC | SC 4428 STARTER DISCONNECT FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4428_YS_IO | MCR4_R23:0:I.Data.08 | SC4428_YS_IO:=MCR4_R23:0:I.Data.08; //SC 4428 STARTER DISCONNECT FRONT SYSTEM BUCKET ELEVATOR |  | _SC4428_YS | P_DIn | Sts_PV | 0
1785 | MCR4 R23G0M13 | 1771-IAD | 23 | 0 | 11 | 1756-IA16 | 23 | 0 | 09 |  | I:230/11 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:0:I.Data.09 | //MCR4_R23:0:I.Data.09 SPARE
1786 | MCR4 R23G0M14 | 1771-IAD | 23 | 0 | 12 | 1756-IA16 | 23 | 0 | 10 | BC401_WQS | I:230/12 | BC | BC-401 TOTALIZER PULSE | [10 empty] | MCR4_R23 | I.Data | INPUT | BC401_WQS_IO | MCR4_R23:0:I.Data.10 | BC401_WQS_IO:=MCR4_R23:0:I.Data.10; //BC-401 TOTALIZER PULSE |  | _BC401_WQS | P_DIn | Sts_PV | 0
1787 | MCR4 R23G0M15 | 1771-IAD | 23 | 0 | 13 | 1756-IA16 | 23 | 0 | 11 | HM4422_SSA | I:230/13 | HM | HM 4422 AUTO FRONT SYSTEM HAMMERMILL | [10 empty] | MCR4_R23 | I.Data | INPUT | HM4422_SSA_IO | MCR4_R23:0:I.Data.11 | HM4422_SSA_IO:=MCR4_R23:0:I.Data.11; //HM 4422 AUTO FRONT SYSTEM HAMMERMILL |  | _HM4422_SSA | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _HM4422_SSA | Front Handling
1788 | MCR4 R23G0M16 | 1771-IAD | 23 | 0 | 14 | 1756-IA16 | 23 | 0 | 12 | HM4422_AUX | I:230/14 | HM | HM 4422 AUX FDBK FRONT SYSTEM HAMMERMILL | [10 empty] | MCR4_R23 | I.Data | INPUT | HM4422_AUX_IO | MCR4_R23:0:I.Data.12 | HM4422_AUX_IO:=MCR4_R23:0:I.Data.12; //HM 4422 AUX FDBK FRONT SYSTEM HAMMERMILL |  | _HM4422_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _HM4422_M01 | Front Handling
1789 | MCR4 R23G0M17 | 1771-IAD | 23 | 0 | 15 | 1756-IA16 | 23 | 0 | 13 | HM4422_YS | I:230/15 | HM | HM 4422 STARTER DISCONNECT FRONT SYSTEM HAMMERMILL | [10 empty] | MCR4_R23 | I.Data | INPUT | HM4422_YS_IO | MCR4_R23:0:I.Data.13 | HM4422_YS_IO:=MCR4_R23:0:I.Data.13; //HM 4422 STARTER DISCONNECT FRONT SYSTEM HAMMERMILL |  | _HM4422_YS | P_DIn | Sts_PV | 0
1790 | MCR4 R23G0M18 | 1771-IAD | 23 | 0 | 16 | 1756-IA16 | 23 | 0 | 14 |  | I:230/16 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:0:I.Data.14 | //MCR4_R23:0:I.Data.14 SPARE
1791 | MCR4 R23G0M19 | 1771-IAD | 23 | 0 | 17 | 1756-IA16 | 23 | 0 | 15 | FIREDECK_ALARM | I:230/17 |  | FIRE DECK/LOCKER ROOM FIRE ALARM | [10 empty] | MCR4_R23 | I.Data | INPUT | FIREDECK_ALARM_IO | MCR4_R23:0:I.Data.15 | FIREDECK_ALARM_IO:=MCR4_R23:0:I.Data.15; //FIRE DECK/LOCKER ROOM FIRE ALARM |  | _FIREDECK_ALARM | P_DIn | Sts_PV | 0
1792 | MCR4 R23G0M1 | 1771-ODD | 23 | 1 | L1-0 | 1756-OA16I | 23 | 3 | 0 | HM4422_COIL | O:230/0 | HM | HM 4422 RUN FRONT SYSTEM HAMMERMILL | [10 empty] | MCR4_R23 | O.Data | OUTPUT | HM4422_COIL_IO | MCR4_R23:3:O.Data.0 | MCR4_R23:3:O.Data.0:=HM4422_COIL_IO; //HM 4422 RUN FRONT SYSTEM HAMMERMILL |  | _HM4422_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _HM4422_M01 | Front Handling
1793 | MCR4 R23G0M2 | 1771-ODD | 23 | 1 | L1-1 | 1756-OA16I | 23 | 3 | 1 | SC4427_COIL | O:230/1 | SC | SC 4427 RUN FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | O.Data | OUTPUT | SC4427_COIL_IO | MCR4_R23:3:O.Data.1 | MCR4_R23:3:O.Data.1:=SC4427_COIL_IO; //SC 4427 RUN FRONT SYSTEM SCREW CONVEYOR |  | _SC4427_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _SC4427_M01 | Front Handling
1794 | MCR4 R23G0M3 | 1771-ODD | 23 | 1 | L1-2 | 1756-OA16I | 23 | 3 | 2 | BE4424C_COIL | O:230/2 | BE | BE 4424-C RUN FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | O.Data | OUTPUT | BE4424C_COIL_IO | MCR4_R23:3:O.Data.2 | MCR4_R23:3:O.Data.2:=BE4424C_COIL_IO; //BE 4424-C RUN FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _BE4424C_M01 | Front Handling
1795 | MCR4 R23G0M4 | 1771-ODD | 23 | 1 | L1-3 | 1756-OA16I | 23 | 3 | 3 | SC4428_COIL | O:230/3 | SC | SC 4428 RUN FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | O.Data | OUTPUT | SC4428_COIL_IO | MCR4_R23:3:O.Data.3 | MCR4_R23:3:O.Data.3:=SC4428_COIL_IO; //SC 4428 RUN FRONT SYSTEM SCREW CONVEYOR |  | _SC4428_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _SC4428_M01 | Front Handling
1796 | MCR4 R23G0M6 | 1771-ODD | 23 | 1 | L1-4 | 1756-OA16I | 23 | 3 | 4 | SC4430A_COIL | O:230/4 | SC | SC 4430-A RUN FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | O.Data | OUTPUT | SC4430A_COIL_IO | MCR4_R23:3:O.Data.4 | MCR4_R23:3:O.Data.4:=SC4430A_COIL_IO; //SC 4430-A RUN FRONT SYSTEM SCREW CONVEYOR |  | _SC4430A_M01 | P_Motor | PCmd_Start | 1 | Front_Handling_TaskC | Task_C | _SC4430A_M01 | Front Handling
1797 | MCR4 R23G0M7 | 1771-ODD | 23 | 1 | L1-5 | 1756-OA16I | 23 | 3 | 5 | FN2210_COIL | O:230/5 | FN | FN 2-210 RUN KILN 2 OHMART/VEGA COOLING FAN | [10 empty] | MCR4_R23 | O.Data | OUTPUT | FN2210_COIL_IO | MCR4_R23:3:O.Data.5 | MCR4_R23:3:O.Data.5:=FN2210_COIL_IO; //FN 2-210 RUN KILN 2 OHMART/VEGA COOLING FAN |  | _FN2210_M01 | P_Motor | PCmd_Start | 1 | Kiln2_Main_TaskC | Task_C | _FN2210_M01 | Kiln 2
1798 | MCR4 R23G0M8 | 1771-ODD | 23 | 1 | L1-6 | 1756-OA16I | 23 | 3 | 6 | BC434_YAY | O:230/6 |  | BC434 TRUCK LOADOUT STARTUP ALARM | NEED TO FIELD VERIFY | [9 empty] | MCR4_R23 | O.Data | OUTPUT | BC434_YAY_IO | MCR4_R23:3:O.Data.6 | MCR4_R23:3:O.Data.6:=BC434_YAY_IO; //BC434 TRUCK LOADOUT STARTUP ALARM |  | NA | NA | NA
1799 | MCR4 R23G0M9 | 1771-ODD | 23 | 1 | L1-7 | 1756-OA16I | 23 | 3 | 7 | BC434_START_DO | O:230/7 |  | 434 START CONTACT MOMENTARY | NEED TO FIELD VERIFY | [9 empty] | MCR4_R23 | O.Data | OUTPUT | BC434_START_DO_IO | MCR4_R23:3:O.Data.7 | MCR4_R23:3:O.Data.7:=BC434_START_DO_IO; //434 START CONTACT MOMENTARY |  | NA | NA | NA
1800 | MCR4 R23G0M11 | 1771-ODD | 23 | 1 | L1-10 | 1756-OA16I | 23 | 3 | 8 | BC434_HAND_DO | O:230/10 |  | BC434 RUN HAND POSITION | NEED TO FIELD VERIFY | [9 empty] | MCR4_R23 | O.Data | OUTPUT | BC434_HAND_DO_IO | MCR4_R23:3:O.Data.8 | MCR4_R23:3:O.Data.8:=BC434_HAND_DO_IO; //BC434 RUN HAND POSITION |  | NA | NA | NA
1801 | MCR4 R23G0M12 | 1771-ODD | 23 | 1 | L1-11 | 1756-OA16I | 23 | 3 | 9 |  | O:230/11 |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:3:O.Data.9 | //MCR4_R23:3:O.Data.9 SPARE
1802 | MCR4 R23G0M13 | 1771-ODD | 23 | 1 | L1-12 | 1756-OA16I | 23 | 3 | 10 |  | O:230/12 |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:3:O.Data.10 | //MCR4_R23:3:O.Data.10 SPARE
1803 | MCR4 R23G0M14 | 1771-ODD | 23 | 1 | L1-13 | 1756-OA16I | 23 | 3 | 11 |  | O:230/13 |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:3:O.Data.11 | //MCR4_R23:3:O.Data.11 SPARE
1804 | MCR4 R23G0M16 | 1771-ODD | 23 | 1 | L1-14 | 1756-OA16I | 23 | 3 | 12 | DG516_YS_COKE | O:230/14 |  | DG-516 DIVERTER GATE TO COKE | ANDCO DRESSER MODEL# 3118A | [9 empty] | MCR4_R23 | O.Data | OUTPUT | DG516_YS_COKE_IO | MCR4_R23:3:O.Data.12 | MCR4_R23:3:O.Data.12:=DG516_YS_COKE_IO; //DG-516 DIVERTER GATE TO COKE |  | _DG4516 | P_D4SD | PCmd_St1 | 2 | Fuel_Handling_TaskC | Task_C | _DG4516 | Fuel Handling
1805 | MCR4 R23G0M17 | 1771-ODD | 23 | 1 | L1-15 | 1756-OA16I | 23 | 3 | 13 |  | O:230/15 |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:3:O.Data.13 | //MCR4_R23:3:O.Data.13 SPARE
1806 | MCR4 R23G0M18 | 1771-ODD | 23 | 1 | L1-16 | 1756-OA16I | 23 | 3 | 14 |  | O:230/16 |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:3:O.Data.14 | //MCR4_R23:3:O.Data.14 SPARE
1807 | MCR4 R23G0M19 | 1771-ODD | 23 | 1 | L1-17 | 1756-OA16I | 23 | 3 | 15 |  | O:230/17 |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:3:O.Data.15 | //MCR4_R23:3:O.Data.15 SPARE
1808 | MCR4 R23G1M4 | 1771-IAD | 23 | 2 | 00 | 1756-IA16 | 23 | 1 | 00 | SC4430A_SSA | I:231/0 | SC | SC 4430-A AUTO FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4430A_SSA_IO | MCR4_R23:1:I.Data.00 | SC4430A_SSA_IO:=MCR4_R23:1:I.Data.00; //SC 4430-A AUTO FRONT SYSTEM SCREW CONVEYOR |  | _SC4430A_SSA | P_DIn | Sts_PV | 1 |  |  |  | Front Handling
1809 | MCR4 R23G1M5 | 1771-IAD | 23 | 2 | 01 | 1756-IA16 | 23 | 1 | 01 | SC441_AUX | I:231/1 | SC | SC-441 RECYCLE SCREW AUX FEEDBACK | [10 empty] | MCR4_R23 | I.Data | INPUT | SC441_AUX_IO | MCR4_R23:1:I.Data.01 | SC441_AUX_IO:=MCR4_R23:1:I.Data.01; //SC-441 RECYCLE SCREW AUX FEEDBACK |  | NA | NA | NA | 0
1810 | MCR4 R23G1M6 | 1771-IAD | 23 | 2 | 02 | 1756-IA16 | 23 | 1 | 02 | SC4430A_AUX | I:231/2 | SC | SC 4430-A AUX FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4430A_AUX_IO | MCR4_R23:1:I.Data.02 | SC4430A_AUX_IO:=MCR4_R23:1:I.Data.02; //SC 4430-A AUX FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4430A_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _SC4430A_M01 | Front Handling
1811 | MCR4 R23G1M7 | 1771-IAD | 23 | 2 | 03 | 1756-IA16 | 23 | 1 | 03 | SC4430A_YS | I:231/3 | SC | SC 4430-A STARTER DISCONNECT FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4430A_YS_IO | MCR4_R23:1:I.Data.03 | SC4430A_YS_IO:=MCR4_R23:1:I.Data.03; //SC 4430-A STARTER DISCONNECT FRONT SYSTEM SCREW CONVEYOR |  | _SC4430A_YS | P_DIn | Sts_PV | 0
1812 | MCR4 R23G1M8 | 1771-IAD | 23 | 2 | 04 | 1756-IA16 | 23 | 1 | 04 |  | I:231/4 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:1:I.Data.04 | //MCR4_R23:1:I.Data.04 SPARE
1813 | MCR4 R23G1M9 | 1771-IAD | 23 | 2 | 05 | 1756-IA16 | 23 | 1 | 05 | SC4427_SSA | I:231/5 |  | SC 4427 AUTO FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4427_SSA_IO | MCR4_R23:1:I.Data.05 | SC4427_SSA_IO:=MCR4_R23:1:I.Data.05; //SC 4427 AUTO FRONT SYSTEM SCREW CONVEYOR |  | _SC4427_SSA | P_DIn | Sts_PV | 0
1814 | MCR4 R23G1M10 | 1771-IAD | 23 | 2 | 06 | 1756-IA16 | 23 | 1 | 06 | SC4427_YS | I:231/6 |  | SC 4427 STARTER DISCONNECT FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4427_YS_IO | MCR4_R23:1:I.Data.06 | SC4427_YS_IO:=MCR4_R23:1:I.Data.06; //SC 4427 STARTER DISCONNECT FRONT SYSTEM SCREW CONVEYOR |  | _SC4427_YS | P_DIn | Sts_PV | 0
1815 | MCR4 R23G1M11 | 1771-IAD | 23 | 2 | 07 | 1756-IA16 | 23 | 1 | 07 |  | I:231/7 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:1:I.Data.07 | //MCR4_R23:1:I.Data.07 SPARE
1816 | MCR4 R23G1M12 | 1771-IAD | 23 | 2 | 10 | 1756-IA16 | 23 | 1 | 08 | BE4424C_JOG_SET | I:231/10 |  | BE 4424-C JOG INSERTED FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | I.Data | INPUT | BE4424C_JOG_SET_IO | MCR4_R23:1:I.Data.08 | BE4424C_JOG_SET_IO:=MCR4_R23:1:I.Data.08; //BE 4424-C JOG INSERTED FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_M01 | P_Motor | Sts_Ext | 0 | Front_Handling_TaskC | Task_C | _BE4424C_M01
1817 | MCR4 R23G1M13 | 1771-IAD | 23 | 2 | 11 | 1756-IA16 | 23 | 1 | 09 | BE4424C_PB_JOG | I:231/11 |  | BE 4424-C JOG FRONT SYSTEM BUCKET ELEVATOR | [10 empty] | MCR4_R23 | I.Data | INPUT | BE4424C_PB_JOG_IO | MCR4_R23:1:I.Data.09 | BE4424C_PB_JOG_IO:=MCR4_R23:1:I.Data.09; //BE 4424-C JOG FRONT SYSTEM BUCKET ELEVATOR |  | _BE4424C_M01 | P_Motor | Sts_Jogging | 0 | Front_Handling_TaskC | Task_C | _BE4424C_M01
1818 | MCR4 R23G1M14 | 1771-IAD | 23 | 2 | 12 | 1756-IA16 | 23 | 1 | 10 | FN2210_SSA | I:231/12 |  | FN 2210 AUTO KILN 2 OHMART/VEGA COOLING FAN | [10 empty] | MCR4_R23 | I.Data | INPUT | FN2210_SSA_IO | MCR4_R23:1:I.Data.10 | FN2210_SSA_IO:=MCR4_R23:1:I.Data.10; //FN 2210 AUTO KILN 2 OHMART/VEGA COOLING FAN |  | _FN2210_SSA | P_DIn | Sts_PV | 1 | Kiln2_Main_TaskB | Task_B | _FN2210_SSA | Kiln 2
1819 | MCR4 R23G1M15 | 1771-IAD | 23 | 2 | 13 | 1756-IA16 | 23 | 1 | 11 | FN2210_AUX | I:231/13 | FN | FN 2210 AUX FDBK KILN 2 OHMART/VEGA COOLING FAN | [10 empty] | MCR4_R23 | I.Data | INPUT | FN2210_AUX_IO | MCR4_R23:1:I.Data.11 | FN2210_AUX_IO:=MCR4_R23:1:I.Data.11; //FN 2210 AUX FDBK KILN 2 OHMART/VEGA COOLING FAN |  | _FN2210_M01 | P_Motor | Sts_Running | 1 | Kiln2_Main_TaskC | Task_C | _FN2210_M01 | Kiln 2
1820 | MCR4 R23G1M16 | 1771-IAD | 23 | 2 | 14 | 1756-IA16 | 23 | 1 | 12 |  | I:231/14 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:1:I.Data.12 | //MCR4_R23:1:I.Data.12 SPARE
1821 | MCR4 R23G1M17 | 1771-IAD | 23 | 2 | 15 | 1756-IA16 | 23 | 1 | 13 | BC434_HSE_A | I:231/15 |  | BC434 NC STOP | PHYSICALLY CCHECK FIELD WIRING | [9 empty] | MCR4_R23 | I.Data | INPUT | BC434_HSE_A_IO | MCR4_R23:1:I.Data.13 | BC434_HSE_A_IO:=MCR4_R23:1:I.Data.13; //BC434 NC STOP |  | NA | NA | NA | 0
1822 | MCR4 R23G1M18 | 1771-IAD | 23 | 2 | 16 | 1756-IA16 | 23 | 1 | 14 | BC434_HSE_B | I:231/16 |  | BC'434 NO STOP | PHYSICALLY CCHECK FIELD WIRING | [9 empty] | MCR4_R23 | I.Data | INPUT | BC434_HSE_B_IO | MCR4_R23:1:I.Data.14 | BC434_HSE_B_IO:=MCR4_R23:1:I.Data.14; //BC'434 NO STOP |  | NA | NA | NA | 0
1823 | MCR4 R23G1M19 | 1771-IAD | 23 | 2 | 17 | 1756-IA16 | 23 | 1 | 15 | BC434_AUX | I:231/17 |  | BC434 AUX CONTACT FEEDBACK | [10 empty] | MCR4_R23 | I.Data | INPUT | BC434_AUX_IO | MCR4_R23:1:I.Data.15 | BC434_AUX_IO:=MCR4_R23:1:I.Data.15; //BC434 AUX CONTACT FEEDBACK |  | NA | NA | NA | 0
1824 | MCR4 R23G2M4 | 1771-IAD | 23 | 4 | 00 | 1756-IA16 | 23 | 2 | 00 | SC4427_MS | I:232/0 | SC | SC 4427 MOTION SWITCH | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4427_MS_IO | MCR4_R23:2:I.Data.00 | SC4427_MS_IO:=MCR4_R23:2:I.Data.00; //SC 4427 MOTION SWITCH |  | _SC4427_MS | P_DIn | Sts_PV | 1 | Front_Handling_TaskB | Task_B | _SC4427_MS | Front Handling
1825 | MCR4 R23G2M5 | 1771-IAD | 23 | 4 | 01 | 1756-IA16 | 23 | 2 | 01 | SC4427_AUX | I:232/1 | SC | SC 4427 AUX FDBK FRONT SYSTEM SCREW CONVEYOR | [10 empty] | MCR4_R23 | I.Data | INPUT | SC4427_AUX_IO | MCR4_R23:2:I.Data.01 | SC4427_AUX_IO:=MCR4_R23:2:I.Data.01; //SC 4427 AUX FDBK FRONT SYSTEM SCREW CONVEYOR |  | _SC4427_M01 | P_Motor | Sts_Running | 1 | Front_Handling_TaskC | Task_C | _SC4427_M01 | Front Handling
1826 | MCR4 R23G2M6 | 1771-IAD | 23 | 4 | 02 | 1756-IA16 | 23 | 2 | 02 |  | I:232/2 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.02 | //MCR4_R23:2:I.Data.02 SPARE
1827 | MCR4 R23G2M7 | 1771-IAD | 23 | 4 | 03 | 1756-IA16 | 23 | 2 | 03 |  | I:232/3 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.03 | //MCR4_R23:2:I.Data.03 SPARE
1828 | MCR4 R23G2M8 | 1771-IAD | 23 | 4 | 04 | 1756-IA16 | 23 | 2 | 04 |  | I:232/4 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.04 | //MCR4_R23:2:I.Data.04 SPARE
1829 | MCR4 R23G2M9 | 1771-IAD | 23 | 4 | 05 | 1756-IA16 | 23 | 2 | 05 |  | I:232/5 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.05 | //MCR4_R23:2:I.Data.05 SPARE
1830 | MCR4 R23G2M10 | 1771-IAD | 23 | 4 | 06 | 1756-IA16 | 23 | 2 | 06 |  | I:232/6 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.06 | //MCR4_R23:2:I.Data.06 SPARE
1831 | MCR4 R23G2M11 | 1771-IAD | 23 | 4 | 07 | 1756-IA16 | 23 | 2 | 07 | WF2601A_SSA | I:232/7 |  | WF2601A AUTO KILN 1 COKE #2 BIN WEIGH BELT | POWERFLEX 525B | [9 empty] | MCR4_R23 | I.Data | INPUT | WF2601A_SSA_IO | MCR4_R23:2:I.Data.07 | WF2601A_SSA_IO:=MCR4_R23:2:I.Data.07; //WF2601A AUTO KILN 1 COKE #2 BIN WEIGH BELT |  | _WF2601A_SSA | P_DIn | Sts_PV | 1 |  |  |  | Kiln 1
1832 | MCR4 R23G2M12 | 1771-IAD | 23 | 4 | 10 | 1756-IA16 | 23 | 2 | 08 | WF2601A_AUX | I:232/10 | WF | WF2601A AUX FDBK KILN 1 COKE #2 BIN WEIGH BELT | POWERFLEX 525B | [9 empty] | MCR4_R23 | I.Data | INPUT | WF2601A_AUX_IO | MCR4_R23:2:I.Data.08 | WF2601A_AUX_IO:=MCR4_R23:2:I.Data.08; //WF2601A AUX FDBK KILN 1 COKE #2 BIN WEIGH BELT |  | _WF2601A_M01 | P_Motor | Sts_PV | 0
1833 | MCR4 R23G2M13 | 1771-IAD | 23 | 4 | 11 | 1756-IA16 | 23 | 2 | 09 | WF2601A_FLT | I:232/11 |  | WF2601A FAULT KILN 1 COKE #2 BIN WEIGH BELT | POWERFLEX 525B | [9 empty] | MCR4_R23 | I.Data | INPUT | WF2601A_FLT_IO | MCR4_R23:2:I.Data.09 | WF2601A_FLT_IO:=MCR4_R23:2:I.Data.09; //WF2601A FAULT KILN 1 COKE #2 BIN WEIGH BELT |  | _WF2601A_FLT | P_DIn | Sts_PV | 0
1834 | MCR4 R23G2M14 | 1771-IAD | 23 | 4 | 12 | 1756-IA16 | 23 | 2 | 10 |  | I:232/12 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.10 | //MCR4_R23:2:I.Data.10 SPARE
1835 | MCR4 R23G2M15 | 1771-IAD | 23 | 4 | 13 | 1756-IA16 | 23 | 2 | 11 |  | I:232/13 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.11 | //MCR4_R23:2:I.Data.11 SPARE
1836 | MCR4 R23G2M16 | 1771-IAD | 23 | 4 | 14 | 1756-IA16 | 23 | 2 | 12 | WF2601A_WQS | I:232/14 |  | WF2601A PULSE 0.1 TON KILN 1 COKE #2 BIN WEIGH BELT | RAMSEY BELT SCALE MODEL# | [9 empty] | MCR4_R23 | I.Data | INPUT | WF2601A_WQS_IO | MCR4_R23:2:I.Data.12 | WF2601A_WQS_IO:=MCR4_R23:2:I.Data.12; //WF2601A PULSE 0.1 TON KILN 1 COKE #2 BIN WEIGH BELT |  | _WF2601A_WQS | P_DIn | Sts_PV | 0
1837 | MCR4 R23G2M17 | 1771-IAD | 23 | 4 | 15 | 1756-IA16 | 23 | 2 | 13 | DG4516_ZS_COAL | I:232/15 |  | DG-4516 Gate Position to Coal | ANDCO DRESSER MODEL# 3118A | [9 empty] | MCR4_R23 | I.Data | INPUT | DG4516_ZS_COAL_IO | MCR4_R23:2:I.Data.13 | DG4516_ZS_COAL_IO:=MCR4_R23:2:I.Data.13; //DG-4516 Gate Position to Coal |  | _DG4516 | P_D4SD | Sts_St0 | 1 | Fuel_Handling_TaskC | Task_C | _DG4516 | Fuel Handling
1838 | MCR4 R23G2M18 | 1771-IAD | 23 | 4 | 16 | 1756-IA16 | 23 | 2 | 14 | DG4516_ZS_COKE | I:232/16 |  | DG-4516 Gate Position to Coke | ANDCO DRESSER MODEL# 3118A | [9 empty] | MCR4_R23 | I.Data | INPUT | DG4516_ZS_COKE_IO | MCR4_R23:2:I.Data.14 | DG4516_ZS_COKE_IO:=MCR4_R23:2:I.Data.14; //DG-4516 Gate Position to Coke |  | _DG4516 | P_D4SD | Sts_St1 | 1 | Fuel_Handling_TaskC | Task_C | _DG4516 | Fuel Handling
1839 | MCR4 R23G2M19 | 1771-IAD | 23 | 4 | 17 | 1756-IA16 | 23 | 2 | 15 |  | I:232/17 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:2:I.Data.15 | //MCR4_R23:2:I.Data.15 SPARE
1840 | MCR4 R23G3M4 | 1771-IAD | 23 | 6 | 00 | 1756-IA16 | 23 | REMOVE | 00 |  | I:233/0 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.00 | //MCR4_R23:REMOVE:I.Data.00 SPARE
1841 | MCR4 R23G3M5 | 1771-IAD | 23 | 6 | 01 | 1756-IA16 | 23 | REMOVE | 01 |  | I:233/1 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.01 | //MCR4_R23:REMOVE:I.Data.01 SPARE
1842 | MCR4 R23G3M6 | 1771-IAD | 23 | 6 | 02 | 1756-IA16 | 23 | REMOVE | 02 |  | I:233/2 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.02 | //MCR4_R23:REMOVE:I.Data.02 SPARE
1843 | MCR4 R23G3M7 | 1771-IAD | 23 | 6 | 03 | 1756-IA16 | 23 | REMOVE | 03 |  | I:233/3 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.03 | //MCR4_R23:REMOVE:I.Data.03 SPARE
1844 | MCR4 R23G3M8 | 1771-IAD | 23 | 6 | 04 | 1756-IA16 | 23 | REMOVE | 04 |  | I:233/4 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.04 | //MCR4_R23:REMOVE:I.Data.04 SPARE
1845 | MCR4 R23G3M9 | 1771-IAD | 23 | 6 | 05 | 1756-IA16 | 23 | REMOVE | 05 |  | I:233/5 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.05 | //MCR4_R23:REMOVE:I.Data.05 SPARE
1846 | MCR4 R23G3M10 | 1771-IAD | 23 | 6 | 06 | 1756-IA16 | 23 | REMOVE | 06 |  | I:233/6 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.06 | //MCR4_R23:REMOVE:I.Data.06 SPARE
1847 | MCR4 R23G3M11 | 1771-IAD | 23 | 6 | 07 | 1756-IA16 | 23 | REMOVE | 07 |  | I:233/7 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.07 | //MCR4_R23:REMOVE:I.Data.07 SPARE
1848 | MCR4 R23G3M12 | 1771-IAD | 23 | 6 | 10 | 1756-IA16 | 23 | REMOVE | 08 |  | I:233/10 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.08 | //MCR4_R23:REMOVE:I.Data.08 SPARE
1849 | MCR4 R23G3M13 | 1771-IAD | 23 | 6 | 11 | 1756-IA16 | 23 | REMOVE | 09 |  | I:233/11 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.09 | //MCR4_R23:REMOVE:I.Data.09 SPARE
1850 | MCR4 R23G3M14 | 1771-IAD | 23 | 6 | 12 | 1756-IA16 | 23 | REMOVE | 10 |  | I:233/12 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.10 | //MCR4_R23:REMOVE:I.Data.10 SPARE
1851 | MCR4 R23G3M15 | 1771-IAD | 23 | 6 | 13 | 1756-IA16 | 23 | REMOVE | 11 |  | I:233/13 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.11 | //MCR4_R23:REMOVE:I.Data.11 SPARE
1852 | MCR4 R23G3M16 | 1771-IAD | 23 | 6 | 14 | 1756-IA16 | 23 | REMOVE | 12 |  | I:233/14 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.12 | //MCR4_R23:REMOVE:I.Data.12 SPARE
1853 | MCR4 R23G3M17 | 1771-IAD | 23 | 6 | 15 | 1756-IA16 | 23 | REMOVE | 13 |  | I:233/15 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.13 | //MCR4_R23:REMOVE:I.Data.13 SPARE
1854 | MCR4 R23G3M18 | 1771-IAD | 23 | 6 | 16 | 1756-IA16 | 23 | REMOVE | 14 |  | I:233/16 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.14 | //MCR4_R23:REMOVE:I.Data.14 SPARE
1855 | MCR4 R23G3M19 | 1771-IAD | 23 | 6 | 17 | 1756-IA16 | 23 | REMOVE | 15 |  | I:233/17 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.15 | //MCR4_R23:REMOVE:I.Data.15 SPARE
1856 | MCR4 R23G4M4 | 1771-IAD | 23 | 8 | 00 | 1756-IA16 | 23 | REMOVE | 00 |  | I:234/0 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.00 | //MCR4_R23:REMOVE:I.Data.00 SPARE
1857 | MCR4 R23G4M5 | 1771-IAD | 23 | 8 | 01 | 1756-IA16 | 23 | REMOVE | 01 |  | I:234/1 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.01 | //MCR4_R23:REMOVE:I.Data.01 SPARE
1858 | MCR4 R23G4M6 | 1771-IAD | 23 | 8 | 02 | 1756-IA16 | 23 | REMOVE | 02 |  | I:234/2 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.02 | //MCR4_R23:REMOVE:I.Data.02 SPARE
1859 | MCR4 R23G4M7 | 1771-IAD | 23 | 8 | 03 | 1756-IA16 | 23 | REMOVE | 03 |  | I:234/3 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.03 | //MCR4_R23:REMOVE:I.Data.03 SPARE
1860 | MCR4 R23G4M8 | 1771-IAD | 23 | 8 | 04 | 1756-IA16 | 23 | REMOVE | 04 |  | I:234/4 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.04 | //MCR4_R23:REMOVE:I.Data.04 SPARE
1861 | MCR4 R23G4M9 | 1771-IAD | 23 | 8 | 05 | 1756-IA16 | 23 | REMOVE | 05 |  | I:234/5 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.05 | //MCR4_R23:REMOVE:I.Data.05 SPARE
1862 | MCR4 R23G4M10 | 1771-IAD | 23 | 8 | 06 | 1756-IA16 | 23 | REMOVE | 06 |  | I:234/6 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.06 | //MCR4_R23:REMOVE:I.Data.06 SPARE
1863 | MCR4 R23G4M11 | 1771-IAD | 23 | 8 | 07 | 1756-IA16 | 23 | REMOVE | 07 |  | I:234/7 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.07 | //MCR4_R23:REMOVE:I.Data.07 SPARE
1864 | MCR4 R23G4M12 | 1771-IAD | 23 | 8 | 10 | 1756-IA16 | 23 | REMOVE | 08 |  | I:234/10 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.08 | //MCR4_R23:REMOVE:I.Data.08 SPARE
1865 | MCR4 R23G4M13 | 1771-IAD | 23 | 8 | 11 | 1756-IA16 | 23 | REMOVE | 09 |  | I:234/11 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.09 | //MCR4_R23:REMOVE:I.Data.09 SPARE
1866 | MCR4 R23G4M14 | 1771-IAD | 23 | 8 | 12 | 1756-IA16 | 23 | REMOVE | 10 |  | I:234/12 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.10 | //MCR4_R23:REMOVE:I.Data.10 SPARE
1867 | MCR4 R23G4M15 | 1771-IAD | 23 | 8 | 13 | 1756-IA16 | 23 | REMOVE | 11 |  | I:234/13 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.11 | //MCR4_R23:REMOVE:I.Data.11 SPARE
1868 | MCR4 R23G4M16 | 1771-IAD | 23 | 8 | 14 | 1756-IA16 | 23 | REMOVE | 12 |  | I:234/14 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.12 | //MCR4_R23:REMOVE:I.Data.12 SPARE
1869 | MCR4 R23G4M17 | 1771-IAD | 23 | 8 | 15 | 1756-IA16 | 23 | REMOVE | 13 |  | I:234/15 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.13 | //MCR4_R23:REMOVE:I.Data.13 SPARE
1870 | MCR4 R23G4M18 | 1771-IAD | 23 | 8 | 16 | 1756-IA16 | 23 | REMOVE | 14 |  | I:234/16 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.14 | //MCR4_R23:REMOVE:I.Data.14 SPARE
1871 | MCR4 R23G4M19 | 1771-IAD | 23 | 8 | 17 | 1756-IA16 | 23 | REMOVE | 15 |  | I:234/17 |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.15 | //MCR4_R23:REMOVE:I.Data.15 SPARE
1872 | MCR4 R23G5M4 | 1771-IAD | 23 | 10 | 00 | 1756-IA16 | 23 | REMOVE | 00 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.00 | //MCR4_R23:REMOVE:I.Data.00 SPARE
1873 | MCR4 R23G5M5 | 1771-IAD | 23 | 10 | 01 | 1756-IA16 | 23 | REMOVE | 01 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.01 | //MCR4_R23:REMOVE:I.Data.01 SPARE
1874 | MCR4 R23G5M6 | 1771-IAD | 23 | 10 | 02 | 1756-IA16 | 23 | REMOVE | 02 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.02 | //MCR4_R23:REMOVE:I.Data.02 SPARE
1875 | MCR4 R23G5M7 | 1771-IAD | 23 | 10 | 03 | 1756-IA16 | 23 | REMOVE | 03 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.03 | //MCR4_R23:REMOVE:I.Data.03 SPARE
1876 | MCR4 R23G5M8 | 1771-IAD | 23 | 10 | 04 | 1756-IA16 | 23 | REMOVE | 04 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.04 | //MCR4_R23:REMOVE:I.Data.04 SPARE
1877 | MCR4 R23G5M9 | 1771-IAD | 23 | 10 | 05 | 1756-IA16 | 23 | REMOVE | 05 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.05 | //MCR4_R23:REMOVE:I.Data.05 SPARE
1878 | MCR4 R23G5M10 | 1771-IAD | 23 | 10 | 06 | 1756-IA16 | 23 | REMOVE | 06 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.06 | //MCR4_R23:REMOVE:I.Data.06 SPARE
1879 | MCR4 R23G5M11 | 1771-IAD | 23 | 10 | 07 | 1756-IA16 | 23 | REMOVE | 07 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.07 | //MCR4_R23:REMOVE:I.Data.07 SPARE
1880 | MCR4 R23G5M12 | 1771-IAD | 23 | 10 | 10 | 1756-IA16 | 23 | REMOVE | 08 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.08 | //MCR4_R23:REMOVE:I.Data.08 SPARE
1881 | MCR4 R23G5M13 | 1771-IAD | 23 | 10 | 11 | 1756-IA16 | 23 | REMOVE | 09 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.09 | //MCR4_R23:REMOVE:I.Data.09 SPARE
1882 | MCR4 R23G5M14 | 1771-IAD | 23 | 10 | 12 | 1756-IA16 | 23 | REMOVE | 10 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.10 | //MCR4_R23:REMOVE:I.Data.10 SPARE
1883 | MCR4 R23G5M15 | 1771-IAD | 23 | 10 | 13 | 1756-IA16 | 23 | REMOVE | 11 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.11 | //MCR4_R23:REMOVE:I.Data.11 SPARE
1884 | MCR4 R23G5M16 | 1771-IAD | 23 | 10 | 14 | 1756-IA16 | 23 | REMOVE | 12 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.12 | //MCR4_R23:REMOVE:I.Data.12 SPARE
1885 | MCR4 R23G5M17 | 1771-IAD | 23 | 10 | 15 | 1756-IA16 | 23 | REMOVE | 13 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.13 | //MCR4_R23:REMOVE:I.Data.13 SPARE
1886 | MCR4 R23G5M18 | 1771-IAD | 23 | 10 | 16 | 1756-IA16 | 23 | REMOVE | 14 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.14 | //MCR4_R23:REMOVE:I.Data.14 SPARE
1887 | MCR4 R23G5M19 | 1771-IAD | 23 | 10 | 17 | 1756-IA16 | 23 | REMOVE | 15 |  |  |  | SPARE | [10 empty] | MCR4_R23 | I.Data | INPUT |  | MCR4_R23:REMOVE:I.Data.15 | //MCR4_R23:REMOVE:I.Data.15 SPARE
|  |  | 1 |  | 00 | 1756-IA16 | 1 | 4 | 00 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.00 | //MCR4_R01:4:I.Data.00 SPARE
|  |  | 1 |  | 01 | 1756-IA16 | 1 | 4 | 01 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.01 | //MCR4_R01:4:I.Data.01 SPARE
|  |  | 1 |  | 02 | 1756-IA16 | 1 | 4 | 02 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.02 | //MCR4_R01:4:I.Data.02 SPARE
|  |  | 1 |  | 03 | 1756-IA16 | 1 | 4 | 03 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.03 | //MCR4_R01:4:I.Data.03 SPARE
|  |  | 1 |  | 04 | 1756-IA16 | 1 | 4 | 04 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.04 | //MCR4_R01:4:I.Data.04 SPARE
|  |  | 1 |  | 05 | 1756-IA16 | 1 | 4 | 05 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.05 | //MCR4_R01:4:I.Data.05 SPARE
|  |  | 1 |  | 06 | 1756-IA16 | 1 | 4 | 06 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.06 | //MCR4_R01:4:I.Data.06 SPARE
|  |  | 1 |  | 07 | 1756-IA16 | 1 | 4 | 07 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.07 | //MCR4_R01:4:I.Data.07 SPARE
|  |  | 1 |  | 10 | 1756-IA16 | 1 | 4 | 08 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.08 | //MCR4_R01:4:I.Data.08 SPARE
|  |  | 1 |  | 11 | 1756-IA16 | 1 | 4 | 09 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.09 | //MCR4_R01:4:I.Data.09 SPARE
|  |  | 1 |  | 12 | 1756-IA16 | 1 | 4 | 10 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.10 | //MCR4_R01:4:I.Data.10 SPARE
|  |  | 1 |  | 13 | 1756-IA16 | 1 | 4 | 11 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.11 | //MCR4_R01:4:I.Data.11 SPARE
|  |  | 1 |  | 14 | 1756-IA16 | 1 | 4 | 12 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.12 | //MCR4_R01:4:I.Data.12 SPARE
|  |  | 1 |  | 15 | 1756-IA16 | 1 | 4 | 13 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.13 | //MCR4_R01:4:I.Data.13 SPARE
|  |  | 1 |  | 16 | 1756-IA16 | 1 | 4 | 14 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.14 | //MCR4_R01:4:I.Data.14 SPARE
|  |  | 1 |  | 17 | 1756-IA16 | 1 | 4 | 15 |  |  |  | SPARE | [10 empty] | MCR4_R01 | I.Data | INPUT |  | MCR4_R01:4:I.Data.15 | //MCR4_R01:4:I.Data.15 SPARE
|  |  | 10 |  | L1-0 | 1756-OA16I | 10 | 10 | 0 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.0 | // MCR1_R10:10:O.Data.0 SPARE
|  |  | 10 |  | L1-1 | 1756-OA16I | 10 | 10 | 1 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.1 | // MCR1_R10:10:O.Data.1 SPARE
|  |  | 10 |  | L1-2 | 1756-OA16I | 10 | 10 | 2 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.2 | // MCR1_R10:10:O.Data.2 SPARE
|  |  | 10 |  | L1-3 | 1756-OA16I | 10 | 10 | 3 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.3 | // MCR1_R10:10:O.Data.3 SPARE
|  |  | 10 |  | L1-4 | 1756-OA16I | 10 | 10 | 4 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.4 | // MCR1_R10:10:O.Data.4 SPARE
|  |  | 10 |  | L1-5 | 1756-OA16I | 10 | 10 | 5 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.5 | // MCR1_R10:10:O.Data.5 SPARE
|  |  | 10 |  | L1-6 | 1756-OA16I | 10 | 10 | 6 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.6 | // MCR1_R10:10:O.Data.6 SPARE
|  |  | 10 |  | L1-7 | 1756-OA16I | 10 | 10 | 7 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.7 | // MCR1_R10:10:O.Data.7 SPARE
|  |  | 10 |  | L1-10 | 1756-OA16I | 10 | 10 | 8 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.8 | // MCR1_R10:10:O.Data.8 SPARE
|  |  | 10 |  | L1-11 | 1756-OA16I | 10 | 10 | 9 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.9 | // MCR1_R10:10:O.Data.9 SPARE
|  |  | 10 |  | L1-12 | 1756-OA16I | 10 | 10 | 10 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.10 | // MCR1_R10:10:O.Data.10 SPARE
|  |  | 10 |  | L1-13 | 1756-OA16I | 10 | 10 | 11 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.11 | // MCR1_R10:10:O.Data.11 SPARE
|  |  | 10 |  | L1-14 | 1756-OA16I | 10 | 10 | 12 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.12 | // MCR1_R10:10:O.Data.12 SPARE
|  |  | 10 |  | L1-15 | 1756-OA16I | 10 | 10 | 13 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.13 | // MCR1_R10:10:O.Data.13 SPARE
|  |  | 10 |  | L1-16 | 1756-OA16I | 10 | 10 | 14 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.14 | // MCR1_R10:10:O.Data.14 SPARE
|  |  | 10 |  | L1-17 | 1756-OA16I | 10 | 10 | 15 |  |  |  | SPARE | [10 empty] | MCR1_R10 | O.Data | OUTPUT |  | MCR1_R10:10:O.Data.15 | // MCR1_R10:10:O.Data.15 SPARE
|  |  | 10 |  | CH1 | 1756-IF16 | 10 | 13 | 0 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch0Data | // MCR1_R10:13:I.Ch0Data SPARE
|  |  | 10 |  | CH2 | 1756-IF16 | 10 | 13 | 1 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch1Data | // MCR1_R10:13:I.Ch1Data SPARE
|  |  | 10 |  | CH3 | 1756-IF16 | 10 | 13 | 2 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch2Data | // MCR1_R10:13:I.Ch2Data SPARE
|  |  | 10 |  | CH4 | 1756-IF16 | 10 | 13 | 3 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch3Data | // MCR1_R10:13:I.Ch3Data SPARE
|  |  | 10 |  | CH5 | 1756-IF16 | 10 | 13 | 4 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch4Data | // MCR1_R10:13:I.Ch4Data SPARE
|  |  | 10 |  | CH6 | 1756-IF16 | 10 | 13 | 5 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch5Data | // MCR1_R10:13:I.Ch5Data SPARE
|  |  | 10 |  | CH7 | 1756-IF16 | 10 | 13 | 6 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch6Data | // MCR1_R10:13:I.Ch6Data SPARE
|  |  | 10 |  | CH8 | 1756-IF16 | 10 | 13 | 7 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch7Data | // MCR1_R10:13:I.Ch7Data SPARE
|  |  | 10 |  | CH9 | 1756-IF16 | 10 | 13 | 8 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch8Data | // MCR1_R10:13:I.Ch8Data SPARE
|  |  | 10 |  | CH10 | 1756-IF16 | 10 | 13 | 9 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch9Data | // MCR1_R10:13:I.Ch9Data SPARE
|  |  | 10 |  | CH11 | 1756-IF16 | 10 | 13 | 10 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch10Data | // MCR1_R10:13:I.Ch10Data SPARE
|  |  | 10 |  | CH12 | 1756-IF16 | 10 | 13 | 11 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch11Data | // MCR1_R10:13:I.Ch11Data SPARE
|  |  | 10 |  | CH13 | 1756-IF16 | 10 | 13 | 12 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch12Data | // MCR1_R10:13:I.Ch12Data SPARE
|  |  | 10 |  | CH14 | 1756-IF16 | 10 | 13 | 13 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch13Data | // MCR1_R10:13:I.Ch13Data SPARE
|  |  | 10 |  | CH15 | 1756-IF16 | 10 | 13 | 14 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch14Data | // MCR1_R10:13:I.Ch14Data SPARE
|  |  | 10 |  | CH16 | 1756-IF16 | 10 | 13 | 15 |  |  |  | SPARE | [10 empty] | MCR1_R10 | I.Ch | INPUT |  | MCR1_R10:13:I.Ch15Data | // MCR1_R10:13:I.Ch15Data SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 0 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.0 | //MCR4_R23:4:O.Data.0 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 1 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.1 | //MCR4_R23:4:O.Data.1 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 2 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.2 | //MCR4_R23:4:O.Data.2 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 3 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.3 | //MCR4_R23:4:O.Data.3 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 4 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.4 | //MCR4_R23:4:O.Data.4 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 5 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.5 | //MCR4_R23:4:O.Data.5 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 6 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.6 | //MCR4_R23:4:O.Data.6 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 7 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.7 | //MCR4_R23:4:O.Data.7 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 8 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.8 | //MCR4_R23:4:O.Data.8 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 9 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.9 | //MCR4_R23:4:O.Data.9 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 10 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.10 | //MCR4_R23:4:O.Data.10 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 11 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.11 | //MCR4_R23:4:O.Data.11 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 12 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.12 | //MCR4_R23:4:O.Data.12 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 13 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.13 | //MCR4_R23:4:O.Data.13 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 14 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.14 | //MCR4_R23:4:O.Data.14 SPARE
[6 empty] | 1756-OA16I | 23 | 4 | 15 |  |  |  | SPARE | [10 empty] | MCR4_R23 | O.Data | OUTPUT |  | MCR4_R23:4:O.Data.15 | //MCR4_R23:4:O.Data.15 SPARE

## Sheet4
| Minutos | Bloques | Minutos | Horas | Dias
_BC302HP_YAY | 10 | 607 | 6070 | 101.1667 | 8.4306
_BC302TUN_YAY | 10 | 100 | 1000 | 16.6667 | 1.3889
_BC329_YAY
_BC401_WQS
_BC401_WT
_BC4401_M01
_BC4401_EY
_BC4401_MS
_BC4401_PCD
_BC4401_TE
_BC4401_YYS
_BC4402_LT
_BC4504C_M01
_BC4504C_DI
_BC4504C_SPT
_BC4504C_WQS
_WS4504C_WT
_BC4506_M01
_BC4506_MS
_BC4506_WQS
_WS4506_WT
_BC4506_YAY
_BC4514_16_YAY
_BC4514_M01
_BC4516_M01
_BC8225_M01
_BC8302_M01
_BC8302_IT
_BC8302_MS
_BC8302_PCD
_BC8303A_M01
_BC8303A_MS
_BC8329_M01
_BC8329_MS
_BE1317_M01
_BE1317_MS
NOT USED
_BE2317_MS
_BE2317_M01
_BE2317_PCD
_BE4403_M01
_BE4403_EY
_BE4403_IT
_BE4403_MS
_BE4403_YYS
_BE4406E_M01
_BE4406E_EY
_BE4406E_IT
_BE4406E_MS
_BE4406E_YYS
_BE4406W_M01
_BE4406W_EY
_BE4406W_IT
_BE4406W_MS
_BE4406W_YYS
_BE4423_M01
_BE4423_IT
_BE4423_MS
_BE44241_IT
_BE44241_M01
_BE44242_IT
_BE44241_MS
_BE44242_M01
_BE44242_MS
_BE4424C_M01
_BE4424C_IT
_BE4424C_MS
_BE4424C_AUTO
_BE4424C_DISC
_BE4446_M01
_BE4446_EY
_BE4446_IT
_BE4446_MS
_BE4446_YYS
_BE4521_M01
_BE4521_MS
_BE4521_IT
_BIN4461_LAH
_BL4460_AUX
_BM1602_1_IT
_BM1602_2_LT
_BM1602_M01
_BM1602_INLET_TE
_BM1602_IT
_BM1602_OUTLET_TE
_BM1602_TE_DISCHARGE
_BM1602_TE_FEEDEND
_BM2602_1_TE_OUTLET
_BM2602_2_TE_OUTLET
_BM2602_M01
_BM2602_LT
_BM2602_FQS
_BM2602_FSE_DI
_BM2602_FSW_DI
_BM2602_IT
_BM2602_PT
_BM2602_TE_INBOARD
_BM2602_TE_INLET
_BM2602_TE_OUTBOARD
_BM2602_UY
_BM2602_YAY
_BN210_LAH
_BN2318_LAH
_BN2318_LT
_BN318_LAH
_BV1518_M01
_BV2518_M01
_BV4504C_M01
_BV4518_M01
_CA4441_M01
_CAP_ALM
_CL1310_LAH
_CL2310_1_TE_DISCHARGE
CL2310_2_TE_DISCHARGE
_CL2310_LAH
_CL310_DPT
_COAL_BIN_LSH
_COALSILO_TE
_COKEBIN_LSH
_DA2313E
_DC1313_DPT
_DC22313_DPT
_DC2313BH_TE_INLET
_DC2313BH_TE_OUTLET
_DC2313BK_TE_INLET
_DC2319_EXIT_TE
_DC2319_PT
_DG1401_SPT
_DG1401_ZT
_DG1420_SPT
_DG1420_ZT
_DG2401_SPT
_DG2401_ZT
_DG2420_SPT
_DG2420_ZT
__DG4442_ZS_JUNK
_DG44421_ZS_BE4403
_DG44421_ZS_DG4448
_DG444210
_DG44422
_DG44423
_DG44424
_DG44425
_DG44426
_DG44427
_DG44428
_DG44429
_DG4443
_DG4448
_DG4449
_DG4514
_DG4516
_DG8330
_FIREDECK_ALARM
_FIREDP_PT
_FN1307A_M01
_FN1307A_SSA
_FN1312_1_FT
_FN1312_2_FT
_FN1312_IT
_'FN1314_IT
_FN1314_PT_INLET
_FN1321_M01
_FN1326_M01
_FN1308A_M01
_FN1341_M01
_FN1605_M01
_FN1605_INLET_TE
_FN1605_IT
_FN1605_SPT
_FN1605_SSA
_FN1614_M01
_FN2210_M01
_FN2210_SSA
_FN2215_M01
_FN2308_A_M01
_FN2308A_M01
_FN2308A_EY
_FN2308B_M01
_FN2308B_EY
_FN2312_M01
_FN2312_IT
_FN2312_PT
_FN2314_IT
_FN2314_PT_INLET
_FN2314_TE
_FN2314_VT_A
_FN2314_VT_B
_FN23141_TE
_FN23143_TE
_FN23144_TE
_FN23145_TE
_FN23146_TE
_FN2314N_1_TE
_FN2314N_2_TE
_FN2314S_1_TE
_FN2314S_2_TE
_FN2321_M01
_FN2326_M01
_FN2605_M01
_FN2605_1_IT
_FN2605_IT
_FN2605_SSA
_FN2605_HZ
_FN2605_TE_INLET
_FN44141_M01
_FN44141_EY
_FN44141_YYS
_FN4452_M01
_FN4437B_M01
_FN4460_IT
_FN4460_PT_DISCHARGE
_FN4527_M01
_FN47621_M01
_FN7621_M01
_FN8213_M01
_FN8213_SSA
_FV1312_ZT
_FV1340_ZT
_FV1607A_ZT
_FV1607B_ZT
_FV2211_ZT
_FV2215_ZT
_FV2216_ZT
_FV2220_ZT
_FV2228_ZT
_FV2272_TE
_FV2272_ZT
_FV2273_ZT
_FV2308E_TE
_FV2308N_TE
_FV2308S_TE
_FV2308W_TE
_FV2310E_ZT
_FV2310N_ZT
_FV2310S_ZT
_FV2310W_ZT
_FV2313_ZT
_FV2319_ZT
_HM44022_M01
_HM44022_MS
_HM44051_1_AUX
_HM44051_1_COIL
_HM44051_2_AUX
_HM44051_2_COIL
_HM44051_EY
_HM44051_HS
_HM44051_IT
_HM44051_SSA
_HM4422_M01
_HM4422_IT
_HM4422_SSA
_HM4422_YS
_HP260212_PSH
_K1FZ01_TE
_K202_PV
_K22300_PIT
_K2FZ01_TE
_KD1308_1_ALM
_KD1308_2_ALM
_KD1308_LT
_KD1308_LUBE_SV
_KD2308_LT
_KD2308_LUBE_SV
_KD2308_SPT
_KD2308A_RES_DI
_KD2308B_RES_DI
_KD308K1K2_YAY
_KL1301NE_TE
_KL1301NW_TE
_KL1301SE_TE
_KL1301SW_TE
_KL1302NE_TE
_KL1302NW_TE
_KL1302SE_TE
_KL1302SW_TE
_KL13EXIT_TE
_KL1FN_M01
_KL1O2_FS
_KL2301NE_TE
_KL2301NW_TE
_KL2301SE_TE
_KL2301SW_TE
_KL2302NE_TE
_KL2302NW_TE
_KL2302SE_TE
_KL2302SW_TE
_KL2KD_YZ
_KL2OS_FS
_KL2PH01_INLET_ET
_KL2PH01_OUTLET_TE
_KN1_CAN_PAL
_KN1_SA_TE
_KN1BM_DPT
_KN1BP_PT
_KN1HD_PT
_KN2261_1_PT
_KN2261_2_PT
_KN2COALBIN_LAL
_KN2KD_ALM
_KN2PNY_SLOCK_DI
_LKD_1_SYSTEM
_LKD_2_SYSTEM
_MCR1_ALM
_MCR1_UPS_DI
_MCR2_ALM
_MCR3_ALM
_MCR4_ALM
_MCR5_ALM
_MCR6_ALM
_OHV1310_LT
_OV1310_LT
_OV2310_LT
_PC4420_M01
_PC4420_MS
_PC4421_M01
_PC4421_MS
_PC4460_M01
_PH1_PT_OUTLET
_PH1306_IN_TE
_PH1306_OUT_TE
_PH2_FILTER_PH
_PH2_HYD_LL
_PH2_HYD_LLL
_PH2_HYD_OIL_TL
_PH2_PT_OUTLET
_PH2305_LAMPTST
_PH2RAM1_TE
_PH2RAM11_TE
_PH2RAM13_TE
_PH2RAM15_TE
_PH2RAM17_TE
_PH2RAM3_TE
_PH2RAM5_TE
_PH2RAM7_TE
_PH2RAM9_TE
_PL00_AT
_PL00_PAL
_PL00_YAY_A
_PM13051_M01
_PM13052_M01
_PM1602A1_M01
_PM1602A2_M01
_PM23051_M01
_PM23051_PT
_PM23051_SS
_PM23052_M01
_PM23052_PT
_PM23052_SS
_PM26021_M01
_PM26022_M01
_PM4461_M01
_PM4461_IT
_PM46101_M01
_PM46102_M01
_PM4610KL1_FT
_PM4610KL2_1_FT
_PM4610KL2_2_FT
_PNY_SLOCK_DI
_PS_UY
_PU326_LSL
_RA1319_M01
_RA1604_M01
_RA1614_M01
_RA23131_M01
_RA23131_HS
_RA23131_MS
_RA231310_M01
_RA231310_HS
_RA231310_MS
_RA23132_M01
_RA23132_HS
_RA23132_MS
_RA23133_M01
_RA23133_HS
_RA23133_MS
_RA23134_M01
_RA23134_HS
_RA23134_MS
_RA23135_M01
_RA23135_HS
_RA23135_MS
_RA23136_M01
_RA23136_HS
_RA23136_MS
_RA23137_M01
_RA23137_HS
_RA23137_MS
_RA23138_M01
_RA23138_HS
_RA23138_MS
_RA23139_M01
_RA23139_HS
_RA23139_MS
_RA2319_M01
_RA2606_M01
_RA2612_1_M01
_RA2612_2_M01
_RA2612_M01
_RA44144_M01
_RA44144_EY
_RA44144_MS
_RA44144_YYS
_RA4437B_M01
_RA4527_M01
_RA47621_M01
_RC44441_1_M01
_RC44441_2_MS
_RC44441_M01
_RC44441_EY
_RC44441_IT
_RC44441_YYS
_RC44442_1_AUX
_RC44442_2_MS
_RC44442_M01
_RC44442_EY
_RC44442_IT
_RC44442_YYS
_RC45051_M01
_RC45052_M01
_RC4522_1_IT
_RC4522_2_IT
_RC45221_M01
_RC45222_M01
_SB2304_LIH
_SB2304_LIL
_SC_1613_PCD
_SC1316_M01
_SC1316_MS
_SC1316A_M01
_SC1318_M01
_SC1318_MS
_SC1613_M01
_SC1613A_HS
_SC1613A_IT
_SC1613B_AUX
_SC1613B_HS
_SC1613B_IT
_SC1613B_MS
_SC2316_1_AUX
_SC2316_2_AUX
_SC2316_M01
_SC2316A_1_AUX
_SC2316A_2_AUX
_SC2316A_M01
_SC2316B_1_AUX
_SC2316B_2_AUX
_SC2316B_M01
_SC2316C_1_AUX
_SC2316C_M01
_SC2316D_1_AUX
_SC2316D_2_AUX
_SC2316D_M01
_SC2316D_HS
_SC2316E_1_AUX
_SC2316E_2_AUX
_SC2316E_M01
_SC2316E_HS
_SC2316F_1_AUX
_SC2316F_2_AUX
_SC2316F_M01
_SC2316F_HS
_SC2316G_1_AUX
_SC2316G_2_AUX
_SC2316G_M01
_SC2316G_HS
_SC316A_MS
_SC4408_M01
_SC4408_MS
_SC4408A_M01
_SC4408A_MS
_SC4408B_M01
_SC4408B_MS
_SC4408C_M01
_SC4408C_EY
_SC4408C_IT
_SC4408C_MS
_SC4408C_YYS
_SC4412_M01
_SC4412_YYS
_SC44122_MS
_SC44122_YYS
_SC4413_M01
_SC4413_IT
_SC4413_MS
_SC44142_M01
_SC44142_EY
_SC4425_M01
_SC4425_MS
_SC4426_M01
_SC4426_MS
_SC4427_M01
_SC4427_MS
_SC4427_SSA
_SC4427_YS
_SC4428_M01
_SC4428_IT
_SC4428_MS
_SC4428_SSA
_SC4428_YS
_SC443_YYS
_SC4430A_M01
_SC4430A_SSA
_SC4430A_YS
_SC4443_M01
_SC4443_EY
_SC4443_IT
_SC4443_MS
_SC4445_M01
_SC4445_EY
_SC4445_IT
_SC4445_MS
_SC4445_YYS
_SC4447_M01
_SC4447_EY
_SC4447_IT
_SC4447_MS
_SC4447_YYS
_SG4462_SV
_SILO1_LAH
_SILO2_LAH
_SILO3_LAH
_SILO3A_LT
_SILO4_LAH
_SILO5_LAH
_SILO6_LAH
_SL401A_LIH
_SL402A_LIH
_SL403A_LIH
_TK_02_LAH
_TK_02_LAL
_VF1340A_M01
_VF1340A_SPT
_VF1340A_TE
_VF1340B_M01
_VF1340B_SPT
_VF1340B_TE
_VF1340C_M01
_VF1340C_SPT
_VF1340C_TE
_VF1340D_M01
_VF1340D_SPT
_VF1340D_TE
_VF2311_M01
_VF2311_YS
_VF2311_YYS
_VF83011_M01
_VF3011_SPT
_VF83012_M01
_VF3012_SPT
_VF3013_M01
_VF3013_SPT
_VF3014_M01
_VF3014_SPT
_VF3015_M01
_VF3015_SPT
_VF3016_M01
_VF3016_SPT
_VF4504A_M01
_VF4504A_SPT
_VF4504A_SSA
_VF4504B_M01
_VF4504B_SPT
_VF4504B_SSA
_VF504A_PGE_PS
_VF504B_PGE_PS
_VF83011_AUX
_VF83011_SSA
_VF83012_AUX
_VF83012_SSA
_VF83013_AUX
_VF83013_M01
_VF83013_SSA
_VF83014_AUX
_VF83014_M01
_VF83015_AUX
_VF83015_M01
_VF83016_M01
_VS4432_IT
_VS328_IT
_VS4404_M01
_VS4404_EY
_VS4404_IT
_VS4404_YYS
_VS4432_M01
_VS4432_YAY
_VS8328_M01
_WF1601_M01
_WT1601_WS
_WF161_WQS
_WF2601_M01
_WF2601_PCD
_WF2601_SPT
_WF2601_FT
_WF2601A_M01
_WF2601A_FLT
_WF2601A_SSA
_WF2601A_WQS
_WP13261_M01
_WP13262_M01
_WP23261_M01
_WP23262_M01
_WP3083_M01
_WS8303A_WIT
_WS8303A_WQS
_WS8329_WIT
_WS8329_WQS

## Sheet1
FN2314_PT_INLET | K2 ID FAN INLET 0-50" WC
FN1314_PT_INLET | K1 ID FAN INLET PRESSURE 0-50"WC
2313MOD1_ZSO_INLET | MODULE 1 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD1_ZSO_INLET | DA2313MOD1_ZSO_INLET
2313MOD1_ZSC_INLET | MODULE 1 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD1_ZSC_INLET | DA2313MOD1_ZSC_INLET
2313MOD1_ZSO_OUTLET | MODULE 1 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD1_ZSO_OUTLET | DA2313MOD1_ZSO_OUTLET
2313MOD1_ZSC_OUTLET | MODULE 1 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD1_ZSC_OUTLET | DA2313MOD1_ZSC_OUTLET
2313MOD1_SEQ | MODULE 1 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD1_SEQ | KN2313MOD1_SEQ
2313MOD1_SEQ_ADVANCE | MODULE 1 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD1_SEQ_ADVANCE | KN2313MOD1_SEQ_ADVANCE
2313MOD2_ZSO_INLET | MODULE 2 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD2_ZSO_INLET | DA2313MOD2_ZSO_INLET
2313MOD2_ZSC_INLET | MODULE 2 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD2_ZSC_INLET | DA2313MOD2_ZSC_INLET
2313MOD2_ZSO_OUTLET | MODULE 2 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD2_ZSO_OUTLET | DA2313MOD2_ZSO_OUTLET
2313MOD2_ZSC_OUTLET | MODULE 2 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD2_ZSC_OUTLET | DA2313MOD2_ZSC_OUTLET
2313MOD2_SEQ | MODULE 2 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD2_SEQ | KN2313MOD2_SEQ
2313MOD2_SEQ_ADVANCE | MODULE 2 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD2_SEQ_ADVANCE | KN2313MOD2_SEQ_ADVANCE
2313MOD3_ZSO_INLET | MODULE 3 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD3_ZSO_INLET | DA2313MOD3_ZSO_INLET
2313MOD3_ZSC_INLET | MODULE 3 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD3_ZSC_INLET | DA2313MOD3_ZSC_INLET
2313MOD3_ZSO_OUTLET | MODULE 3 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD3_ZSO_OUTLET | DA2313MOD3_ZSO_OUTLET
2313MOD3_ZSC_OUTLET | MODULE 3 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD3_ZSC_OUTLET | DA2313MOD3_ZSC_OUTLET
2313MOD3_SEQ | MODULE 3 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD3_SEQ | KN2313MOD3_SEQ
2313MOD3_SEQ_ADVANCE | MODULE 3 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD3_SEQ_ADVANCE | KN2313MOD3_SEQ_ADVANCE
2313MOD4_ZSO_INLET | MODULE 4 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD4_ZSO_INLET | DA2313MOD4_ZSO_INLET
2313MOD4_ZSC_INLET | MODULE 4 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD4_ZSC_INLET | DA2313MOD4_ZSC_INLET
2313MOD4_ZSO_OUTLET | MODULE 4 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD4_ZSO_OUTLET | DA2313MOD4_ZSO_OUTLET
2313MOD4_ZSC_OUTLET | MODULE 4 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD4_ZSC_OUTLET | DA2313MOD4_ZSC_OUTLET
2313MOD4_SEQ | MODULE 4 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD4_SEQ | KN2313MOD4_SEQ
2313MOD4_SEQ_ADVANCE | MODULE 4 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD4_SEQ_ADVANCE | KN2313MOD4_SEQ_ADVANCE
2313MOD5_ZSO_INLET | MODULE 5 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD5_ZSO_INLET | DA2313MOD5_ZSO_INLET
2313MOD5_ZSC_INLET | MODULE 5 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD5_ZSC_INLET | DA2313MOD5_ZSC_INLET
2313MOD5_ZSO_OUTLET | MODULE 5 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD5_ZSO_OUTLET | DA2313MOD5_ZSO_OUTLET
2313MOD5_ZSC_OUTLET | MODULE 5 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD5_ZSC_OUTLET | DA2313MOD5_ZSC_OUTLET
2313MOD5_SEQ | MODULE 5 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD5_SEQ | KN2313MOD5_SEQ
2313MOD5_SEQ_ADVANCE | MODULE 5 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD5_SEQ_ADVANCE | KN2313MOD5_SEQ_ADVANCE
2313MOD6_ZSO_INLET | MODULE 6 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD6_ZSO_INLET | DA2313MOD6_ZSO_INLET
2313MOD6_ZSC_INLET | MODULE 6 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD6_ZSC_INLET | DA2313MOD6_ZSC_INLET
2313MOD6_ZSO_OUTLET | MODULE 6 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD6_ZSO_OUTLET | DA2313MOD6_ZSO_OUTLET
2313MOD6_ZSC_OUTLET | MODULE 6 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD6_ZSC_OUTLET | DA2313MOD6_ZSC_OUTLET
2313MOD6_SEQ | MODULE 6 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD6_SEQ | KN2313MOD6_SEQ
2313MOD6_SEQ_ADVANCE | MODULE 6 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD6_SEQ_ADVANCE | KN2313MOD6_SEQ_ADVANCE
2313MOD7_ZSO_INLET | MODULE 7 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD7_ZSO_INLET | DA2313MOD7_ZSO_INLET
2313MOD7_ZSC_INLET | MODULE 7 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD7_ZSC_INLET | DA2313MOD7_ZSC_INLET
2313MOD7_ZSO_OUTLET | MODULE 7 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD7_ZSO_OUTLET | DA2313MOD7_ZSO_OUTLET
2313MOD7_ZSC_OUTLET | MODULE 7 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD7_ZSC_OUTLET | DA2313MOD7_ZSC_OUTLET
2313MOD7_SEQ | MODULE 7 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD7_SEQ | KN2313MOD7_SEQ
2313MOD7_SEQ_ADVANCE | MODULE 7 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD7_SEQ_ADVANCE | KN2313MOD7_SEQ_ADVANCE
2313MOD8_ZSO_INLET | MODULE 8 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD8_ZSO_INLET | DA2313MOD8_ZSO_INLET
2313MOD8_ZSC_INLET | MODULE 8 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD8_ZSC_INLET | DA2313MOD8_ZSC_INLET
2313MOD8_ZSO_OUTLET | MODULE 8 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD8_ZSO_OUTLET | DA2313MOD8_ZSO_OUTLET
2313MOD8_ZSC_OUTLET | MODULE 8 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD8_ZSC_OUTLET | DA2313MOD8_ZSC_OUTLET
2313MOD8_SEQ | MODULE 8 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD8_SEQ | KN2313MOD8_SEQ
2313MOD8_SEQ_ADVANCE | MODULE 8 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD8_SEQ_ADVANCE | KN2313MOD8_SEQ_ADVANCE
2313MOD9_ZSO_INLET | MODULE 9 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD9_ZSO_INLET | DA2313MOD9_ZSO_INLET
2313MOD9_ZSC_INLET | MODULE 9 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD9_ZSC_INLET | DA2313MOD9_ZSC_INLET
2313MOD9_ZSO_OUTLET | MODULE 9 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD9_ZSO_OUTLET | DA2313MOD9_ZSO_OUTLET
2313MOD9_ZSC_OUTLET | MODULE 9 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD9_ZSC_OUTLET | DA2313MOD9_ZSC_OUTLET
2313MOD9_SEQ | MODULE 9 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD9_SEQ | KN2313MOD9_SEQ
2313MOD9_SEQ_ADVANCE | MODULE 9 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD9_SEQ_ADVANCE | KN2313MOD9_SEQ_ADVANCE
2313MOD10_ZSO_INLET | MODULE 10 DAMPER OPEN KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD10_ZSO_INLET | DA2313MOD10_ZSO_INLET
2313MOD10_ZSC_INLET | MODULE 10 DAMPER CLOSED KILN 2 BAGHOUSE INLET DAMPER | DA | DA2313MOD10_ZSC_INLET | DA2313MOD10_ZSC_INLET
2313MOD10_ZSO_OUTLET | MODULE 10 DAMPER OPEN KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD10_ZSO_OUTLET | DA2313MOD10_ZSO_OUTLET
2313MOD10_ZSC_OUTLET | MODULE 10 DAMPER CLOSED KILN 2 BAGHOUSE OUTLET DAMPER | DA | DA2313MOD10_ZSC_OUTLET | DA2313MOD10_ZSC_OUTLET
2313MOD10_SEQ | MODULE 10 SEQUENCER KILN 2 BAGHOUSE | KN | KN2313MOD10_SEQ | KN2313MOD10_SEQ
2313MOD10_SEQ_ADVANCE | MODULE 10 SEQUENCER KILN 2 BAGHOUSE CARD IN LAST POSITION | KN | KN2313MOD10_SEQ_ADVANCE | KN2313MOD10_SEQ_ADVANCE
26021&2_PSH | 2-602-1&2 HIGH PRESSURE SWITCHES | HP | HP26021&2_PSH | HP26021&2_PSH

## Sheet2
RA2612 | 1 | AUX | IO | _RA2612
CA4441 | AUX | IO |  | _CA4441
FN2326 | AUX | IO |  | _FN2326
WP23261 | AUX | IO |  | _WP23261
WP23262 | AUX | IO |  | _WP23262
WF2601 | AUX | IO |  | _WF2601
PM46101 | AUX | IO |  | _PM46101
PM46102 | AUX | IO |  | _PM46102
BE44241 | AUX | IO |  | _BE44241
BE44242 | AUX | IO |  | _BE44242
BE4423 | AUX | IO |  | _BE4423
SC4426 | AUX | IO |  | _SC4426
PC4420 | AUX | IO |  | _PC4420
FN2308A | 1 | AUX | IO | _FN2308A
PM26021 | AUX | IO |  | _PM26021
PM26022 | AUX | IO |  | _PM26022
RA2606 | AUX | IO |  | _RA2606
FN2215 | AUX | IO |  | _FN2215
PC4421 | AUX | IO |  | _PC4421
VF2311 | AUX | IO |  | _VF2311
RA2612 | AUX | IO |  | _RA2612
FN4437 | AUX | IO |  | _FN4437
VS4432 | AUX | IO |  | _VS4432
SC4413 | AUX | IO |  | _SC4413
FN4452 | AUX | IO |  | _FN4452
FN4430 | AUX | IO |  | _FN4430
FN44195 | AUX | IO |  | _FN44195
FN47621 | AUX | IO |  | _FN47621
FN2605 | AUX | IO |  | _FN2605
BM2602 | AUX | IO |  | _BM2602
SC4425 | AUX | IO |  | _SC4425
SC1316 | AUX | IO |  | _SC1316
SC1316A | AUX | IO |  | _SC1316A
BE1317 | AUX | IO |  | _BE1317
SC1318 | AUX | IO |  | _SC1318
RA1319 | AUX | IO |  | _RA1319
FN1321 | AUX | IO |  | _FN1321
BC8225 | AUX | IO |  | _BC8225
PM13052 | AUX | IO |  | _PM13052
PM13051 | AUX | IO |  | _PM13051
FN1326 | AUX | IO |  | _FN1326
WP13261 | AUX | IO |  | _WP13261
WP13262 | AUX | IO |  | _WP13262
FN1307 | AUX | IO |  | _FN1307
WP3083 | AUX | IO |  | _WP3083
FN8213 | AUX | IO |  | _FN8213
BC8302 | AUX | IO |  | _BC8302
VS8328 | AUX | IO |  | _VS8328
BC8329 | AUX | IO |  | _BC8329
KL1FN | AUX | IO |  | _KL1FN
VF1340A | AUX | IO |  | _VF1340A
VF1340B | AUX | IO |  | _VF1340B
VF1340C | AUX | IO |  | _VF1340C
VF1340D | AUX | IO |  | _VF1340D
WF1601 | AUX | IO |  | _WF1601
PM23051 | AUX | IO |  | _PM23051
PM23052 | AUX | IO |  | _PM23052
VF3011 | AUX | IO |  | _VF3011
VF3012 | AUX | IO |  | _VF3012
VF3013 | AUX | IO |  | _VF3013
VF3014 | AUX | IO |  | _VF3014
VF3015 | AUX | IO |  | _VF3015
VF3016 | AUX | IO |  | _VF3016
VF83011 | AUX | IO |  | _VF83011
VF83012 | AUX | IO |  | _VF83012
VF83013 | AUX | IO |  | _VF83013
FN2321 | AUX | IO |  | _FN2321
SC2316 | 1 | AUX | IO | _SC2316
SC2316A | 1 | AUX | IO | _SC2316A
SC2316B | 1 | AUX | IO | _SC2316B
SC2316C | 1 | AUX | IO | _SC2316C
BE2317 | 1 | AUX | IO | _BE2317
BL4460 | AUX | IO |  | _BL4460
PM4461 | AUX | IO |  | _PM4461
RA2319 | AUX | IO |  | _RA2319
VF83015 | AUX | IO |  | _VF83015
VF83016 | AUX | IO |  | _VF83016
VF83014 | AUX | IO |  | _VF83014
BC8303A | AUX | IO |  | _BC8303A
BE2317 | 2 | AUX | IO | _BE2317
SC2316 | 2 | AUX | IO | _SC2316
SC2316A | 2 | AUX | IO | _SC2316A
SC2316B | 2 | AUX | IO | _SC2316B
SC2316C | 2 | AUX | IO | _SC2316C
BE2317 | 3 | AUX | IO | _BE2317
FN1331 | AUX | DO | IO | _FN1331
BM1602 | AUX | DO | IO | _BM1602
FN2314 | AUX | DO | IO | _FN2314
BM2602 | AUX | DO | IO | _BM2602
FN2308A | 2 | AUX | IO | _FN2308A
FN2308B | AUX | IO |  | _FN2308B
BC4401 | AUX | IO |  | _BC4401
BE4403 | AUX | IO |  | _BE4403
SC4443 | 1 | AUX | IO | _SC4443
RC44441 | 1 | AUX | IO | _RC44441
RC44442 | 1 | AUX | IO | _RC44442
SC4412 | AUX | IO |  | _SC4412
SC4445 | AUX | IO |  | _SC4445
BE4446 | AUX | IO |  | _BE4446
HM44051 | 1 | AUX | IO | _HM44051
HM44051 | 2 | AUX | IO | _HM44051
VS4404 | AUX | IO |  | _VS4404
SC4447 | AUX | IO |  | _SC4447
BE4406W | AUX | IO |  | _BE4406W
SC1613B | AUX | IO |  | _SC1613B
SC4408A | AUX | IO |  | _SC4408A
SC4408B | AUX | IO |  | _SC4408B
BE4406E | AUX | IO |  | _BE4406E
SC4408 | AUX | IO |  | _SC4408
SC4408C | AUX | IO |  | _SC4408C
FN44141 | AUX | IO |  | _FN44141
SC44142 | AUX | IO |  | _SC44142
RA44144 | AUX | IO |  | _RA44144
BC4504C | AUX | IO |  | _BC4504C
BC4506 | 1 | AUX | IO | _BC4506
SC4443 | 2 | AUX | IO | _SC4443
FN1605 | AUX | IO |  | _FN1605
FN1335 | AUX | IO |  | _FN1335
FN1614 | AUX | IO |  | _FN1614
BV1518 | AUX | IO |  | _BV1518
RA1614 | AUX | IO |  | _RA1614
BM1602 | AUX | IO |  | _BM1602
FN1341 | AUX | IO |  | _FN1341
VF4504A | AUX | IO |  | _VF4504A
VF4504B | AUX | IO |  | _VF4504B
RC45051 | AUX | IO |  | _RC45051
RC45052 | AUX | IO |  | _RC45052
BC4506 | 2 | AUX | IO | _BC4506
BC4514 | AUX | IO |  | _BC4514
PM1602A1 | AUX | IO |  | _PM1602A1
PM1602A2 | AUX | IO |  | _PM1602A2
RC44441 | 2 | AUX | IO | _RC44441
RC44442 | 2 | AUX | IO | _RC44442
RA23131 | AUX | IO |  | _RA23131
RA23132 | AUX | IO |  | _RA23132
RA23133 | AUX | IO |  | _RA23133
RA23134 | AUX | IO |  | _RA23134
RA23135 | AUX | IO |  | _RA23135
RA23136 | AUX | IO |  | _RA23136
RA23137 | AUX | IO |  | _RA23137
RA23138 | AUX | IO |  | _RA23138
RA23139 | AUX | IO |  | _RA23139
RA231310 | AUX | IO |  | _RA231310
SC2316G | 1 | AUX | IO | _SC2316G
SC2316F | 1 | AUX | IO | _SC2316F
SC2316E | 1 | AUX | IO | _SC2316E
SC2316D | 1 | AUX | IO | _SC2316D
SC2316G | 2 | AUX | IO | _SC2316G
SC2316F | 2 | AUX | IO | _SC2316F
SC2316E | 2 | AUX | IO | _SC2316E
SC2316D | 2 | AUX | IO | _SC2316D
FN4437A | AUX | IO |  | _FN4437A
FN4437C | AUX | IO |  | _FN4437C
RA4437B | AUX | IO |  | _RA4437B
FN4437D | AUX | IO |  | _FN4437D
RA47621 | AUX | IO |  | _RA47621
FN4437E | AUX | IO |  | _FN4437E
FN4527 | AUX | IO |  | _FN4527
FN4437F | AUX | IO |  | _FN4437F
RA4527 | AUX | IO |  | _RA4527
BV2518 | AUX | IO |  | _BV2518
RC45221 | AUX | IO |  | _RC45221
RC45222 | AUX | IO |  | _RC45222
BE4521 | AUX | IO |  | _BE4521
BC4516 | AUX | IO |  | _BC4516
BE4424C | AUX | IO |  | _BE4424C
SC4428 | AUX | IO |  | _SC4428
HM4422 | AUX | IO |  | _HM4422
SC441 | AUX | IO |  | _SC441
SC4430A | AUX | IO |  | _SC4430A
FN2210 | AUX | IO |  | _FN2210
BC434 | AUX | IO |  | _BC434
SC4427 | AUX | IO |  | _SC4427
WF2601A | AUX | IO |  | _WF2601A

## Sheet3
BC302HP_YAY | BC302HP | YAY |  | _BC302HP_YAY
BC302TUN_YAY | BC302TUN | YAY |  | _BC302TUN_YAY
BC329_YAY | BC329 | YAY |  | _BC329_YAY
BC401_WQS | BC401 | WQS |  | _BC401_WQS
BC401_WT | BC401 | WT |  | _BC401_WT
_
BC434_AUX | BC434 | AUX |  | _BC434_M01
BC434_HAND_DO | BC434 | HAND | DO | _BC434_HAND_DO
BC434_HSE_A | BC434 | HSE | A | _BC434_HSE_A
BC434_HSE_B | BC434 | HSE | B | _BC434_HSE_B
BC434_START_DO | BC434 | START | DO | _BC434_START_DO
BC434_YAY | BC434 | YAY |  | _BC434_YAY
BC4401_AUX | BC4401 | AUX |  | _BC4401_M01
BC4401_COIL | BC4401 | COIL |  | _BC4401_M01
_
BC4401_EY | BC4401 | EY |  | _BC4401_EY
BC4401_MS | BC4401 | MS |  | _BC4401_MS
BC4401_PCD | BC4401 | PCD |  | _BC4401_PCD
BC4401_TE | BC4401 | TE |  | _BC4401_TE
BC4401_YYS | BC4401 | YYS |  | _BC4401_YYS
BC4402_LT | BC4402 | LT |  | _BC4402_LT
_
_
_
_
BC4504C_AUX | BC4504C | AUX |  | _BC4504C_M01
BC4504C_COIL | BC4504C | COIL |  | _BC4504C_M01
BC4504C_DI | BC4504C | DI |  | _BC4504C_DI
BC4504C_FLT_DI | BC4504C | FLT | DI | _BC4504C_FLT_DI
BC4504C_SPT | BC4504C | SPT |  | _BC4504C_SPT
BC4504C_WQS | BC4504C | WQS |  | _BC4504C_WQS
BC4504C_WT | BC4504C | WT |  | _BC4504C_WT
BC4506_1_AUX | BC4506 | 1 | AUX | _BC4506_1_AUX
BC4506_2_AUX | BC4506 | 2 | AUX | _BC4506_2_AUX
BC4506_COIL | BC4506 | COIL |  | _BC4506_M01
BC4506_WQS | BC4506 | WQS |  | _BC4506_WQS
BC4506_WT | BC4506 | WT |  | _BC4506_WT
BC4506_YAY | BC4506 | YAY |  | _BC4506_YAY
BC4514_16_YAY | BC4514 | 16 | YAY | _BC4514_16_YAY
BC4514_AUX | BC4514 | AUX |  | _BC4514_M01
BC4514_COIL | BC4514 | COIL |  | _BC4514_M01
BC4516_AUX | BC4516 | AUX |  | _BC4516_M01
BC4516_COIL | BC4516 | COIL |  | _BC4516_M01
BC8225_AUX | BC8225 | AUX |  | _BC8225_M01
_
BC8225_COIL | BC8225 | COIL |  | _BC8225_M01
BC8302_AUX | BC8302 | AUX |  | _BC8302_M01
BC8302_COIL | BC8302 | COIL |  | _BC8302_M01
BC8302_IT | BC8302 | IT |  | _BC8302_IT
BC8302_MS | BC8302 | MS |  | _BC8302_MS
BC8302_PCD | BC8302 | PCD |  | _BC8302_PCD
BC8303A_AUX | BC8303A | AUX |  | _BC8303A_M01
BC8303A_COIL | BC8303A | COIL |  | _BC8303A_M01
BC8303A_MS | BC8303A | MS |  | _BC8303A_MS
BC8329_AUX | BC8329 | AUX |  | _BC8329_M01
BC8329_COIL | BC8329 | COIL |  | _BC8329_M01
BC8329_MS | BC8329 | MS |  | _BC8329_MS
BE1317_AUX | BE1317 | AUX |  | _BE1317_M01
BE1317_COIL | BE1317 | COIL |  | _BE1317_M01
BE1317_DI | BE1317 | DI |  | _BE1317_DI
_
BE1317_MS | BE1317 | MS |  | _BE1317_MS
BE1317_PB_JOG | BE1317 | PB | JOG | _BE1317_PB_JOG
BE2317_1_AUX | BE2317 | 1 | AUX | _BE2317_1_AUX
BE2317_2_AUX | BE2317 | 2 | AUX | _BE2317_2_AUX
_
BE2317_3_AUX | BE2317 | 3 | AUX | _BE2317_3_AUX
BE2317_COIL | BE2317 | COIL |  | _BE2317_M01
BE2317_PCD | BE2317 | PCD |  | _BE2317_PCD
BE4403_AUX | BE4403 | AUX |  | _BE4403_M01
BE4403_COIL | BE4403 | COIL |  | _BE4403_M01
_
BE4403_EY | BE4403 | EY |  | _BE4403_EY
BE4403_IT | BE4403 | IT |  | _BE4403_IT
BE4403_JOG_SET | BE4403 | JOG | SET | _BE4403_JOG_SET
BE4403_MS | BE4403 | MS |  | _BE4403_MS
BE4403_PB_JOG | BE4403 | PB | JOG | _BE4403_PB_JOG
BE4403_YYS | BE4403 | YYS |  | _BE4403_YYS
_
_
BE4406E_AUX | BE4406E | AUX |  | _BE4406E_M01
BE4406E_COIL | BE4406E | COIL |  | _BE4406E_M01
BE4406E_EY | BE4406E | EY |  | _BE4406E_EY
BE4406E_IT | BE4406E | IT |  | _BE4406E_IT
BE4406E_JOG_SET | BE4406E | JOG | SET | _BE4406E_JOG_SET
BE4406E_MS | BE4406E | MS |  | _BE4406E_MS
BE4406E_PB_JOG | BE4406E | PB | JOG | _BE4406E_PB_JOG
BE4406E_YYS | BE4406E | YYS |  | _BE4406E_YYS
BE4406W_AUX | BE4406W | AUX |  | _BE4406W_M01
BE4406W_COIL | BE4406W | COIL |  | _BE4406W_M01
BE4406W_EY | BE4406W | EY |  | _BE4406W_EY
BE4406W_IT | BE4406W | IT |  | _BE4406W_IT
BE4406W_JOG_SET | BE4406W | JOG | SET | _BE4406W_JOG_SET
BE4406W_MS | BE4406W | MS |  | _BE4406W_MS
BE4406W_PB_JOG | BE4406W | PB | JOG | _BE4406W_PB_JOG
BE4406W_YYS | BE4406W | YYS |  | _BE4406W_YYS
BE4423_AUX | BE4423 | AUX |  | _BE4423_M01
BE4423_COIL | BE4423 | COIL |  | _BE4423_M01
BE4423_IT | BE4423 | IT |  | _BE4423_IT
BE4423_JOG_SET | BE4423 | JOG | SET | _BE4423_JOG_SET
BE4423_MS | BE4423 | MS |  | _BE4423_MS
BE4423_PB_JOG | BE4423 | PB | JOG | _BE4423_PB_JOG
BE4424_1_IT | BE4424 | 1 | IT | _BE4424_1_IT
BE4424_1_JOG_SET | BE4424 | 1 | JOG | _BE4424_1_JOG_SET
BE4424_2_IT | BE4424 | 2 | IT | _BE4424_2_IT
BE44241_AUX | BE44241 | AUX |  | _BE44241_M01
_
BE44241_COIL | BE44241 | COIL |  | _BE44241_M01
BE44241_MS | BE44241 | MS |  | _BE44241_MS
BE44241_PB_JOG | BE44241 | PB | JOG | _BE44241_PB_JOG
BE44242_AUX | BE44242 | AUX |  | _BE44242_M01
BE44242_COIL | BE44242 | COIL |  | _BE44242_M01
BE44242_JOG_SET | BE44242 | JOG | SET | _BE44242_JOG_SET
BE44242_MS | BE44242 | MS |  | _BE44242_MS
BE44242_PB_JOG | BE44242 | PB | JOG | _BE44242_PB_JOG
BE4424C_AUX | BE4424C | AUX |  | _BE4424C_M01
BE4424C_COIL | BE4424C | COIL |  | _BE4424C_M01
BE4424C_IT | BE4424C | IT |  | _BE4424C_IT
BE4424C_JOG_SET | BE4424C | JOG | SET | _BE4424C_JOG_SET
BE4424C_MS | BE4424C | MS |  | _BE4424C_MS
BE4424C_PB_JOG | BE4424C | PB | JOG | _BE4424C_PB_JOG
BE4424C_SSA | BE4424C | SSA |  | _BE4424C_SSA
BE4424C_YS | BE4424C | YS |  | _BE4424C_YS
BE4446_AUX | BE4446 | AUX |  | _BE4446_M01
BE4446_COIL | BE4446 | COIL |  | _BE4446_M01
BE4446_EY | BE4446 | EY |  | _BE4446_EY
BE4446_IT | BE4446 | IT |  | _BE4446_IT
BE4446_JOG_SET | BE4446 | JOG | SET | _BE4446_JOG_SET
BE4446_MS | BE4446 | MS |  | _BE4446_MS
BE4446_PB_JOG | BE4446 | PB | JOG | _BE4446_PB_JOG
BE4446_YYS | BE4446 | YYS |  | _BE4446_YYS
BE4521_AUX | BE4521 | AUX |  | _BE4521_M01
BE4521_COIL | BE4521 | COIL |  | _BE4521_M01
BE4521_JOG_SET | BE4521 | JOG | SET | _BE4521_JOG_SET
BE4521_MS | BE4521 | MS |  | _BE4521_MS
BE4521_PB_JOG | BE4521 | PB | JOG | _BE4521_PB_JOG
BE521_IT | BE521 | IT |  | _BE521_IT
BIN4461_LAH | BIN4461 | LAH |  | _BIN4461_LAH
BL4460_AUX | BL4460 | AUX |  | _BL4460_M01
BM1602_1_IT | BM1602 | 1 | IT | _BM1602_1_IT
BM1602_2_LT | BM1602 | 2 | LT | _BM1602_2_LT
BM1602_AUX_DO | BM1602 | AUX | DO | _BM1602_M01
BM1602_AUX | BM1602 | AUX |  | _BM1602_M01
_
_
_
_
_
_
BM1602_COIL | BM1602 | COIL |  | _BM1602_M01
BM1602_INLET_TE | BM1602 | INLET | TE | _BM1602_INLET_TE
_
_
_
_
_
_
_
BM1602_IT | BM1602 | IT |  | _BM1602_IT
BM1602_LUBE_LAL | BM1602 | LUBE | LAL | _BM1602_LUBE_LAL
_
_
_
_
_
_
_
_
_
_
_
_
_
_
BM1602_LUBE_SV | BM1602 | LUBE | SV | _BM1602_LUBE_SV
BM1602_OUTLET_TE | BM1602 | OUTLET | TE | _BM1602_OUTLET_TE
BM1602_TE_DISCHARGE | BM1602 | TE | DISCHARGE | _BM1602_TE_DISCHARGE
BM1602_TE_FEEDEND | BM1602 | TE | FEEDEND | _BM1602_TE_FEEDEND
BM1602_YAY | BM1602 | YAY |  | _BM1602_YAY
BM1602_YYS | BM1602 | YYS |  | _BM1602_YYS
_
_
_
_
_
_
_
_
_
_
BM2602_1_TE_OUTLET | BM2602 | 1 | TE | _BM2602_1_TE_OUTLET
BM2602_2_TE_OUTLET | BM2602 | 2 | TE | _BM2602_2_TE_OUTLET
BM2602_AUX_DO | BM2602 | AUX | DO | _BM2602_M01
BM2602_AUX | BM2602 | AUX |  | _BM2602_M01
BM2602_B_LT | BM2602 | B | LT | _BM2602_B_LT
BM2602_COIL | BM2602 | COIL |  | _BM2602_M01
BM2602_FQS | BM2602 | FQS |  | _BM2602_FQS
BM2602_FSE_DI | BM2602 | FSE | DI | _BM2602_FSE_DI
BM2602_FSW_DI | BM2602 | FSW | DI | _BM2602_FSW_DI
BM2602_IT | BM2602 | IT |  | _BM2602_IT
_
_
_
BM2602_LT | BM2602 | LT |  | _BM2602_LT
BM2602_PT | BM2602 | PT |  | _BM2602_PT
BM2602_TE_INBOARD | BM2602 | TE | INBOARD | _BM2602_TE_INBOARD
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
BM2602_TE_INLET | BM2602 | TE | INLET | _BM2602_TE_INLET
_
BM2602_TE_OUTBOARD | BM2602 | TE | OUTBOARD | _BM2602_TE_OUTBOARD
BM2602_UY | BM2602 | UY |  | _BM2602_UY
BM2602_YAY | BM2602 | YAY |  | _BM2602_YAY
BN210_LAH | BN210 | LAH |  | _BN210_LAH
BN2318_LAH | BN2318 | LAH |  | _BN2318_LAH
BN2318_LT | BN2318 | LT |  | _BN2318_LT
_
_
BN318_LAH | BN318 | LAH |  | _BN318_LAH
_
BV1518_AUX | BV1518 | AUX |  | _BV1518_M01
_
_
_
BV2518_AUX | BV2518 | AUX |  | _BV2518_M01
_
_
BV2518_COIL | BV2518 | COIL |  | _BV2518_M01
BV4504C_COIL | BV4504C | COIL |  | _BV4504C_M01
BV4518_COIL | BV4518 | COIL |  | _BV4518_M01
CA4441_AUX | CA4441 | AUX |  | _CA4441_M01
CA4441_COIL | CA4441 | COIL |  | _CA4441_M01
_
_
CAP_ALM | CAP | ALM |  | _CAP_ALM
CL1310_LAH | CL1310 | LAH |  | _CL1310_LAH
CL2310_1_TE_DISCHARGE | CL2310 | 1 | TE | _CL2310_1_TE_DISCHARGE
CL2310_2_TE_DISCHARGE | CL2310 | 2 | TE | _CL2310_2_TE_DISCHARGE
CL2310_LAH | CL2310 | LAH |  | _CL2310_LAH
CL310_DPT | CL310 | DPT |  | _CL310_DPT
_
_
COAL_BIN_LSH | COAL | BIN | LSH | _COAL_BIN_LSH
_
_
_
_
_
_
_
_
_
_
_
_
_
COALSILO_TE | COALSILO | TE |  | _COALSILO_TE
COKEBIN_LSH | COKEBIN | LSH |  | _COKEBIN_LSH
DA2313E_XY_A | DA2313E | XY | A | _DA2313E_XY_A
DA2313E_XY_B | DA2313E | XY | B | _DA2313E_XY_B
DA2313E_ZSC | DA2313E | ZSC |  | _DA2313E_ZSC
DA2313E_ZSO | DA2313E | ZSO |  | _DA2313E_ZSO
DA2313MOD1_ZSC_INLET | DA2313MOD1 | ZSC | INLET | _DA2313MOD1_ZSC_INLET
DA2313MOD1_ZSC_OUTLET | DA2313MOD1 | ZSC | OUTLET | _DA2313MOD1_ZSC_OUTLET
DA2313MOD1_ZSO_INLET | DA2313MOD1 | ZSO | INLET | _DA2313MOD1_ZSO_INLET
DA2313MOD1_ZSO_OUTLET | DA2313MOD1 | ZSO | OUTLET | _DA2313MOD1_ZSO_OUTLET
DA2313MOD10_ZSC_INLET | DA2313MOD10 | ZSC | INLET | _DA2313MOD10_ZSC_INLET
DA2313MOD10_ZSC_OUTLET | DA2313MOD10 | ZSC | OUTLET | _DA2313MOD10_ZSC_OUTLET
DA2313MOD10_ZSO_INLET | DA2313MOD10 | ZSO | INLET | _DA2313MOD10_ZSO_INLET
DA2313MOD10_ZSO_OUTLET | DA2313MOD10 | ZSO | OUTLET | _DA2313MOD10_ZSO_OUTLET
DA2313MOD2_ZSC_INLET | DA2313MOD2 | ZSC | INLET | _DA2313MOD2_ZSC_INLET
_
_
DA2313MOD2_ZSC_OUTLET | DA2313MOD2 | ZSC | OUTLET | _DA2313MOD2_ZSC_OUTLET
DA2313MOD2_ZSO_INLET | DA2313MOD2 | ZSO | INLET | _DA2313MOD2_ZSO_INLET
DA2313MOD2_ZSO_OUTLET | DA2313MOD2 | ZSO | OUTLET | _DA2313MOD2_ZSO_OUTLET
DA2313MOD3_ZSC_INLET | DA2313MOD3 | ZSC | INLET | _DA2313MOD3_ZSC_INLET
DA2313MOD3_ZSC_OUTLET | DA2313MOD3 | ZSC | OUTLET | _DA2313MOD3_ZSC_OUTLET
DA2313MOD3_ZSO_INLET | DA2313MOD3 | ZSO | INLET | _DA2313MOD3_ZSO_INLET
DA2313MOD3_ZSO_OUTLET | DA2313MOD3 | ZSO | OUTLET | _DA2313MOD3_ZSO_OUTLET
_
_
DA2313MOD4_ZSC_INLET | DA2313MOD4 | ZSC | INLET | _DA2313MOD4_ZSC_INLET
_
DA2313MOD4_ZSC_OUTLET | DA2313MOD4 | ZSC | OUTLET | _DA2313MOD4_ZSC_OUTLET
DA2313MOD4_ZSO_INLET | DA2313MOD4 | ZSO | INLET | _DA2313MOD4_ZSO_INLET
DA2313MOD4_ZSO_OUTLET | DA2313MOD4 | ZSO | OUTLET | _DA2313MOD4_ZSO_OUTLET
DA2313MOD5_ZSC_INLET | DA2313MOD5 | ZSC | INLET | _DA2313MOD5_ZSC_INLET
_
_
DA2313MOD5_ZSC_OUTLET | DA2313MOD5 | ZSC | OUTLET | _DA2313MOD5_ZSC_OUTLET
DA2313MOD5_ZSO_INLET | DA2313MOD5 | ZSO | INLET | _DA2313MOD5_ZSO_INLET
DA2313MOD5_ZSO_OUTLET | DA2313MOD5 | ZSO | OUTLET | _DA2313MOD5_ZSO_OUTLET
DA2313MOD6_ZSC_INLET | DA2313MOD6 | ZSC | INLET | _DA2313MOD6_ZSC_INLET
_
_
DA2313MOD6_ZSC_OUTLET | DA2313MOD6 | ZSC | OUTLET | _DA2313MOD6_ZSC_OUTLET
_
DA2313MOD6_ZSO_INLET | DA2313MOD6 | ZSO | INLET | _DA2313MOD6_ZSO_INLET
DA2313MOD6_ZSO_OUTLET | DA2313MOD6 | ZSO | OUTLET | _DA2313MOD6_ZSO_OUTLET
_
_
_
_
DA2313MOD7_ZSC_INLET | DA2313MOD7 | ZSC | INLET | _DA2313MOD7_ZSC_INLET
DA2313MOD7_ZSC_OUTLET | DA2313MOD7 | ZSC | OUTLET | _DA2313MOD7_ZSC_OUTLET
DA2313MOD7_ZSO_INLET | DA2313MOD7 | ZSO | INLET | _DA2313MOD7_ZSO_INLET
DA2313MOD7_ZSO_OUTLET | DA2313MOD7 | ZSO | OUTLET | _DA2313MOD7_ZSO_OUTLET
DA2313MOD8_ZSC_INLET | DA2313MOD8 | ZSC | INLET | _DA2313MOD8_ZSC_INLET
DA2313MOD8_ZSC_OUTLET | DA2313MOD8 | ZSC | OUTLET | _DA2313MOD8_ZSC_OUTLET
_
DA2313MOD8_ZSO_INLET | DA2313MOD8 | ZSO | INLET | _DA2313MOD8_ZSO_INLET
_
_
_
_
DA2313MOD8_ZSO_OUTLET | DA2313MOD8 | ZSO | OUTLET | _DA2313MOD8_ZSO_OUTLET
DA2313MOD9_ZSC_INLET | DA2313MOD9 | ZSC | INLET | _DA2313MOD9_ZSC_INLET
_
DA2313MOD9_ZSC_OUTLET | DA2313MOD9 | ZSC | OUTLET | _DA2313MOD9_ZSC_OUTLET
_
_
DA2313MOD9_ZSO_INLET | DA2313MOD9 | ZSO | INLET | _DA2313MOD9_ZSO_INLET
_
DA2313MOD9_ZSO_OUTLET | DA2313MOD9 | ZSO | OUTLET | _DA2313MOD9_ZSO_OUTLET
_
_
_
_
DC1313_DPT | DC1313 | DPT |  | _DC1313_DPT
DC22313_DPT | DC22313 | DPT |  | _DC22313_DPT
DC2313BH_TE_INLET | DC2313BH | TE | INLET | _DC2313BH_TE_INLET
DC2313BH_TE_OUTLET | DC2313BH | TE | OUTLET | _DC2313BH_TE_OUTLET
DC2313BK_TE_INLET | DC2313BK | TE | INLET | _DC2313BK_TE_INLET
_
_
_
_
_
_
_
_
_
_
DC2319_EXIT_TE | DC2319 | EXIT | TE | _DC2319_EXIT_TE
DC2319_PT | DC2319 | PT |  | _DC2319_PT
DG1401_SPT | DG1401 | SPT |  | _DG1401_SPT
DG1401_ZT | DG1401 | ZT |  | _DG1401_ZT
DG1420_SPT | DG1420 | SPT |  | _DG1420_SPT
DG1420_ZT | DG1420 | ZT |  | _DG1420_ZT
DG2401_SPT | DG2401 | SPT |  | _DG2401_SPT
DG2401_ZT | DG2401 | ZT |  | _DG2401_ZT
DG2420_SPT | DG2420 | SPT |  | _DG2420_SPT
DG2420_ZT | DG2420 | ZT |  | _DG2420_ZT
DG4442_ZS_JUNK | DG4442 | ZS | JUNK | _DG4442_ZS_JUNK
DG44421_ZS_BE4403 | DG44421 | ZS | BE4403 | _DG44421_ZS_BE4403
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
DG44421_ZS_DG4448 | DG44421 | ZS | DG4448 | _DG44421_ZS_DG4448
DG444210_SV | DG444210 | SV |  | _DG444210_SV
DG444210_ZS_SC4408 | DG444210 | ZS | SC4408 | _DG444210_ZS_SC4408
DG444210_ZS_SC4408A | DG444210 | ZS | SC4408A | _DG444210_ZS_SC4408A
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
DG44422_SV | DG44422 | SV |  | _DG44422_SV
_
DG44422_ZS_SC4443 | DG44422 | ZS | SC4443 | _DG44422_ZS_SC4443
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
DG44423_SV | DG44423 | SV |  | _DG44423_SV
_
_
_
DG44423_ZS_BE4406W | DG44423 | ZS | BE4406W | _DG44423_ZS_BE4406W
DG44424_SV | DG44424 | SV |  | _DG44424_SV
_
_
_
_
_
_
_
_
_
_
DG44424_ZS_BE4406E | DG44424 | ZS | BE4406E | _DG44424_ZS_BE4406E
DG44424_ZS_BE4406W | DG44424 | ZS | BE4406W | _DG44424_ZS_BE4406W
DG44425_ZS_DG44426 | DG44425 | ZS | DG44426 | _DG44425_ZS_DG44426
DG44425_ZS_SC4408 | DG44425 | ZS | SC4408 | _DG44425_ZS_SC4408
DG44426_SV | DG44426 | SV |  | _DG44426_SV
DG44426_ZS_DG44429 | DG44426 | ZS | DG44429 | _DG44426_ZS_DG44429
_
_
DG44426_ZS_SC4408C | DG44426 | ZS | SC4408C | _DG44426_ZS_SC4408C
DG44427_SV | DG44427 | SV |  | _DG44427_SV
_
DG44427_ZS_DG44428 | DG44427 | ZS | DG44428 | _DG44427_ZS_DG44428
_
_
_
DG44427_ZS_SC4408 | DG44427 | ZS | SC4408 | _DG44427_ZS_SC4408
_
_
_
_
DG44428_ZS_DG44429 | DG44428 | ZS | DG44429 | _DG44428_ZS_DG44429
DG44428_ZS_SC4408C | DG44428 | ZS | SC4408C | _DG44428_ZS_SC4408C
_
_
_
_
_
_
_
_
_
_
DG44429_SV | DG44429 | SV |  | _DG44429_SV
_
DG44429_ZS_SC4408B | DG44429 | ZS | SC4408B | _DG44429_ZS_SC4408B
_
_
_
_
_
_
_
_
_
_
_
_
_
DG44429_ZS_SILO2 | DG44429 | ZS | SILO2 | _DG44429_ZS_SILO2
DG4443_ZS_BE4406E | DG4443 | ZS | BE4406E | _DG4443_ZS_BE4406E
_
_
DG4448_ZS_BE4406E | DG4448 | ZS | BE4406E | _DG4448_ZS_BE4406E
DG4448_ZS_BE4406W | DG4448 | ZS | BE4406W | _DG4448_ZS_BE4406W
DG4449_ZS_SC4408A | DG4449 | ZS | SC4408A | _DG4449_ZS_SC4408A
DG4449_ZS_SILO5 | DG4449 | ZS | SILO5 | _DG4449_ZS_SILO5
DG4514_COIL | DG4514 | COIL |  | _DG4514_M01
DG4514_ZS_BC4514 | DG4514 | ZS | BC4514 | _DG4514_ZS_BC4514
DG4514_ZS_RC4522 | DG4514 | ZS | RC4522 | _DG4514_ZS_RC4522
DG4516_ZS_COAL | DG4516 | ZS | COAL | _DG4516_ZS_COAL
DG4516_ZS_COKE | DG4516 | ZS | COKE | _DG4516_ZS_COKE
DG516_YS_COKE | DG516 | YS | COKE | _DG516_YS_COKE
DG8330_COIL_KN1 | DG8330 | COIL | KN1 | _DG8330_M01
DG8330_COIL_KN2 | DG8330 | COIL | KN2 | _DG8330_M01
DG8330_ZS_KN1 | DG8330 | ZS | KN1 | _DG8330_ZS_KN1
_
_
_
_
_
_
_
_
_
DG8330_ZS_KN2 | DG8330 | ZS | KN2 | _DG8330_ZS_KN2
FIREDECK_ALARM | FIREDECK | ALARM |  | _FIREDECK_ALARM
FIREDP_PT | FIREDP | PT |  | _FIREDP_PT
FN1307_AUX | FN1307 | AUX |  | _FN1307_M01
FN1307A_COIL | FN1307A | COIL |  | _FN1307A_M01
FN1307A_SSA | FN1307A | SSA |  | _FN1307A_SSA
FN1312_1_FT | FN1312 | 1 | FT | _FN1312_1_FT
FN1312_2_FT | FN1312 | 2 | FT | _FN1312_2_FT
FN1312_IT | FN1312 | IT |  | _FN1312_IT
FN1314_IT | FN1314 | IT |  | _FN1314_IT
FN1314_PT_INLET | FN1314 | PT | INLET | _FN1314_PT_INLET
FN1321_AUX | FN1321 | AUX |  | _FN1321_M01
FN1321_COIL | FN1321 | COIL |  | _FN1321_M01
FN1326_AUX | FN1326 | AUX |  | _FN1326_M01
FN1326_COIL | FN1326 | COIL |  | _FN1326_M01
FN1331_AUX_DO | FN1331 | AUX | DO | _FN1331_M01
FN1335_AUX | FN1335 | AUX |  | _FN1335_M01
FN1335_COIL | FN1335 | COIL |  | _FN1335_M01
FN1341_AUX | FN1341 | AUX |  | _FN1341_M01
FN1341_COIL | FN1341 | COIL |  | _FN1341_M01
FN1605_1_COIL | FN1605 | 1 | COIL | _FN1605_1_COIL
FN1605_2_COIL | FN1605 | 2 | COIL | _FN1605_2_COIL
FN1605_ATSPD_DI | FN1605 | ATSPD | DI | _FN1605_ATSPD_DI
FN1605_AUX | FN1605 | AUX |  | _FN1605_M01
FN1605_FLT_DI | FN1605 | FLT | DI | _FN1605_FLT_DI
FN1605_HZ | FN1605 | HZ |  | _FN1605_HZ
FN1605_INLET_TE | FN1605 | INLET | TE | _FN1605_INLET_TE
FN1605_IT | FN1605 | IT |  | _FN1605_IT
SPARE | SPARE |  |  | _SPARE
SPARE | SPARE |  |  | _SPARE
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
FN1605_SPT | FN1605 | SPT |  | _FN1605_SPT
FN1605_SSA | FN1605 | SSA |  | _FN1605_SSA
FN1605_YYS | FN1605 | YYS |  | _FN1605_YYS
_
_
_
_
FN1614_AUX | FN1614 | AUX |  | _FN1614_M01
FN2210_AUX | FN2210 | AUX |  | _FN2210_M01
FN2210_COIL | FN2210 | COIL |  | _FN2210_M01
FN2210_SSA | FN2210 | SSA |  | _FN2210_SSA
_
_
_
FN2215_AUX | FN2215 | AUX |  | _FN2215_M01
FN2215_COIL | FN2215 | COIL |  | _FN2215_M01
FN2308_A_COIL | FN2308 | A | COIL | _FN2308_A_COIL
_
FN2308A_1_AUX | FN2308A | 1 | AUX | _FN2308A_1_AUX
FN2308A_2_AUX | FN2308A | 2 | AUX | _FN2308A_2_AUX
_
_
_
FN2308A_COIL | FN2308A | COIL |  | _FN2308A_M01
FN2308A_EY | FN2308A | EY |  | _FN2308A_EY
FN2308B_AUX | FN2308B | AUX |  | _FN2308B_M01
FN2308B_COIL | FN2308B | COIL |  | _FN2308B_M01
FN2308B_EY | FN2308B | EY |  | _FN2308B_EY
FN2312_COIL | FN2312 | COIL |  | _FN2312_M01
FN2312_IT | FN2312 | IT |  | _FN2312_IT
FN2312_PT | FN2312 | PT |  | _FN2312_PT
FN2314_AUX_DO | FN2314 | AUX | DO | _FN2314_M01
FN2314_IT | FN2314 | IT |  | _FN2314_IT
FN2314_PT_INLET | FN2314 | PT | INLET | _FN2314_PT_INLET
FN2314_TE | FN2314 | TE |  | _FN2314_TE
FN2314_VT_A | FN2314 | VT | A | _FN2314_VT_A
FN2314_VT_B | FN2314 | VT | B | _FN2314_VT_B
FN23141_TE | FN23141 | TE |  | _FN23141_TE
FN23143_TE | FN23143 | TE |  | _FN23143_TE
FN23144_TE | FN23144 | TE |  | _FN23144_TE
FN23145_TE | FN23145 | TE |  | _FN23145_TE
FN23146_TE | FN23146 | TE |  | _FN23146_TE
FN2314N_1_TE | FN2314N | 1 | TE | _FN2314N_1_TE
FN2314N_2_TE | FN2314N | 2 | TE | _FN2314N_2_TE
FN2314S_1_TE | FN2314S | 1 | TE | _FN2314S_1_TE
FN2314S_2_TE | FN2314S | 2 | TE | _FN2314S_2_TE
FN2321_AUX | FN2321 | AUX |  | _FN2321_M01
FN2321_COIL | FN2321 | COIL |  | _FN2321_M01
FN2326_AUX | FN2326 | AUX |  | _FN2326_M01
FN2326_COIL | FN2326 | COIL |  | _FN2326_M01
FN2605_1_COIL | FN2605 | 1 | COIL | _FN2605_1_COIL
FN2605_1_IT | FN2605 | 1 | IT | _FN2605_1_IT
FN2605_2_COIL | FN2605 | 2 | COIL | _FN2605_2_COIL
FN2605_2_IT | FN2605 | 2 | IT | _FN2605_2_IT
FN2605_ATSPD_DI | FN2605 | ATSPD | DI | _FN2605_ATSPD_DI
FN2605_AUX | FN2605 | AUX |  | _FN2605_M01
FN2605_FLT_DI | FN2605 | FLT | DI | _FN2605_FLT_DI
FN2605_SPT | FN2605 | SPT |  | _FN2605_SPT
FN2605_SSA | FN2605 | SSA |  | _FN2605_SSA
FN2605_ST | FN2605 | ST |  | _FN2605_ST
FN2605_TE | FN2605 | TE |  | _FN2605_TE
FN2605_UY | FN2605 | UY |  | _FN2605_UY
FN2605_YYS | FN2605 | YYS |  | _FN2605_YYS
FN44141_AUX | FN44141 | AUX |  | _FN44141_M01
FN44141_COIL | FN44141 | COIL |  | _FN44141_M01
FN44141_EY | FN44141 | EY |  | _FN44141_EY
FN44141_YYS | FN44141 | YYS |  | _FN44141_YYS
FN44195_AUX | FN44195 | AUX |  | _FN44195_M01
FN4430_AUX | FN4430 | AUX |  | _FN4430_M01
FN4430_COIL | FN4430 | COIL |  | _FN4430_M01
FN4437_AUX | FN4437 | AUX |  | _FN4437_M01
FN4437A_AUX | FN4437A | AUX |  | _FN4437A_M01
FN4437B_COIL | FN4437B | COIL |  | _FN4437B_M01
FN4437C_AUX | FN4437C | AUX |  | _FN4437C_M01
FN4437D_AUX | FN4437D | AUX |  | _FN4437D_M01
FN4437E_AUX | FN4437E | AUX |  | _FN4437E_M01
FN4437F_AUX | FN4437F | AUX |  | _FN4437F_M01
FN4452_AUX | FN4452 | AUX |  | _FN4452_M01
FN4452_COIL | FN4452 | COIL |  | _FN4452_M01
FN4460_IT | FN4460 | IT |  | _FN4460_IT
FN4460_PT_DISCHARGE | FN4460 | PT | DISCHARGE | _FN4460_PT_DISCHARGE
FN4527_AUX | FN4527 | AUX |  | _FN4527_M01
FN4527_COIL | FN4527 | COIL |  | _FN4527_M01
FN47621_AUX | FN47621 | AUX |  | _FN47621_M01
FN47621_COIL | FN47621 | COIL |  | _FN47621_M01
FN8213_AUX | FN8213 | AUX |  | _FN8213_M01
FN8213_COIL | FN8213 | COIL |  | _FN8213_M01
FN8213_SSA | FN8213 | SSA |  | _FN8213_SSA
FV1312_ZT | FV1312 | ZT |  | _FV1312_ZT
FV1340_ZT | FV1340 | ZT |  | _FV1340_ZT
FV1607A_ZT | FV1607A | ZT |  | _FV1607A_ZT
FV1607B_XY_A | FV1607B | XY | A | _FV1607B_XY_A
FV1607B_XY_B | FV1607B | XY | B | _FV1607B_XY_B
FV1607B_ZT | FV1607B | ZT |  | _FV1607B_ZT
FV2211_XY_A | FV2211 | XY | A | _FV2211_XY_A
FV2211_XY_B | FV2211 | XY | B | _FV2211_XY_B
FV2211_ZT | FV2211 | ZT |  | _FV2211_ZT
FV2215_XY_A | FV2215 | XY | A | _FV2215_XY_A
FV2215_XY_B | FV2215 | XY | B | _FV2215_XY_B
FV2215_ZT | FV2215 | ZT |  | _FV2215_ZT
FV2216_ZT | FV2216 | ZT |  | _FV2216_ZT
FV2220_XY_A | FV2220 | XY | A | _FV2220_XY_A
FV2220_XY_B | FV2220 | XY | B | _FV2220_XY_B
FV2220_ZT | FV2220 | ZT |  | _FV2220_ZT
FV2228_ZT | FV2228 | ZT |  | _FV2228_ZT
FV2272_TE | FV2272 | TE |  | _FV2272_TE
FV2272_XY_A | FV2272 | XY | A | _FV2272_XY_A
FV2272_XY_B | FV2272 | XY | B | _FV2272_XY_B
FV2272_ZT | FV2272 | ZT |  | _FV2272_ZT
FV2273_XY_A | FV2273 | XY | A | _FV2273_XY_A
FV2273_XY_B | FV2273 | XY | B | _FV2273_XY_B
FV2273_ZT | FV2273 | ZT |  | _FV2273_ZT
FV2308E_TE | FV2308E | TE |  | _FV2308E_TE
FV2308N_TE | FV2308N | TE |  | _FV2308N_TE
FV2308S_TE | FV2308S | TE |  | _FV2308S_TE
FV2308W_TE | FV2308W | TE |  | _FV2308W_TE
FV2310E_XY_A | FV2310E | XY | A | _FV2310E_XY_A
FV2310E_XY_B | FV2310E | XY | B | _FV2310E_XY_B
FV2310E_ZT | FV2310E | ZT |  | _FV2310E_ZT
FV2310N_XY_A | FV2310N | XY | A | _FV2310N_XY_A
FV2310N_XY_B | FV2310N | XY | B | _FV2310N_XY_B
FV2310N_ZT | FV2310N | ZT |  | _FV2310N_ZT
FV2310S_XY_A | FV2310S | XY | A | _FV2310S_XY_A
FV2310S_XY_B | FV2310S | XY | B | _FV2310S_XY_B
FV2310S_ZT | FV2310S | ZT |  | _FV2310S_ZT
FV2310W_XY_A | FV2310W | XY | A | _FV2310W_XY_A
FV2310W_XY_B | FV2310W | XY | B | _FV2310W_XY_B
FV2310W_ZT | FV2310W | ZT |  | _FV2310W_ZT
SPARE | SPARE |  |  | _SPARE
FV2313_ZT | FV2313 | ZT |  | _FV2313_ZT
FV2319_ZT | FV2319 | ZT |  | _FV2319_ZT
_
_
_
_
HM44022_COIL | HM44022 | COIL |  | _HM44022_M01
HM44022_MS | HM44022 | MS |  | _HM44022_MS
HM44051_1_AUX | HM44051 | 1 | AUX | _HM44051_1_AUX
HM44051_1_COIL | HM44051 | 1 | COIL | _HM44051_1_COIL
HM44051_2_AUX | HM44051 | 2 | AUX | _HM44051_2_AUX
HM44051_2_COIL | HM44051 | 2 | COIL | _HM44051_2_COIL
HM44051_EY | HM44051 | EY |  | _HM44051_EY
HM44051_HS | HM44051 | HS |  | _HM44051_HS
HM44051_IT | HM44051 | IT |  | _HM44051_IT
_
_
_
HM44051_SSA | HM44051 | SSA |  | _HM44051_SSA
HM44051REV_HS | HM44051REV | HS |  | _HM44051REV_HS
HM4422_AUX | HM4422 | AUX |  | _HM4422_M01
HM4422_COIL | HM4422 | COIL |  | _HM4422_M01
HM4422_IT | HM4422 | IT |  | _HM4422_IT
HM4422_SSA | HM4422 | SSA |  | _HM4422_SSA
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
HM4422_YS | HM4422 | YS |  | _HM4422_YS
HP260212_PSH | HP260212 | PSH |  | _HP260212_PSH
IV1211_ZVC | IV1211 | ZVC |  | _IV1211_ZVC
IV1211_ZVO | IV1211 | ZVO |  | _IV1211_ZVO
IV1215_ZVC | IV1215 | ZVC |  | _IV1215_ZVC
_
_
_
IV1215_ZVO | IV1215 | ZVO |  | _IV1215_ZVO
IV1607_ZVO | IV1607 | ZVO |  | _IV1607_ZVO
IV211_ZSC | IV211 | ZSC |  | _IV211_ZSC
IV211_ZSO | IV211 | ZSO |  | _IV211_ZSO
IV2211_15_XY | IV2211 | 15 | XY | _IV2211_15_XY
IV2215_ZSC | IV2215 | ZSC |  | _IV2215_ZSC
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
IV2215_ZSO | IV2215 | ZSO |  | _IV2215_ZSO
K1AIRCANNON_SV | K1AIRCANNON | SV |  | _K1AIRCANNON_SV
_
_
_
_
_
_
K1FZ01_TE | K1FZ01 | TE |  | _K1FZ01_TE
K202_PV | K202 | PV |  | _K202_PV
K22300_PIT | K22300 | PIT |  | _K22300_PIT
K2AIRCANNON_SV | K2AIRCANNON | SV |  | _K2AIRCANNON_SV
K2FZ01_TE | K2FZ01 | TE |  | _K2FZ01_TE
KD1308_1_ALM | KD1308 | 1 | ALM | _KD1308_1_ALM
_
_
_
_
_
_
_
_
_
_
KD1308_2_ALM | KD1308 | 2 | ALM | _KD1308_2_ALM
KD1308_LT | KD1308 | LT |  | _KD1308_LT
KD1308_LUBE_SV | KD1308 | LUBE | SV | _KD1308_LUBE_SV
KD2308_LT | KD2308 | LT |  | _KD2308_LT
_
_
_
_
KD2308_LUBE_SV | KD2308 | LUBE | SV | _KD2308_LUBE_SV
KD2308_SPT | KD2308 | SPT |  | _KD2308_SPT
KD2308A_RES_DI | KD2308A | RES | DI | _KD2308A_RES_DI
KD2308B_RES_DI | KD2308B | RES | DI | _KD2308B_RES_DI
KD308K1K2_YAY | KD308K1K2 | YAY |  | _KD308K1K2_YAY
KL1301NE_TE | KL1301NE | TE |  | _KL1301NE_TE
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
KL1301NW_TE | KL1301NW | TE |  | _KL1301NW_TE
KL1301SE_TE | KL1301SE | TE |  | _KL1301SE_TE
KL1301SW_TE | KL1301SW | TE |  | _KL1301SW_TE
KL1302NE_TE | KL1302NE | TE |  | _KL1302NE_TE
KL1302NW_TE | KL1302NW | TE |  | _KL1302NW_TE
KL1302SE_TE | KL1302SE | TE |  | _KL1302SE_TE
KL1302SW_TE | KL1302SW | TE |  | _KL1302SW_TE
KL13EXIT_TE | KL13EXIT | TE |  | _KL13EXIT_TE
KL1FN_AUX | KL1FN | AUX |  | _KL1FN_M01
KL1O2_FS | KL1O2 | FS |  | _KL1O2_FS
KL2301NE_TE | KL2301NE | TE |  | _KL2301NE_TE
KL2301NW_TE | KL2301NW | TE |  | _KL2301NW_TE
KL2301SE_TE | KL2301SE | TE |  | _KL2301SE_TE
KL2301SW_TE | KL2301SW | TE |  | _KL2301SW_TE
KL2302NE_TE | KL2302NE | TE |  | _KL2302NE_TE
_
KL2302NW_TE | KL2302NW | TE |  | _KL2302NW_TE
KL2302SE_TE | KL2302SE | TE |  | _KL2302SE_TE
KL2302SW_TE | KL2302SW | TE |  | _KL2302SW_TE
KL2KD_YZ | KL2KD | YZ |  | _KL2KD_YZ
KL2OS_FS | KL2OS | FS |  | _KL2OS_FS
KL2PH01_INLET_ET | KL2PH01 | INLET | ET | _KL2PH01_INLET_ET
KL2PH01_OUTLET_TE | KL2PH01 | OUTLET | TE | _KL2PH01_OUTLET_TE
_
KN1_CAN_PAL | KN1 | CAN | PAL | _KN1_CAN_PAL
KN1_CAN_TCM_SV | KN1 | CAN | TCM | _KN1_CAN_TCM_SV
KN1_CAN_TCN_SV | KN1 | CAN | TCN | _KN1_CAN_TCN_SV
KN1_CAN_TCS_SV | KN1 | CAN | TCS | _KN1_CAN_TCS_SV
KN1_CAN1_SV | KN1 | CAN1 | SV | _KN1_CAN1_SV
_
_
_
KN1_CAN10_SV | KN1 | CAN10 | SV | _KN1_CAN10_SV
KN1_CAN14_SV | KN1 | CAN14 | SV | _KN1_CAN14_SV
KN1_CAN15_SV | KN1 | CAN15 | SV | _KN1_CAN15_SV
KN1_CAN2_SV | KN1 | CAN2 | SV | _KN1_CAN2_SV
KN1_CAN3_SV | KN1 | CAN3 | SV | _KN1_CAN3_SV
KN1_CAN4_SV | KN1 | CAN4 | SV | _KN1_CAN4_SV
KN1_CAN5_SV | KN1 | CAN5 | SV | _KN1_CAN5_SV
KN1_CAN6_SV | KN1 | CAN6 | SV | _KN1_CAN6_SV
KN1_CAN7_SV | KN1 | CAN7 | SV | _KN1_CAN7_SV
KN1_CAN8_SV | KN1 | CAN8 | SV | _KN1_CAN8_SV
KN1_CAN9_SV | KN1 | CAN9 | SV | _KN1_CAN9_SV
KN1_DS_SV | KN1 | DS | SV | _KN1_DS_SV
KN1_SA_TE | KN1 | SA | TE | _KN1_SA_TE
KN1BM_DPT | KN1BM | DPT |  | _KN1BM_DPT
KN1BP_PT | KN1BP | PT |  | _KN1BP_PT
KN1HD_PT | KN1HD | PT |  | _KN1HD_PT
KN2_CAN1_SV | KN2 | CAN1 | SV | _KN2_CAN1_SV
KN2_CAN10_SV | KN2 | CAN10 | SV | _KN2_CAN10_SV
_
KN2_CAN11_SV | KN2 | CAN11 | SV | _KN2_CAN11_SV
KN2_CAN12_SV | KN2 | CAN12 | SV | _KN2_CAN12_SV
KN2_CAN13_SV | KN2 | CAN13 | SV | _KN2_CAN13_SV
KN2_CAN14_SV | KN2 | CAN14 | SV | _KN2_CAN14_SV
KN2_CAN2_SV | KN2 | CAN2 | SV | _KN2_CAN2_SV
_
KN2_CAN3_SV | KN2 | CAN3 | SV | _KN2_CAN3_SV
KN2_CAN4_SV | KN2 | CAN4 | SV | _KN2_CAN4_SV
KN2_CAN5_SV | KN2 | CAN5 | SV | _KN2_CAN5_SV
KN2_CAN6_SV | KN2 | CAN6 | SV | _KN2_CAN6_SV
KN2_CAN7_SV | KN2 | CAN7 | SV | _KN2_CAN7_SV
KN2_CAN8_SV | KN2 | CAN8 | SV | _KN2_CAN8_SV
KN2_CAN9_SV | KN2 | CAN9 | SV | _KN2_CAN9_SV
KN2_DS_SV | KN2 | DS | SV | _KN2_DS_SV
KN2_EXIT_TE | KN2 | EXIT | TE | _KN2_EXIT_TE
_
_
_
KN2_PT_FEEDEND | KN2 | PT | FEEDEND | _KN2_PT_FEEDEND
KN2261_1_PT | KN2261 | 1 | PT | _KN2261_1_PT
KN2261_2_PT | KN2261 | 2 | PT | _KN2261_2_PT
_
_
_
_
_
KN2313MOD1_SEQ_ADVANCE | KN2313MOD1 | SEQ | ADVANCE | _KN2313MOD1_SEQ_ADVANCE
KN2313MOD1_SEQ | KN2313MOD1 | SEQ |  | _KN2313MOD1_SEQ
KN2313MOD10_SEQ_ADVANCE | KN2313MOD10 | SEQ | ADVANCE | _KN2313MOD10_SEQ_ADVANCE
_
_
_
_
_
_
_
_
KN2313MOD10_SEQ | KN2313MOD10 | SEQ |  | _KN2313MOD10_SEQ
KN2313MOD2_SEQ_ADVANCE | KN2313MOD2 | SEQ | ADVANCE | _KN2313MOD2_SEQ_ADVANCE
KN2313MOD2_SEQ | KN2313MOD2 | SEQ |  | _KN2313MOD2_SEQ
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
KN2313MOD3_SEQ_ADVANCE | KN2313MOD3 | SEQ | ADVANCE | _KN2313MOD3_SEQ_ADVANCE
KN2313MOD3_SEQ | KN2313MOD3 | SEQ |  | _KN2313MOD3_SEQ
KN2313MOD4_SEQ_ADVANCE | KN2313MOD4 | SEQ | ADVANCE | _KN2313MOD4_SEQ_ADVANCE
KN2313MOD4_SEQ | KN2313MOD4 | SEQ |  | _KN2313MOD4_SEQ
KN2313MOD5_SEQ_ADVANCE | KN2313MOD5 | SEQ | ADVANCE | _KN2313MOD5_SEQ_ADVANCE
KN2313MOD5_SEQ | KN2313MOD5 | SEQ |  | _KN2313MOD5_SEQ
KN2313MOD6_SEQ_ADVANCE | KN2313MOD6 | SEQ | ADVANCE | _KN2313MOD6_SEQ_ADVANCE
KN2313MOD6_SEQ | KN2313MOD6 | SEQ |  | _KN2313MOD6_SEQ
KN2313MOD7_SEQ_ADVANCE | KN2313MOD7 | SEQ | ADVANCE | _KN2313MOD7_SEQ_ADVANCE
KN2313MOD7_SEQ | KN2313MOD7 | SEQ |  | _KN2313MOD7_SEQ
KN2313MOD8_SEQ_ADVANCE | KN2313MOD8 | SEQ | ADVANCE | _KN2313MOD8_SEQ_ADVANCE
KN2313MOD8_SEQ | KN2313MOD8 | SEQ |  | _KN2313MOD8_SEQ
KN2313MOD9_SEQ_ADVANCE | KN2313MOD9 | SEQ | ADVANCE | _KN2313MOD9_SEQ_ADVANCE
KN2313MOD9_SEQ | KN2313MOD9 | SEQ |  | _KN2313MOD9_SEQ
KN2COALBIN_LAL | KN2COALBIN | LAL |  | _KN2COALBIN_LAL
KN2KD_ALM | KN2KD | ALM |  | _KN2KD_ALM
KN2PNY_SLOCK_DI | KN2PNY | SLOCK | DI | _KN2PNY_SLOCK_DI
LKD_1_SYSTEM | LKD | 1 | SYSTEM | _LKD_1_SYSTEM
LKD_2_SYSTEM | LKD | 2 | SYSTEM | _LKD_2_SYSTEM
MCR1_ALM | MCR1 | ALM |  | _MCR1_ALM
MCR1_UPS_DI | MCR1 | UPS | DI | _MCR1_UPS_DI
MCR2_ALM | MCR2 | ALM |  | _MCR2_ALM
MCR3_ALM | MCR3 | ALM |  | _MCR3_ALM
MCR4_ALM | MCR4 | ALM |  | _MCR4_ALM
MCR5_ALM | MCR5 | ALM |  | _MCR5_ALM
MCR6_ALM | MCR6 | ALM |  | _MCR6_ALM
MD231301_KS | MD231301 | KS |  | _MD231301_KS
MD231301_SV | MD231301 | SV |  | _MD231301_SV
MD231302_KS | MD231302 | KS |  | _MD231302_KS
MD231302_SV | MD231302 | SV |  | _MD231302_SV
MD231303_KS | MD231303 | KS |  | _MD231303_KS
_
MD231303_SV | MD231303 | SV |  | _MD231303_SV
MD231304_KS | MD231304 | KS |  | _MD231304_KS
MD231304_SV | MD231304 | SV |  | _MD231304_SV
MD231305_KS | MD231305 | KS |  | _MD231305_KS
MD231305_SV | MD231305 | SV |  | _MD231305_SV
MD231306_KS | MD231306 | KS |  | _MD231306_KS
MD231306_SV | MD231306 | SV |  | _MD231306_SV
MD231307_KS | MD231307 | KS |  | _MD231307_KS
MD231307_SV | MD231307 | SV |  | _MD231307_SV
MD231308_KS | MD231308 | KS |  | _MD231308_KS
MD231308_SV | MD231308 | SV |  | _MD231308_SV
MD231309_KS | MD231309 | KS |  | _MD231309_KS
MD231309_SV | MD231309 | SV |  | _MD231309_SV
MD231310_KS | MD231310 | KS |  | _MD231310_KS
MD231310_SV | MD231310 | SV |  | _MD231310_SV
_
O2AN_BLD_SV | O2AN | BLD | SV | _O2AN_BLD_SV
O2AN_FRO_SV | O2AN | FRO | SV | _O2AN_FRO_SV
O2AN_PGE_SV | O2AN | PGE | SV | _O2AN_PGE_SV
OHV1310_LT | OHV1310 | LT |  | _OHV1310_LT
OV1310_LT | OV1310 | LT |  | _OV1310_LT
OV2310_LT | OV2310 | LT |  | _OV2310_LT
PC4420_AUX | PC4420 | AUX |  | _PC4420_M01
PC4420_COIL | PC4420 | COIL |  | _PC4420_M01
PC4420_MS | PC4420 | MS |  | _PC4420_MS
PC4421_AUX | PC4421 | AUX |  | _PC4421_M01
PC4421_COIL | PC4421 | COIL |  | _PC4421_M01
PC4421_MS | PC4421 | MS |  | _PC4421_MS
_
_
_
_
PC4460_COIL | PC4460 | COIL |  | _PC4460_M01
PH1_PT_OUTLET | PH1 | PT | OUTLET | _PH1_PT_OUTLET
PH1306_IN_TE | PH1306 | IN | TE | _PH1306_IN_TE
PH1306_OUT_TE | PH1306 | OUT | TE | _PH1306_OUT_TE
PH2_FILTER_PH | PH2 | FILTER | PH | _PH2_FILTER_PH
PH2_HYD_LL | PH2 | HYD | LL | _PH2_HYD_LL
PH2_HYD_LLL | PH2 | HYD | LLL | _PH2_HYD_LLL
PH2_HYD_NDUMP_SV | PH2 | HYD | NDUMP | _PH2_HYD_NDUMP_SV
PH2_HYD_OIL_TL | PH2 | HYD | OIL | _PH2_HYD_OIL_TL
_
_
_
PH2_HYD_SDUMP_SV | PH2 | HYD | SDUMP | _PH2_HYD_SDUMP_SV
_
_
_
PH2_PT_OUTLET | PH2 | PT | OUTLET | _PH2_PT_OUTLET
_
PH2305_1_ZSO | PH2305 | 1 | ZSO | _PH2305_1_ZSO
PH2305_2_ZSO | PH2305 | 2 | ZSO | _PH2305_2_ZSO
PH2RAM1_LS_A | PH2RAM1 | LS | A | _PH2RAM1_LS_A
PH2RAM1_LS_B | PH2RAM1 | LS | B | _PH2RAM1_LS_B
PH2RAM1_SS | PH2RAM1 | SS |  | _PH2RAM1_SS
PH2RAM1_SV | PH2RAM1 | SV |  | _PH2RAM1_SV
PH2RAM1_TE | PH2RAM1 | TE |  | _PH2RAM1_TE
_
_
_
_
_
_
_
PH2RAM10_LS_A | PH2RAM10 | LS | A | _PH2RAM10_LS_A
_
PH2RAM10_LS_B | PH2RAM10 | LS | B | _PH2RAM10_LS_B
PH2RAM10_SS | PH2RAM10 | SS |  | _PH2RAM10_SS
PH2RAM10_SV | PH2RAM10 | SV |  | _PH2RAM10_SV
PH2RAM11_LS_A | PH2RAM11 | LS | A | _PH2RAM11_LS_A
PH2RAM11_LS_B | PH2RAM11 | LS | B | _PH2RAM11_LS_B
PH2RAM11_SS | PH2RAM11 | SS |  | _PH2RAM11_SS
PH2RAM11_SV | PH2RAM11 | SV |  | _PH2RAM11_SV
_
PH2RAM11_TE | PH2RAM11 | TE |  | _PH2RAM11_TE
_
PH2RAM12_LS_A | PH2RAM12 | LS | A | _PH2RAM12_LS_A
PH2RAM12_LS_B | PH2RAM12 | LS | B | _PH2RAM12_LS_B
PH2RAM12_SS | PH2RAM12 | SS |  | _PH2RAM12_SS
PH2RAM12_SV | PH2RAM12 | SV |  | _PH2RAM12_SV
PH2RAM13_LS_A | PH2RAM13 | LS | A | _PH2RAM13_LS_A
_
PH2RAM13_LS_B | PH2RAM13 | LS | B | _PH2RAM13_LS_B
_
PH2RAM13_SS | PH2RAM13 | SS |  | _PH2RAM13_SS
PH2RAM13_SV | PH2RAM13 | SV |  | _PH2RAM13_SV
PH2RAM13_TE | PH2RAM13 | TE |  | _PH2RAM13_TE
PH2RAM14_LS_A | PH2RAM14 | LS | A | _PH2RAM14_LS_A
PH2RAM14_LS_B | PH2RAM14 | LS | B | _PH2RAM14_LS_B
PH2RAM14_SS | PH2RAM14 | SS |  | _PH2RAM14_SS
PH2RAM14_SV | PH2RAM14 | SV |  | _PH2RAM14_SV
PH2RAM15_LS_A | PH2RAM15 | LS | A | _PH2RAM15_LS_A
PH2RAM15_LS_B | PH2RAM15 | LS | B | _PH2RAM15_LS_B
PH2RAM15_SS | PH2RAM15 | SS |  | _PH2RAM15_SS
PH2RAM15_SV | PH2RAM15 | SV |  | _PH2RAM15_SV
PH2RAM15_TE | PH2RAM15 | TE |  | _PH2RAM15_TE
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
PH2RAM16_LS_A | PH2RAM16 | LS | A | _PH2RAM16_LS_A
PH2RAM16_LS_B | PH2RAM16 | LS | B | _PH2RAM16_LS_B
PH2RAM16_SS | PH2RAM16 | SS |  | _PH2RAM16_SS
PH2RAM16_SV | PH2RAM16 | SV |  | _PH2RAM16_SV
_
_
_
_
PH2RAM17_LS_A | PH2RAM17 | LS | A | _PH2RAM17_LS_A
PH2RAM17_LS_B | PH2RAM17 | LS | B | _PH2RAM17_LS_B
PH2RAM17_SS | PH2RAM17 | SS |  | _PH2RAM17_SS
PH2RAM17_SV | PH2RAM17 | SV |  | _PH2RAM17_SV
_
_
_
_
PH2RAM17_TE | PH2RAM17 | TE |  | _PH2RAM17_TE
PH2RAM18_LS_A | PH2RAM18 | LS | A | _PH2RAM18_LS_A
PH2RAM18_LS_B | PH2RAM18 | LS | B | _PH2RAM18_LS_B
PH2RAM18_SS | PH2RAM18 | SS |  | _PH2RAM18_SS
PH2RAM18_SV | PH2RAM18 | SV |  | _PH2RAM18_SV
PH2RAM2_LS_A | PH2RAM2 | LS | A | _PH2RAM2_LS_A
PH2RAM2_LS_B | PH2RAM2 | LS | B | _PH2RAM2_LS_B
PH2RAM2_SS | PH2RAM2 | SS |  | _PH2RAM2_SS
PH2RAM2_SV | PH2RAM2 | SV |  | _PH2RAM2_SV
PH2RAM3_LS_A | PH2RAM3 | LS | A | _PH2RAM3_LS_A
PH2RAM3_LS_B | PH2RAM3 | LS | B | _PH2RAM3_LS_B
PH2RAM3_SS | PH2RAM3 | SS |  | _PH2RAM3_SS
PH2RAM3_SV | PH2RAM3 | SV |  | _PH2RAM3_SV
PH2RAM3_TE | PH2RAM3 | TE |  | _PH2RAM3_TE
PH2RAM4_LS_A | PH2RAM4 | LS | A | _PH2RAM4_LS_A
PH2RAM4_LS_B | PH2RAM4 | LS | B | _PH2RAM4_LS_B
PH2RAM4_SS | PH2RAM4 | SS |  | _PH2RAM4_SS
PH2RAM4_SV | PH2RAM4 | SV |  | _PH2RAM4_SV
PH2RAM5_LS_A | PH2RAM5 | LS | A | _PH2RAM5_LS_A
_
PH2RAM5_LS_B | PH2RAM5 | LS | B | _PH2RAM5_LS_B
PH2RAM5_SS | PH2RAM5 | SS |  | _PH2RAM5_SS
PH2RAM5_SV | PH2RAM5 | SV |  | _PH2RAM5_SV
PH2RAM5_TE | PH2RAM5 | TE |  | _PH2RAM5_TE
PH2RAM6_LS_A | PH2RAM6 | LS | A | _PH2RAM6_LS_A
PH2RAM6_LS_B | PH2RAM6 | LS | B | _PH2RAM6_LS_B
PH2RAM6_SS | PH2RAM6 | SS |  | _PH2RAM6_SS
_
_
PH2RAM6_SV | PH2RAM6 | SV |  | _PH2RAM6_SV
PH2RAM7_LS_A | PH2RAM7 | LS | A | _PH2RAM7_LS_A
_
PH2RAM7_LS_B | PH2RAM7 | LS | B | _PH2RAM7_LS_B
PH2RAM7_SS | PH2RAM7 | SS |  | _PH2RAM7_SS
PH2RAM7_SV | PH2RAM7 | SV |  | _PH2RAM7_SV
PH2RAM7_TE | PH2RAM7 | TE |  | _PH2RAM7_TE
PH2RAM8_LS_A | PH2RAM8 | LS | A | _PH2RAM8_LS_A
PH2RAM8_LS_B | PH2RAM8 | LS | B | _PH2RAM8_LS_B
PH2RAM8_SS | PH2RAM8 | SS |  | _PH2RAM8_SS
PH2RAM8_SV | PH2RAM8 | SV |  | _PH2RAM8_SV
PH2RAM9_LS_A | PH2RAM9 | LS | A | _PH2RAM9_LS_A
PH2RAM9_LS_B | PH2RAM9 | LS | B | _PH2RAM9_LS_B
PH2RAM9_SS | PH2RAM9 | SS |  | _PH2RAM9_SS
PH2RAM9_SV | PH2RAM9 | SV |  | _PH2RAM9_SV
PH2RAM9_TE | PH2RAM9 | TE |  | _PH2RAM9_TE
PL00_AT | PL00 | AT |  | _PL00_AT
PL00_PAL | PL00 | PAL |  | _PL00_PAL
PL00_YAY_A | PL00 | YAY | A | _PL00_YAY_A
_
PM13051_AUX | PM13051 | AUX |  | _PM13051_M01
PM13051_COIL | PM13051 | COIL |  | _PM13051_M01
PM13052_AUX | PM13052 | AUX |  | _PM13052_M01
PM13052_COIL | PM13052 | COIL |  | _PM13052_M01
PM1602A1_AUX | PM1602A1 | AUX |  | _PM1602A1_M01
PM1602A1_COIL | PM1602A1 | COIL |  | _PM1602A1_M01
PM1602A2_AUX | PM1602A2 | AUX |  | _PM1602A2_M01
_
PM1602A2_COIL | PM1602A2 | COIL |  | _PM1602A2_M01
PM23051_AUX | PM23051 | AUX |  | _PM23051_M01
PM23051_COIL | PM23051 | COIL |  | _PM23051_M01
PM23051_PT | PM23051 | PT |  | _PM23051_PT
PM23051_SS | PM23051 | SS |  | _PM23051_SS
PM23052_AUX | PM23052 | AUX |  | _PM23052_M01
PM23052_COIL | PM23052 | COIL |  | _PM23052_M01
PM23052_PT | PM23052 | PT |  | _PM23052_PT
PM23052_SS | PM23052 | SS |  | _PM23052_SS
PM2602_1_COIL | PM2602 | 1 | COIL | _PM2602_1_COIL
PM2602_2_COIL | PM2602 | 2 | COIL | _PM2602_2_COIL
PM26021_AUX | PM26021 | AUX |  | _PM26021_M01
PM26022_AUX | PM26022 | AUX |  | _PM26022_M01
PM4461_AUX | PM4461 | AUX |  | _PM4461_M01
PM4461_COIL | PM4461 | COIL |  | _PM4461_M01
PM4461_IT | PM4461 | IT |  | _PM4461_IT
PM46101_AUX | PM46101 | AUX |  | _PM46101_M01
PM46101_COIL | PM46101 | COIL |  | _PM46101_M01
PM46102_AUX | PM46102 | AUX |  | _PM46102_M01
PM46102_COIL | PM46102 | COIL |  | _PM46102_M01
PM4610KL1_FT | PM4610KL1 | FT |  | _PM4610KL1_FT
PM4610KL2_1_FT | PM4610KL2 | 1 | FT | _PM4610KL2_1_FT
PM4610KL2_2_FT | PM4610KL2 | 2 | FT | _PM4610KL2_2_FT
PNY_SLOCK_DI | PNY | SLOCK | DI | _PNY_SLOCK_DI
PS_UY | PS | UY |  | _PS_UY
PU326_LSL | PU326 | LSL |  | _PU326_LSL
RA1319_AUX | RA1319 | AUX |  | _RA1319_M01
RA1604_COIL | RA1604 | COIL |  | _RA1604_M01
RA1614_AUX | RA1614 | AUX |  | _RA1614_M01
RA23131_AUX | RA23131 | AUX |  | _RA23131_M01
RA23131_COIL | RA23131 | COIL |  | _RA23131_M01
RA23131_HS | RA23131 | HS |  | _RA23131_HS
RA23131_MS | RA23131 | MS |  | _RA23131_MS
RA231310_AUX | RA231310 | AUX |  | _RA231310_M01
RA231310_COIL | RA231310 | COIL |  | _RA231310_M01
RA231310_HS | RA231310 | HS |  | _RA231310_HS
RA231310_MS | RA231310 | MS |  | _RA231310_MS
RA23132_AUX | RA23132 | AUX |  | _RA23132_M01
RA23132_COIL | RA23132 | COIL |  | _RA23132_M01
RA23132_HS | RA23132 | HS |  | _RA23132_HS
RA23132_MS | RA23132 | MS |  | _RA23132_MS
RA23133_AUX | RA23133 | AUX |  | _RA23133_M01
RA23133_COIL | RA23133 | COIL |  | _RA23133_M01
RA23133_HS | RA23133 | HS |  | _RA23133_HS
RA23133_MS | RA23133 | MS |  | _RA23133_MS
RA23134_AUX | RA23134 | AUX |  | _RA23134_M01
RA23134_COIL | RA23134 | COIL |  | _RA23134_M01
RA23134_HS | RA23134 | HS |  | _RA23134_HS
RA23134_MS | RA23134 | MS |  | _RA23134_MS
RA23135_AUX | RA23135 | AUX |  | _RA23135_M01
_
RA23135_COIL | RA23135 | COIL |  | _RA23135_M01
RA23135_HS | RA23135 | HS |  | _RA23135_HS
RA23135_MS | RA23135 | MS |  | _RA23135_MS
_
RA23136_AUX | RA23136 | AUX |  | _RA23136_M01
_
_
RA23136_COIL | RA23136 | COIL |  | _RA23136_M01
RA23136_HS | RA23136 | HS |  | _RA23136_HS
_
_
RA23136_MS | RA23136 | MS |  | _RA23136_MS
RA23137_AUX | RA23137 | AUX |  | _RA23137_M01
_
_
RA23137_COIL | RA23137 | COIL |  | _RA23137_M01
_
_
_
_
RA23137_HS | RA23137 | HS |  | _RA23137_HS
RA23137_MS | RA23137 | MS |  | _RA23137_MS
_
_
RA23138_AUX | RA23138 | AUX |  | _RA23138_M01
RA23138_COIL | RA23138 | COIL |  | _RA23138_M01
_
RA23138_HS | RA23138 | HS |  | _RA23138_HS
_
_
RA23138_MS | RA23138 | MS |  | _RA23138_MS
RA23139_AUX | RA23139 | AUX |  | _RA23139_M01
_
_
RA23139_COIL | RA23139 | COIL |  | _RA23139_M01
_
_
_
_
_
_
_
_
RA23139_HS | RA23139 | HS |  | _RA23139_HS
_
_
_
RA23139_MS | RA23139 | MS |  | _RA23139_MS
_
_
RA2319_AUX | RA2319 | AUX |  | _RA2319_M01
_
RA2319_COIL | RA2319 | COIL |  | _RA2319_M01
_
_
RA2606_AUX | RA2606 | AUX |  | _RA2606_M01
_
_
_
RA2606_COIL | RA2606 | COIL |  | _RA2606_M01
_
_
_
RA2612_1_AUX | RA2612 | 1 | AUX | _RA2612_1_AUX
RA2612_2_COIL | RA2612 | 2 | COIL | _RA2612_2_COIL
_
_
RA2612_AUX | RA2612 | AUX |  | _RA2612_M01
_
_
_
RA44144_AUX | RA44144 | AUX |  | _RA44144_M01
RA44144_COIL | RA44144 | COIL |  | _RA44144_M01
_
_
RA44144_EY | RA44144 | EY |  | _RA44144_EY
RA44144_MS | RA44144 | MS |  | _RA44144_MS
_
_
_
RA44144_YYS | RA44144 | YYS |  | _RA44144_YYS
_
_
RA4437B_AUX | RA4437B | AUX |  | _RA4437B_M01
_
_
_
_
_
_
_
_
RA4527_AUX | RA4527 | AUX |  | _RA4527_M01
_
_
RA47621_AUX | RA47621 | AUX |  | _RA47621_M01
RA47621_COIL | RA47621 | COIL |  | _RA47621_M01
_
_
_
_
_
_
_
_
_
_
RC44441_1_AUX | RC44441 | 1 | AUX | _RC44441_1_AUX
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
RC44441_2_AUX | RC44441 | 2 | AUX | _RC44441_2_AUX
RC44441_COIL | RC44441 | COIL |  | _RC44441_M01
RC44441_EY | RC44441 | EY |  | _RC44441_EY
RC44441_IT | RC44441 | IT |  | _RC44441_IT
_
RC44441_YYS | RC44441 | YYS |  | _RC44441_YYS
RC44442_1_AUX | RC44442 | 1 | AUX | _RC44442_1_AUX
_
RC44442_2_AUX | RC44442 | 2 | AUX | _RC44442_2_AUX
_
RC44442_COIL | RC44442 | COIL |  | _RC44442_M01
RC44442_EY | RC44442 | EY |  | _RC44442_EY
_
_
_
_
RC44442_IT | RC44442 | IT |  | _RC44442_IT
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
RC44442_YYS | RC44442 | YYS |  | _RC44442_YYS
RC45051_AUX | RC45051 | AUX |  | _RC45051_M01
RC45051_COIL | RC45051 | COIL |  | _RC45051_M01
RC45052_AUX | RC45052 | AUX |  | _RC45052_M01
RC45052_COIL | RC45052 | COIL |  | _RC45052_M01
RC4522_1_IT | RC4522 | 1 | IT | _RC4522_1_IT
RC4522_2_IT | RC4522 | 2 | IT | _RC4522_2_IT
RC45221_AUX | RC45221 | AUX |  | _RC45221_M01
RC45221_COIL | RC45221 | COIL |  | _RC45221_M01
RC45222_AUX | RC45222 | AUX |  | _RC45222_M01
RC45222_COIL | RC45222 | COIL |  | _RC45222_M01
SB2304_LIH | SB2304 | LIH |  | _SB2304_LIH
SB2304_LIL | SB2304 | LIL |  | _SB2304_LIL
SC_1613_PCD | SC | 1613 | PCD | _SC_1613_PCD
SC1316_AUX | SC1316 | AUX |  | _SC1316_M01
SC1316_COIL | SC1316 | COIL |  | _SC1316_M01
SC1316_MS | SC1316 | MS |  | _SC1316_MS
SC1316A_AUX | SC1316A | AUX |  | _SC1316A_M01
SC1316A_COIL | SC1316A | COIL |  | _SC1316A_M01
SC1318_AUX | SC1318 | AUX |  | _SC1318_M01
SC1318_COIL | SC1318 | COIL |  | _SC1318_M01
SC1318_MS | SC1318 | MS |  | _SC1318_MS
SC1613_COIL | SC1613 | COIL |  | _SC1613_M01
SC1613A_HS | SC1613A | HS |  | _SC1613A_HS
SC1613A_IT | SC1613A | IT |  | _SC1613A_IT
SC1613B_AUX | SC1613B | AUX |  | _SC1613B_M01
SC1613B_HS | SC1613B | HS |  | _SC1613B_HS
SC1613B_IT | SC1613B | IT |  | _SC1613B_IT
SC1613B_MS | SC1613B | MS |  | _SC1613B_MS
SC2316_1_AUX | SC2316 | 1 | AUX | _SC2316_1_AUX
SC2316_2_AUX | SC2316 | 2 | AUX | _SC2316_2_AUX
SC2316_COIL | SC2316 | COIL |  | _SC2316_M01
SC2316A_1_AUX | SC2316A | 1 | AUX | _SC2316A_1_AUX
SC2316A_2_AUX | SC2316A | 2 | AUX | _SC2316A_2_AUX
SC2316A_COIL | SC2316A | COIL |  | _SC2316A_M01
SC2316B_1_AUX | SC2316B | 1 | AUX | _SC2316B_1_AUX
SC2316B_2_AUX | SC2316B | 2 | AUX | _SC2316B_2_AUX
SC2316B_COIL | SC2316B | COIL |  | _SC2316B_M01
SC2316C_1_AUX | SC2316C | 1 | AUX | _SC2316C_1_AUX
SC2316C_2_AUX | SC2316C | 2 | AUX | _SC2316C_2_AUX
SC2316C_COIL | SC2316C | COIL |  | _SC2316C_M01
SC2316D_1_AUX | SC2316D | 1 | AUX | _SC2316D_1_AUX
SC2316D_2_AUX | SC2316D | 2 | AUX | _SC2316D_2_AUX
SC2316D_COIL | SC2316D | COIL |  | _SC2316D_M01
SC2316D_HS | SC2316D | HS |  | _SC2316D_HS
SC2316E_1_AUX | SC2316E | 1 | AUX | _SC2316E_1_AUX
SC2316E_2_AUX | SC2316E | 2 | AUX | _SC2316E_2_AUX
SC2316E_COIL | SC2316E | COIL |  | _SC2316E_M01
SC2316E_HS | SC2316E | HS |  | _SC2316E_HS
SC2316F_1_AUX | SC2316F | 1 | AUX | _SC2316F_1_AUX
SC2316F_2_AUX | SC2316F | 2 | AUX | _SC2316F_2_AUX
SC2316F_COIL | SC2316F | COIL |  | _SC2316F_M01
SC2316F_HS | SC2316F | HS |  | _SC2316F_HS
SC2316G_1_AUX | SC2316G | 1 | AUX | _SC2316G_1_AUX
SC2316G_2_AUX | SC2316G | 2 | AUX | _SC2316G_2_AUX
SC2316G_COIL | SC2316G | COIL |  | _SC2316G_M01
SC2316G_HS | SC2316G | HS |  | _SC2316G_HS
SC316A_MS | SC316A | MS |  | _SC316A_MS
SC4408_AUX | SC4408 | AUX |  | _SC4408_M01
SC4408_COIL | SC4408 | COIL |  | _SC4408_M01
SC4408_MS | SC4408 | MS |  | _SC4408_MS
SC4408A_AUX | SC4408A | AUX |  | _SC4408A_M01
SC4408A_COIL | SC4408A | COIL |  | _SC4408A_M01
SC4408A_MS | SC4408A | MS |  | _SC4408A_MS
SC4408B_AUX | SC4408B | AUX |  | _SC4408B_M01
SC4408B_COIL | SC4408B | COIL |  | _SC4408B_M01
SC4408B_MS | SC4408B | MS |  | _SC4408B_MS
SC4408C_AUX | SC4408C | AUX |  | _SC4408C_M01
SC4408C_COIL | SC4408C | COIL |  | _SC4408C_M01
SC4408C_EY | SC4408C | EY |  | _SC4408C_EY
SC4408C_IT | SC4408C | IT |  | _SC4408C_IT
SC4408C_MS | SC4408C | MS |  | _SC4408C_MS
SC4408C_YYS | SC4408C | YYS |  | _SC4408C_YYS
SC441_AUX | SC441 | AUX |  | _SC441_M01
SC4412_AUX | SC4412 | AUX |  | _SC4412_M01
SC4412_COIL | SC4412 | COIL |  | _SC4412_M01
SC4412_YYS | SC4412 | YYS |  | _SC4412_YYS
SC44122_MS | SC44122 | MS |  | _SC44122_MS
SC44122_YYS | SC44122 | YYS |  | _SC44122_YYS
SC4413_AUX | SC4413 | AUX |  | _SC4413_M01
_
SC4413_COIL | SC4413 | COIL |  | _SC4413_M01
SC4413_IT | SC4413 | IT |  | _SC4413_IT
SC4413_MS | SC4413 | MS |  | _SC4413_MS
SC44142_AUX | SC44142 | AUX |  | _SC44142_M01
SC44142_COIL | SC44142 | COIL |  | _SC44142_M01
SC44142_EY | SC44142 | EY |  | _SC44142_EY
SC4425_AUX | SC4425 | AUX |  | _SC4425_M01
SC4425_COIL | SC4425 | COIL |  | _SC4425_M01
SC4425_MS | SC4425 | MS |  | _SC4425_MS
SC4426_AUX | SC4426 | AUX |  | _SC4426_M01
SC4426_COIL | SC4426 | COIL |  | _SC4426_M01
SC4426_MS | SC4426 | MS |  | _SC4426_MS
SC4427_AUX | SC4427 | AUX |  | _SC4427_M01
SC4427_COIL | SC4427 | COIL |  | _SC4427_M01
_
SC4427_MS | SC4427 | MS |  | _SC4427_MS
SC4427_SSA | SC4427 | SSA |  | _SC4427_SSA
SC4427_YS | SC4427 | YS |  | _SC4427_YS
SC4428_AUX | SC4428 | AUX |  | _SC4428_M01
SC4428_COIL | SC4428 | COIL |  | _SC4428_M01
SC4428_IT | SC4428 | IT |  | _SC4428_IT
SC4428_MS | SC4428 | MS |  | _SC4428_MS
SC4428_SSA | SC4428 | SSA |  | _SC4428_SSA
SC4428_YS | SC4428 | YS |  | _SC4428_YS
SC443_YYS | SC443 | YYS |  | _SC443_YYS
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
SC4430A_AUX | SC4430A | AUX |  | _SC4430A_M01
SC4430A_COIL | SC4430A | COIL |  | _SC4430A_M01
SC4430A_SSA | SC4430A | SSA |  | _SC4430A_SSA
SC4430A_YS | SC4430A | YS |  | _SC4430A_YS
SC4443_1_AUX | SC4443 | 1 | AUX | _SC4443_1_AUX
SC4443_2_AUX | SC4443 | 2 | AUX | _SC4443_2_AUX
SC4443_COIL | SC4443 | COIL |  | _SC4443_M01
SC4443_EY | SC4443 | EY |  | _SC4443_EY
SC4443_IT | SC4443 | IT |  | _SC4443_IT
SC4443_MS | SC4443 | MS |  | _SC4443_MS
SC4445_AUX | SC4445 | AUX |  | _SC4445_M01
SC4445_COIL | SC4445 | COIL |  | _SC4445_M01
SC4445_EY | SC4445 | EY |  | _SC4445_EY
SC4445_IT | SC4445 | IT |  | _SC4445_IT
SC4445_MS | SC4445 | MS |  | _SC4445_MS
SC4445_YYS | SC4445 | YYS |  | _SC4445_YYS
SC4447_AUX | SC4447 | AUX |  | _SC4447_M01
SC4447_COIL | SC4447 | COIL |  | _SC4447_M01
SC4447_EY | SC4447 | EY |  | _SC4447_EY
SC4447_IT | SC4447 | IT |  | _SC4447_IT
SC4447_MS | SC4447 | MS |  | _SC4447_MS
SC4447_YYS | SC4447 | YYS |  | _SC4447_YYS
_
_
_
_
_
_
_
_
_
_
SG4462_SV | SG4462 | SV |  | _SG4462_SV
SILO1_LAH | SILO1 | LAH |  | _SILO1_LAH
SILO2_LAH | SILO2 | LAH |  | _SILO2_LAH
SILO3_LAH | SILO3 | LAH |  | _SILO3_LAH
SILO3A_LT | SILO3A | LT |  | _SILO3A_LT
SILO4_LAH | SILO4 | LAH |  | _SILO4_LAH
SILO5_LAH | SILO5 | LAH |  | _SILO5_LAH
SILO6_LAH | SILO6 | LAH |  | _SILO6_LAH
SL401A_LIH | SL401A | LIH |  | _SL401A_LIH
SL402A_LIH | SL402A | LIH |  | _SL402A_LIH
SL403A_LIH | SL403A | LIH |  | _SL403A_LIH
SPARE | SPARE |  |  | _SPARE
TBD | TBD |  |  | _TBD
TK_02_LAH | TK | 2 | LAH | _TK_02_LAH
_
_
TK_02_LAL | TK | 2 | LAL | _TK_02_LAL
_
_
_
_
_
_
_
VF1340A_AUX | VF1340A | AUX |  | _VF1340A_M01
VF1340A_COIL | VF1340A | COIL |  | _VF1340A_M01
_
VF1340A_SPT | VF1340A | SPT |  | _VF1340A_SPT
VF1340A_TE | VF1340A | TE |  | _VF1340A_TE
_
_
_
VF1340B_AUX | VF1340B | AUX |  | _VF1340B_M01
VF1340B_COIL | VF1340B | COIL |  | _VF1340B_M01
VF1340B_SPT | VF1340B | SPT |  | _VF1340B_SPT
_
_
_
_
_
VF1340B_TE | VF1340B | TE |  | _VF1340B_TE
VF1340C_AUX | VF1340C | AUX |  | _VF1340C_M01
VF1340C_COIL | VF1340C | COIL |  | _VF1340C_M01
VF1340C_SPT | VF1340C | SPT |  | _VF1340C_SPT
VF1340C_TE | VF1340C | TE |  | _VF1340C_TE
VF1340D_AUX | VF1340D | AUX |  | _VF1340D_M01
VF1340D_COIL | VF1340D | COIL |  | _VF1340D_M01
VF1340D_SPT | VF1340D | SPT |  | _VF1340D_SPT
VF1340D_TE | VF1340D | TE |  | _VF1340D_TE
VF2311_AUX | VF2311 | AUX |  | _VF2311_M01
VF2311_COIL | VF2311 | COIL |  | _VF2311_M01
VF2311_SPT | VF2311 | SPT |  | _VF2311_SPT
VF2311_YYS | VF2311 | YYS |  | _VF2311_YYS
VF3011_AUX | VF3011 | AUX |  | _VF3011_M01
VF3011_SPT | VF3011 | SPT |  | _VF3011_SPT
VF3012_AUX | VF3012 | AUX |  | _VF3012_M01
VF3012_SPT | VF3012 | SPT |  | _VF3012_SPT
VF3013_AUX | VF3013 | AUX |  | _VF3013_M01
VF3013_SPT | VF3013 | SPT |  | _VF3013_SPT
VF3014_AUX | VF3014 | AUX |  | _VF3014_M01
VF3014_SPT | VF3014 | SPT |  | _VF3014_SPT
VF3015_AUX | VF3015 | AUX |  | _VF3015_M01
VF3015_SPT | VF3015 | SPT |  | _VF3015_SPT
VF3016_AUX | VF3016 | AUX |  | _VF3016_M01
SPARE | SPARE |  |  | _SPARE
VF3016_SPT | VF3016 | SPT |  | _VF3016_SPT
SPARE | SPARE |  |  | _SPARE
VF4504A_AUX | VF4504A | AUX |  | _VF4504A_M01
SPARE | SPARE |  |  | _SPARE
VF4504A_COIL | VF4504A | COIL |  | _VF4504A_M01
VF4504A_SPT | VF4504A | SPT |  | _VF4504A_SPT
VF4504A_SSA | VF4504A | SSA |  | _VF4504A_SSA
_
_
_
_
_
VF4504B_AUX | VF4504B | AUX |  | _VF4504B_M01
VF4504B_COIL | VF4504B | COIL |  | _VF4504B_M01
VF4504B_SPT | VF4504B | SPT |  | _VF4504B_SPT
VF4504B_SSA | VF4504B | SSA |  | _VF4504B_SSA
VF504A_PGE_PS | VF504A | PGE | PS | _VF504A_PGE_PS
VF504B_PGE_PS | VF504B | PGE | PS | _VF504B_PGE_PS
VF83011_AUX | VF83011 | AUX |  | _VF83011_M01
VF83011_COIL | VF83011 | COIL |  | _VF83011_M01
VF83011_SSA | VF83011 | SSA |  | _VF83011_SSA
VF83012_AUX | VF83012 | AUX |  | _VF83012_M01
VF83012_COIL | VF83012 | COIL |  | _VF83012_M01
_
_
VF83012_SSA | VF83012 | SSA |  | _VF83012_SSA
VF83013_AUX | VF83013 | AUX |  | _VF83013_M01
VF83013_COIL | VF83013 | COIL |  | _VF83013_M01
VF83013_SSA | VF83013 | SSA |  | _VF83013_SSA
_
_
_
_
_
_
_
_
_
_
VF83014_AUX | VF83014 | AUX |  | _VF83014_M01
VF83014_COIL | VF83014 | COIL |  | _VF83014_M01
VF83015_AUX | VF83015 | AUX |  | _VF83015_M01
VF83015_COIL | VF83015 | COIL |  | _VF83015_M01
_
VF83016_AUX | VF83016 | AUX |  | _VF83016_M01
VF83016_COIL | VF83016 | COIL |  | _VF83016_M01
VS_432_IT | VS | 432 | IT | _VS_432_IT
VS328_IT | VS328 | IT |  | _VS328_IT
_
VS4404_AUX | VS4404 | AUX |  | _VS4404_M01
VS4404_COIL | VS4404 | COIL |  | _VS4404_M01
VS4404_EY | VS4404 | EY |  | _VS4404_EY
VS4404_IT | VS4404 | IT |  | _VS4404_IT
_
VS4404_YYS | VS4404 | YYS |  | _VS4404_YYS
VS4432_AUX | VS4432 | AUX |  | _VS4432_M01
VS4432_COIL | VS4432 | COIL |  | _VS4432_M01
VS4432_YAY | VS4432 | YAY |  | _VS4432_YAY
VS8328_AUX | VS8328 | AUX |  | _VS8328_M01
VS8328_COIL | VS8328 | COIL |  | _VS8328_M01
WF1601_AUX | WF1601 | AUX |  | _WF1601_M01
WF1601_WT | WF1601 | WT |  | _WF1601_WT
WF161_WQS | WF161 | WQS |  | _WF161_WQS
WF2601_AUX | WF2601 | AUX |  | _WF2601_M01
_
_
_
WF2601_COIL | WF2601 | COIL |  | _WF2601_M01
_
_
_
WF2601_PCD | WF2601 | PCD |  | _WF2601_PCD
WF2601_SPT | WF2601 | SPT |  | _WF2601_SPT
WF2601_WQS | WF2601 | WQS |  | _WF2601_WQS
WF2601_WT | WF2601 | WT |  | _WF2601_WT
_
WF2601A_AUX | WF2601A | AUX |  | _WF2601A_M01
WF2601A_FLT | WF2601A | FLT |  | _WF2601A_FLT
_
WF2601A_SSA | WF2601A | SSA |  | _WF2601A_SSA
WF2601A_WQS | WF2601A | WQS |  | _WF2601A_WQS
WP13261_AUX | WP13261 | AUX |  | _WP13261_M01
WP13261_COIL | WP13261 | COIL |  | _WP13261_M01
_
WP13262_AUX | WP13262 | AUX |  | _WP13262_M01
WP13262_COIL | WP13262 | COIL |  | _WP13262_M01
WP23261_AUX | WP23261 | AUX |  | _WP23261_M01
WP23261_COIL | WP23261 | COIL |  | _WP23261_M01
WP23262_AUX | WP23262 | AUX |  | _WP23262_M01
_
_
_
_
_
WP23262_COIL | WP23262 | COIL |  | _WP23262_M01
WP3083_AUX | WP3083 | AUX |  | _WP3083_M01
WS8303A_WIT | WS8303A | WIT |  | _WS8303A_WIT
_
_
WS8303A_WQS | WS8303A | WQS |  | _WS8303A_WQS
WS8329_WIT | WS8329 | WIT |  | _WS8329_WIT
WS8329_WQS | WS8329 | WQS |  | _WS8329_WQS
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_
_

## DB_Augost11 (hidden)
02_COOLING_TK | $System |  | °F | 250 | 0 | 0 | 0 | PLC_INTREAD | N58:1 | KILN 1 PERCENT OXYGEN
1_313_AIR_PRESSURE | $System |  | PSI | 150 | 0 | 0 | SPARE TAG | 0 | 0 | 0
1_313_PT | $System |  | PSI | 150 | 0 | 0 | SPARE TAG | 0 | 0 | 0
1_314_PT | $System |  | PSI | 150 | 0 | 0 | SPARE TAG | 0 | 0 | 0
AFHistoricalPath | $System
AIR_CANNON_AUTO | $System |  | None | PLC_DISCWRITE | B100:52/3 | VF 301-5 AUX FDBK
AIR_CANNON_TMR | $System |  | SEC. | 1000 | 0 | 0 | 0 | PLC_FLTWRITE | T4:803.ACC | 2
AIR_CANNON_TMR_PRE | $System |  | SEC. | 1000 | 0 | 0 | 0 | PLC_FLTWRITE | T4:803.PRE | 2
ALARM_SCREEN | $System | ALARM SCREEN SELECTOR NUMBER |  | 100 | 0 | 0 | AccessLevel | 0 | 0 | 0
APEX_DOLO_SILO_LT | $System |  | FT. | 22 | 0 | 0 | 0 | APEX_BULK | N7:0 | WF 1-601 TOTALIZER DAILY
AreaIndex | $System |  |  | 1000 | 0 | 0 | AccessLevel | 0 | 0 | 0
B401MS_X | $System |  | None | 0
Back_System | $System |  | 0
BAG_HOUSE_COMP | $System |  |  | 2 | 0 | 0 | AccessLevel | 0 | 0 | 0
BC_401_RATE | $System |  | TONS/HR | 200 | 0 | 0 | 0 | PLC_FLTREAD | F9:146 | KILN 1 TONS LIMESTONE PER HOUR
BC_401_STROKE_TONS_K1 | $System |  | TONS | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F9:411 | KILN 1 TONS LIMESTONE PER HOUR
BC_401_STROKE_TONS_K2 | $System |  | TONS | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F9:413 | KILN 1 TONS LIMESTONE PER HOUR
BC_401_TOTAL | $System |  | None | PLC_DISCWRITE | B3:93/5
BC_401_TOTAL_RECLAIM_K1 | $System |  | TONS | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F9:141 | KILN 1 TONS LIMESTONE PER HOUR
BC_401_TOTAL_RECLAIM_K2 | $System |  | TONS | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F9:142 | KILN 1 TONS LIMESTONE PER HOUR
BC_401_TOTAL_TONS | $System |  | TONS/HR | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F9:145 | KILN 1 TONS LIMESTONE PER HOUR
BC_401_TOTAL_TONS_YESTERDAY | $System |  | TONS/HR | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F9:143 | KILN 1 TONS LIMESTONE PER HOUR
BC604_MS_X | $System |  | None | 0
BC604MS_X | $System |  | None | 0
BE521_SHUTDOWN_TMR | $System |  | SEC | 1800 | 0 | 0 | 0 | PLC_FLTREAD | N13:0 | FN 2-312 AMPS
BE521_SHUTDOWN_TMR_EN | $System |  | None | PLC_DISCREAD | T4:728.EN
BM1602_LUBE_TMR_REM | $System |  | Sec | 500 | 0 | 0 | 0 | PLC_INTREAD | F27:72
BM2602_LUBE_TMR_REM | $System |  | Sec | 500 | 0 | 0 | 0 | PLC_INTREAD | F27:73
Coal_Feed | $System |  | 0
COI_MAC_TK180_LT_ENG | $System |  | None | 0
COI_MAC_TK180_LT_IND | $System |  | None | 0
COMM_FAILED_0 | $System |  | Off | USCNEL101 | COMM_FAILED.0
COMM_FAILED_01 | $System |  | Off | USCNEL101 | COMM_FAILED.0
COMM_FAILED_02 | $System |  | Off | USCNEL202 | COMM_FAILED.0
cursor | $System | SLIDER FOR ZOOMING IN ON TRENDS |  | 9999 | 5 | 0 | SLIDER FOR ZOOMING IN ON TRENDS | 0 | 0 | 0
DC_2313_Air_Press_IND | $System |  |  | 1 | 0 | 0 | SPARE TAG | 0 | 0 | 0
DG_4516_COAL_IND | $System |  | None | PLC_DISCREAD | B3:92/14
DG_4516_COKE_IND | $System |  | None | PLC_DISCREAD | B3:92/13
DG4516_FAULT_IND | $System |  | On | PLC_DISCREAD | B3:92/12 | COAL COKE DIVERTER GATE STUCK
DG4516_OPEN | $System |  | None | PLC_DISCWRITE | B3:92/15
Dummy_Button | $System |  | None | PLC_ALARM | B30:36/13
Dust_Blending | $System |  | 0
FN1_314_ALM_HIHIWDGTEMP6 | $System |  | None | 0
FN1_314_RT_HRS | $System | ID Fan Runtime in hours | Hrs | 10000 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_RT_HRS
FN1_314_SPD_SP | $System | ID Fan Percent Setpoint | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_SPD_SP
FN1314_TT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | FN1314_TT
FN2314_press_ind | $System |  | in h2o | 50 | 0 | 0 | 0 | PLC_FLTREAD | F9:320 | Dust Bin Level
FN2314MS_Xa | $System |  | None | 0
FRONT_SYS_AUX | $System |  | None | PLC_DISCREAD | I:231/1
Front_System | $System |  | 0
General_Plant | $System |  | 0
HistTrend | $System
HISTTREND_UPDATE | $System | HIST TREND AUTO UPDATE | None | 0
HistTrend1 | $System | HISTORICAL TREND - PENS 1-4
HistTrend2 | $System | HISTORICAL TREND - PENS 5-8
HistTrendPanMins | $System |  |  | 32767 | 0 | 0 |  | 0 | 0 | 0
HistTrendPenScale | $System |  |  | 32767 | 0 | 0 |  | 0 | 0 | 0
HistTrendTitle | $System | KILN 1 & 2 HISTORICAL TREND TITLE
HOUR-PLC | $System | PLC TIME - HOUR | HOUR | 24 | 1 | 0 | 0 | PLC_INTREAD | S:21 | PLC TIME - HOUR
HTMotorFacePlate | $System |  | None | 0
HTPen01 | $System
HTPen02 | $System
HTPen03 | $System
HTPen04 | $System
HTPen05 | $System
HTPen06 | $System
HTPen07 | $System
HTPen08 | $System
HYDRATE_LASTCOMM | $System | COUNTER TO CHECK HYDRATE PLC COMMS | sec | 32000 | 10 | 0 | LOST COMMUNICATION WITH HYDRATE PLC!! | 0 | 0 | 0
Hydrator | $System |  | 0
I@@1 | $System
IndirectAnalogTag | $System | TAG FOR PEN SWAPING IN TRENDS
K1_BH_COMP | $System |  | None | 1
K1_CANNON_FIRE_WITH_RAM# | $System | Ram number to fire cannon with |  | 100 | 0 | 0 | 0 | PLC_INTWRITE | N99:11 | FV 2-216 LOW PID DAMPER SP
K1_CANNON1_FIRE | $System | Cannon to fire | None | 1
K1_CANNON10_FIRE | $System | Cannon to fire | None | 1
K1_CANNON11_FIRE | $System |  | None | 1
K1_CANNON12_FIRE | $System |  | None | 1
K1_CANNON13_FIRE | $System |  | None | 1
K1_CANNON14_FIRE | $System |  | None | 1
K1_CANNON15_FIRE | $System |  | None | 1
K1_CANNON2_FIRE | $System | Cannon to fire | None | 1
K1_CANNON3_FIRE | $System | Cannon to fire | None | 1
K1_CANNON4_FIRE | $System | Cannon to fire | None | 1
K1_CANNON5_FIRE | $System | Cannon to fire | None | 1
K1_CANNON6_FIRE | $System | Cannon to fire | None | 1
K1_CANNON7_FIRE | $System | Cannon to fire | None | 1
K1_CANNON8_FIRE | $System | Cannon to fire | None | 1
K1_CANNON9_FIRE | $System | Cannon to fire | None | 1
K1_CO_PID_MAXO | $System | K1 CO PID Maximum Clamp | % | 100 | 0 | 0 | 0 | PLC_INTREAD | N102:174
K1_CO_PID_MINO | $System | K1 CO PID Minimum Clamp | % | 100 | 0 | 0 | 0 | PLC_INTREAD | N102:175
K1_COAL_BIN_TEMP | $System |  | SEC | 500 | 0 | 0 | 0 | PLC_FLTREAD | F9:325 | FN 2-312 AMPS
K1_ExitTemp_PID_Type | $System |  | Off | 1
K1_FIRE_CANNON_WITH_RAM | $System | Fire Cannon with a Ram | None | PLC_DISCREAD | B100:38/10
K1_O2_PID_MAXO | $System | K1 O2 PID Maximum Clamp | % | 100 | 0 | 0 | 0 | PLC_INTREAD | N85:11
K1_O2_PID_MINO | $System | K1 O2 PID Minimum Output Clamp | % | 100 | 0 | 0 | 0 | PLC_INTREAD | N85:12
K1_S-T | $System |  | None | 0
K1BLAST_INTV | $System |  | sec | 32000 | 0 | 0 | LOST COMMUNICATION WITH HYDRATE PLC!! | 0 | 0 | 0
K1BLAST11_BYP | $System |  | None | PLC_DISCREAD | b100/731
K1BLAST11_PCS | $System | KILN 1 AIR BLASTER CANNON 11 PC START | None | PLC_DISCREAD | b100/795
K1BLAST11_X | $System |  | None | USCNEL101 | NEL_KN1_AC011.EN
K1BLAST12_BYP | $System |  | None | PLC_DISCREAD | b100/732
K1BLAST12_PCS | $System | KILN 1 AIR BLASTER CANNON 12 PC START | None | PLC_DISCREAD | b100/796
K1BLAST12_X | $System |  | None | USCNEL101 | NEL_KN1_AC012.EN
K1BLAST13_BYP | $System |  | None | PLC_DISCREAD | b100/733
K1BLAST13_PCS | $System | KILN 1 AIR BLASTER CANNON 13 PC START | None | PLC_DISCREAD | b100/797
K1BLAST13_X | $System |  | None | USCNEL101 | NEL_KN1_AC013.EN
K1BLAST14_BYP | $System |  | None | PLC_DISCREAD | b100/734
K1BLAST14_PCS | $System | KILN 1 AIR BLASTER CANNON 14 PC START | None | PLC_DISCREAD | b100/798
K1BLAST14_X | $System |  | None | PLC_DISCREAD | O:26\16
K1BLAST15_BYP | $System |  | None | PLC_DISCREAD | b100/735
K1BLAST15_PCS | $System | KILN 1 AIR BLASTER CANNON 15 PC START | None | PLC_DISCREAD | b100/799
K1BLAST15_X | $System |  | None | HYD_DISCREAD | O:26\15
K1CEM_AM | $System | Kiln 1 CEM PID Auto / Manual | None | PLC_DISCREAD | B100:5/8
K1CEM_PV | $System | Kiln 1 CEM Process Variable | ppm | 5000 | 0 | 0 | 0 | PLC_FLTWRITE | F9:240
K1CO_AM | $System | Kiln 1 CO PID Auto / Manual | None | PLC_DISCREAD | B100:39/6
K1CO_AM_APC | $System | Kiln 1 CO PID APC Auto / Manual | None | PLC_DISCREAD | B100:39/7
K1CO_AUTO_SP | $System | Kiln 1 Exit CO PID Setpoint | PPM | 6000 | 0 | 0 | 100 | PLC_FLTREAD | F9:163 | FN 1-312 AMPS
K1DUSTBINHI_ALM | $System |  | None | 0
K1TrendsTabIndex | $System |  |  | 1000 | 0 | 0 | AccessLevel | 0 | 0 | 0
K2_BH_COMP | $System |  | None | 1
K2_CANNON_FIRE_WITH_RAM# | $System | Ram number to fire cannon with |  | 100 | 0 | 0 | 0 | PLC_INTWRITE | N99:12 | FV 2-216 LOW PID DAMPER SP
K2_CANNON1_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON10_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON11_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON12_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON13_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON14_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON15_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON16_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON2_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON3_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON4_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON5_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON6_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON7_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON8_FIRE | $System | Cannon to Fire | None | 1
K2_CANNON9_FIRE | $System | Cannon to Fire | None | 1
K2_FIRE_CANNON_WITH_RAM | $System | Fire cannon with a ram | None | PLC_DISCREAD | B100:38/11
K2_TEMP_DEV | $System | Kiln 2 Exit/Inlet Temperature Deviation Actual | deg F | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F71:27 | KILN 1 PERCENT CARBON MONOXIDE
K2_TEMP_DEV_SP | $System | Kiln 2 Exit/Inlet Temperature Deviation Setpoint | deg F | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F71:26 | KILN 1 PERCENT CARBON MONOXIDE
K2BLAST11_BYP | $System |  | None | PLC_DISCREAD | B100/731
K2BLAST11_X | $System |  | None | PLC_DISCREAD | o:42/12
K2BLAST12_BYP | $System |  | None | PLC_DISCREAD | b100/732
K2BLAST12_X | $System |  | None | PLC_DISCREAD | o:42/13
K2BLAST13_BYP | $System |  | None | PLC_DISCREAD | b100/733
K2BLAST13_X | $System |  | None | PLC_DISCREAD | o:42/14
K2BLAST14_BYP | $System |  | None | PLC_DISCREAD | b100/734
K2BLAST14_X | $System |  | None | PLC_DISCREAD | o:42/15
K2BLAST15_BYP | $System |  | None | PLC_DISCREAD | B100/780
K2BLAST15_PCS | $System |  | None | PLC_DISCREAD | b100/781
K2BLAST15_X | $System |  | None | PLC_DISCREAD | O:42/16
K2BLAST15A_BYP | $System |  | None | PLC_DISCREAD | B100:11 | KILN 2 02 LOW LEVEL
K2BLAST16_BYP | $System |  | None | PLC_DISCREAD | B100/782
K2BLAST16_PCS | $System |  | None | PLC_DISCREAD | b100/783
K2BLAST16_X | $System |  | None | PLC_DISCREAD | O:42/17
K2CEM_AM | $System | Kiln 2 CEM PID Auto / Manual | None | PLC_DISCREAD | B100:5/7
K2CEM_APC | $System | Kiln 2 CEM PID APC / Manual | None | PLC_DISCREAD | B100:39/2
K2CO_APC | $System | Kiln 2 CO PID APC / Manual | None | PLC_DISCREAD | B100:39/1
K2TrendsTabIndex | $System |  |  | 1000 | 0 | 0 | AccessLevel | 0 | 0 | 0
K3CO_AM | $System | Kiln 2 CO PID Auto / Manual | None | PLC_DISCREAD | B100:5/5
K3CO_AUTO_SP | $System | Kiln 2 Exit CO PID Setpoint | PPM | 6000 | 0 | 0 | 100 | PLC_FLTREAD | F9:84 | FN 1-312 AMPS
KD1308_PONYBOX | $System |  | Off | PLC_DISCREAD | I:025/00 | KILN 1 DRIVE PONYBOX OPEN
Kiln1 | $System |  | 0
KILN1_BH | $System |  | 0
KILN1_O2_AVERAGE | $System |  | % | 20.9 | 0 | 0 | 0 | PLC_FLTWRITE | F27:79
Kiln2 | $System |  | 0
KILN2_TEMP_DEV_LOW | $System | Kiln2 Exit/Inlet Temperature Deviation Low | On | PLC_DISCREAD | B101:36/5 | Kiln 2 Exit/Inlet Temperature Deviation Low
LABELSON | $System |  | None | 1
LH1_BE509_AUX | $System |  | None | 0
LH1_BE509_SSA | $System |  | None | 0
LOGIN_BUFFER | $System | PROCESS COMPUTER SYSTEM CRO LOGIN BUFFER | No | NEW LOGIN IN BUFFER
LOGIN_CRO | $System | LOGIN TO SYSTEM | None | PLC_DISCWRITE | B100/610
LOGIN_FINAL | $System | PROCESS COMPUTER SYSTEM CRO LOGIN NAME | No | NEW LOGIN
LOGIN_NOCRO | $System | NO CRO LOGGED IN!! | On | PLC_ALARM | B101/566 | CONTROL ROOM OPERATOR IS NOT LOGGED IN!!
LOGIN_WW | $System | CRO LOGIN WW BUFFER |  | 123199 | 0 | 0 | 0 | PLC_FLTWRITE | F71:15
LOGOUT | $System | Bit to force log out. | None | 0
M@@0 | $System
MainMenuIndex | $System |  |  | 1000 | 0 | 0 | AccessLevel | 0 | 0 | 0
MCFP_DG_DirZSC | $System
MCFP_DG_DirZSE | $System | Extended direction.
MCFP_DG_DirZSO | $System
MCFP_DG_DirZSR | $System | Retracted direction
MCFP_DG_Ilock_Msg | $System
MCFP_DG_Ilock1_FaultState | $System |  | None | 0
MCFP_DG_Ilock1_Ind | $System
MCFP_DG_Ilock2_FaultState | $System |  | None | 0
MCFP_DG_Ilock2_Ind | $System
MCFP_DG_Ilock3_FaultState | $System |  | None | 0
MCFP_DG_Ilock3_Ind | $System
MCFP_DG_Ilock4_FaultState | $System |  | None | 0
MCFP_DG_Ilock4_Ind | $System
MCFP_DG_Ilock5_FaultState | $System |  | None | 0
MCFP_DG_Ilock5_Ind | $System
MCFP_DG_Ilock6_FaultState | $System |  | None | 0
MCFP_DG_Ilock6_Ind | $System
MCFP_DG_Ilock7_FaultState | $System |  | None | 0
MCFP_DG_Ilock7_Ind | $System
MCFP_DG_Ilock8_FaultState | $System |  | None | 0
MCFP_DG_Ilock8_Ind | $System
MCFP_DG_Message1 | $System
MCFP_DG_Message2 | $System
MCFP_DG_SEL_HMI_Ind | $System | Indirect tag for Diverter Gate control
MCFP_DG_ZSC_Ind | $System | Diverter gate closed position limit indirect.
MCFP_DG_ZSE_Ind | $System | Extended
MCFP_DG_ZSO_Ind | $System | Diverter gate open position limit indirect.
MCFP_DG_ZSR_Ind | $System | Retracted
MCFP_HT_Pen1_Ind | $System
MCFP_HT_Pen1_Label | $System
MCFP_HT_Pen2_Ind | $System
MCFP_HT_Pen2_Label | $System
MCFP_HT_Pen3_Ind | $System
MCFP_HT_Pen3_Label | $System
MCFP_HT_Pen4_Ind | $System
MCFP_HT_Pen4_Label | $System
MCFP_HTMotorFacePlate | $System
MCFP_Ilock_Msg | $System
MCFP_Ilock1_FaultState | $System |  | None | 0
MCFP_Ilock1_Ind | $System
MCFP_Ilock2_FaultState | $System |  | None | 0
MCFP_Ilock2_Ind | $System
MCFP_Ilock3_FaultState | $System |  | None | 0
MCFP_Ilock3_Ind | $System
MCFP_Ilock4_FaultState | $System |  | None | 0
MCFP_Ilock4_Ind | $System
MCFP_Ilock5_FaultState | $System |  | None | 0
MCFP_Ilock5_Ind | $System
MCFP_Ilock6_FaultState | $System |  | None | 0
MCFP_Ilock6_Ind | $System
MCFP_Ilock7_FaultState | $System |  | None | 0
MCFP_Ilock7_Ind | $System
MCFP_Ilock8_FaultState | $System |  | None | 0
MCFP_Ilock8_Ind | $System
MCFP_Message1 | $System
MCFP_Message2 | $System
MCFP_Motor_AUX_Ind | $System
MCFP_Motor_FLT_Ind | $System
MCFP_Motor_HRS_TOT_Ind | $System
MCFP_Motor_IT_Ind | $System
MCFP_Motor_IT_PCT_Ind | $System
MCFP_Motor_PBE_HMI_Ind | $System
MCFP_Motor_PBS_HMI_Ind | $System
MCFP_Motor_RT_RST_Ind | $System
MCFP_Motor_SS_BYP_Ind | $System
MCFP_Motor_SS_BYP_PB_Ind | $System
MCFP_Motor_SSA_HMI_Ind | $System
MCFP_Motor_SSA_Sel_Ind | $System
MCFP_Motor_SSM_Ind | $System
MCFP_Motor_SSM_Sel_Ind | $System
MCFP_Motor_SSO_Ind | $System | Motor OFF selector switch
MCFP_Motor_SSO_Sel_Ind | $System | Motor OFF selector switch "OFF" selected
MCFP_REVVFD_AUX_Ind | $System
MCFP_REVVFD_FLT_Ind | $System
MCFP_REVVFD_HRS_TOT_Ind | $System
MCFP_REVVFD_HT_Pen1_Ind | $System
MCFP_REVVFD_HT_Pen1_Label | $System
MCFP_REVVFD_HT_Pen2_Ind | $System
MCFP_REVVFD_HT_Pen2_Label | $System
MCFP_REVVFD_HT_Pen3_Ind | $System
MCFP_REVVFD_HT_Pen3_Label | $System
MCFP_REVVFD_HT_Pen4_Ind | $System
MCFP_REVVFD_HT_Pen4_Label | $System
MCFP_REVVFD_HTMotorFacePlate | $System
MCFP_REVVFD_Ilock_Msg | $System
MCFP_REVVFD_Ilock1_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock1_Ind | $System
MCFP_REVVFD_Ilock2_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock2_Ind | $System
MCFP_REVVFD_Ilock3_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock3_Ind | $System
MCFP_REVVFD_Ilock4_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock4_Ind | $System
MCFP_REVVFD_Ilock5_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock5_Ind | $System
MCFP_REVVFD_Ilock6_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock6_Ind | $System
MCFP_REVVFD_Ilock7_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock7_Ind | $System
MCFP_REVVFD_Ilock8_FaultState | $System |  | None | 0
MCFP_REVVFD_Ilock8_Ind | $System
MCFP_REVVFD_IT_Ind | $System
MCFP_REVVFD_IT_PCT_Ind | $System
MCFP_REVVFD_PBE_HMI_Ind | $System
MCFP_REVVFD_PBS_HMI_Ind | $System
MCFP_REVVFD_RT_RST_Ind | $System
MCFP_REVVFD_SI_Ind | $System
MCFP_REVVFD_SPT_Ind | $System
MCFP_REVVFD_SS_BYP_Ind | $System
MCFP_REVVFD_SS_BYP_PB_Ind | $System
MCFP_REVVFD_SSA_HMI_FWD_Ind | $System
MCFP_REVVFD_SSA_HMI_Ind | $System
MCFP_REVVFDMessage1 | $System | Not Initialized
MCFP_REVVFDMessage2 | $System | Not Initialized
MCFP_SG_DirZSC | $System
MCFP_SG_DirZSO | $System
MCFP_SG_Ilock_Msg | $System
MCFP_SG_Ilock1_FaultState | $System |  | None | 0
MCFP_SG_Ilock1_Ind | $System
MCFP_SG_Ilock2_FaultState | $System |  | None | 0
MCFP_SG_Ilock2_Ind | $System
MCFP_SG_Ilock3_FaultState | $System |  | None | 0
MCFP_SG_Ilock3_Ind | $System
MCFP_SG_Ilock4_FaultState | $System |  | None | 0
MCFP_SG_Ilock4_Ind | $System
MCFP_SG_Ilock5_FaultState | $System |  | None | 0
MCFP_SG_Ilock5_Ind | $System
MCFP_SG_Ilock6_FaultState | $System |  | None | 0
MCFP_SG_Ilock6_Ind | $System
MCFP_SG_Ilock7_FaultState | $System |  | None | 0
MCFP_SG_Ilock7_Ind | $System
MCFP_SG_Ilock8_FaultState | $System |  | None | 0
MCFP_SG_Ilock8_Ind | $System
MCFP_SG_Message1 | $System
MCFP_SG_Message2 | $System
MCFP_SG_SEL_HMI_Ind | $System | Indirect tag for Slide Gate control
MCFP_SG_ZSC_Ind | $System | Slide gate closed position limit indirect.
MCFP_SG_ZSO_Ind | $System | Slide gate open position limit indirect.
MCFP_VFD_AUX_Ind | $System
MCFP_VFD_FLT_Ind | $System
MCFP_VFD_HRS_TOT_Ind | $System
MCFP_VFD_HT_Pen1_Ind | $System
MCFP_VFD_HT_Pen1_Label | $System
MCFP_VFD_HT_Pen2_Ind | $System
MCFP_VFD_HT_Pen2_Label | $System
MCFP_VFD_HT_Pen3_Ind | $System
MCFP_VFD_HT_Pen3_Label | $System
MCFP_VFD_HT_Pen4_Ind | $System
MCFP_VFD_HT_Pen4_Label | $System
MCFP_VFD_HTMotorFacePlate | $System
MCFP_VFD_Ilock_Msg | $System
MCFP_VFD_Ilock1_FaultState | $System |  | None | 0
MCFP_VFD_Ilock1_Ind | $System
MCFP_VFD_Ilock2_FaultState | $System |  | None | 0
MCFP_VFD_Ilock2_Ind | $System
MCFP_VFD_Ilock3_FaultState | $System |  | None | 0
MCFP_VFD_Ilock3_Ind | $System
MCFP_VFD_Ilock4_FaultState | $System |  | None | 0
MCFP_VFD_Ilock4_Ind | $System
MCFP_VFD_Ilock5_FaultState | $System |  | None | 0
MCFP_VFD_Ilock5_Ind | $System
MCFP_VFD_Ilock6_FaultState | $System |  | None | 0
MCFP_VFD_Ilock6_Ind | $System
MCFP_VFD_Ilock7_FaultState | $System |  | None | 0
MCFP_VFD_Ilock7_Ind | $System
MCFP_VFD_Ilock8_FaultState | $System |  | None | 0
MCFP_VFD_Ilock8_Ind | $System
MCFP_VFD_IT_Ind | $System
MCFP_VFD_IT_PCT_Ind | $System
MCFP_VFD_PBE_HMI_Ind | $System
MCFP_VFD_PBS_HMI_Ind | $System
MCFP_VFD_RT_RST_Ind | $System
MCFP_VFD_SI_Ind | $System
MCFP_VFD_SPT_Ind | $System
MCFP_VFD_SS_BYP_Ind | $System
MCFP_VFD_SS_BYP_PB_Ind | $System
MCFP_VFD_SSA_HMI_Ind | $System
MCFP_VFDMessage1 | $System | Not Initialized
MCFP_VFDMessage2 | $System | Not Initialized
MCFP_VFDSetpoint_PCT | $System |  | % | 100 | 0 | 0 | Hours of Operation, 1st Shift | 0 | 0 | 0
METHOD9K1SD2H_ALM | $System | DO METHOD 9 FOR KILN 1 SHUTDOWN | On | PLC_ALARM | B100/102 | DO METHOD 9 FOR KILN 1 SHUTDOWN
METHOD9K1SD4H_ALM | $System | DO METHOD 9 FOR KILN 1 SHUTDOWN | On | PLC_ALARM | B100/101 | DO METHOD 9 FOR KILN 1 SHUTDOWN
METHOD9K1SU1_ALM | $System | DO METHOD 9 FOR KILN 1 START-UP | On | PLC_ALARM | B101/02 | DO METHOD 9 FOR KILN 1 START-UP
METHOD9K1SU2_ALM | $System | DO METHOD 9 FOR KILN 1 START-UP | On | PLC_ALARM | B101/03 | DO METHOD 9 FOR KILN 1 START-UP
METHOD9K2SD2H_ALM | $System | DO METHOD 9 FOR KILN 2 SHUTDOWN | On | PLC_ALARM | B100/105 | DO METHOD 9 FOR KILN 2 SHUTDOWN
METHOD9K2SD4H_ALM | $System | DO METHOD 9 FOR KILN 2 SHUTDOWN | On | PLC_ALARM | B100/104 | DO METHOD 9 FOR KILN 2 SHUTDOWN
METHOD9K2SU1_ALM | $System | DO METHOD 9 FOR KILN 2 START-UP | On | PLC_ALARM | B101/00 | DO METHOD 9 FOR KILN 2 START-UP
METHOD9K2SU2_ALM | $System | DO METHOD 9 FOR KILN 2 START-UP | On | PLC_ALARM | B101/01 | DO METHOD 9 FOR KILN 2 START-UP
MNET_WATCH_DOG_DN | $System |  | None | KILN1_BH_READ | MNET_WATCH_DOG.DN
N7_122 | $System |  | SEC | 15 | 0 | 0 | 0 | PLC_FLTREAD | N7:122 | FN 2-312 AMPS
NavArea | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastAreaA | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastAreaB | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastAreaC | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastAreaD | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastAreaE | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastAreaF | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabIndex | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewAAreaA | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewAAreaB | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewAAreaC | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewAAreaD | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewAAreaE | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewAAreaF | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewBAreaA | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewBAreaB | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewBAreaC | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewBAreaD | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewBAreaE | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewBAreaF | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewCAreaA | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewCAreaB | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewCAreaC | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewCAreaD | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewCAreaE | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewCAreaF | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewDAreaA | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewDAreaB | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewDAreaC | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewDAreaD | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewDAreaE | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewDAreaF | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewEAreaA | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewEAreaB | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewEAreaC | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewEAreaD | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewEAreaE | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavLastTabViewEAreaF | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavPage | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavReturnIndex | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NavView | $System |  |  | 9999 | 0 | 0 |  | 0 | 0 | 0
NEL_ | $System |  | SEC | 15 | 0 | 0 | 0 | USCNEL202 | NEL_ | FN 2-312 AMPS
NEL_1_313_PT | $System |  | PSI | 150 | 0 | 0 | 0 | KILN1_BH_READ | NEL_1_313_PT | 1-313-AIR PRESSURE
NEL_BACK_SILO_1_FT | $System |  |  | 55 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_1_FT
NEL_BACK_SILO_1_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_1.PCT
NEL_BACK_SILO_1_TONS | $System |  |  | 1000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_1_TONS
NEL_BACK_SILO_2_FT | $System |  |  | 55 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_2_FT
NEL_BACK_SILO_2_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_2.PCT
NEL_BACK_SILO_2_TONS | $System |  |  | 1000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_2_TONS
NEL_BACK_SILO_3_FT | $System |  |  | 60 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_3_FT
NEL_BACK_SILO_3_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_3.PCT
NEL_BACK_SILO_3_TONS | $System |  |  | 1000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_3_TONS
NEL_BACK_SILO_4_FT | $System |  |  | 60 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_4_FT
NEL_BACK_SILO_4_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_4.PCT
NEL_BACK_SILO_4_TONS | $System |  |  | 1000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_4_TONS
NEL_BACK_SILO_5_FT | $System |  |  | 60 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_5_FT
NEL_BACK_SILO_5_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_5.PCT
NEL_BACK_SILO_5_TONS | $System |  |  | 1000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_5_TONS
NEL_BACK_SILO_6_FT | $System |  |  | 60 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_6_FT
NEL_BACK_SILO_6_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_6.PCT
NEL_BACK_SILO_6_TONS | $System |  |  | 505 | 0 | 0 | 0 | KILN1_BH_READ | NEL_BACK_SILO_6_TONS
NEL_BE424_1_BYPASS | $System |  | On | PLC_DISCWRITE | B100/737 | BE-424-1 BYPASSED
NEL_BE424_2_BYPASS | $System |  | On | PLC_DISCWRITE | B100/738SUPPORT1 | BE-424-2 BYPASSED
NEL_BH_BN318_LI_PCT | $System | Kiln 2 Dust Bin Level Percent % | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:489
NEL_BP1_RA03002_AUX | $System |  | None | USCNEL207 | NEL_BP1_RA03002.AUX
NEL_BP1_RA03002_MODE_AUTO | $System |  | None | USCNEL207 | NEL_BP1_RA03002.MODE_AUTO
NEL_BP1_RA03002_PBE_HMI | $System |  | None | USCNEL207 | NEL_BP1_RA03002.PBE_HMI
NEL_BP1_RA03002_PBS_HMI | $System |  | None | USCNEL207 | NEL_BP1_RA03002.PBS_HMI
NEL_BP1_TK02001_XT_IND | $System |  | TPH | 500 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_TK02001_XT.IND | WF 2-601 WEIGH FEED PC SETPOINT
NEL_BP1_TK03002_XT_IND | $System |  | TPH | 100 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_TK03002_XT.IND | WF 2-601 WEIGH FEED PC SETPOINT
NEL_FRONT_1A_TONS | $System |  |  | 3315 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_1A_TONS
NEL_FRONT_SILO_1A_FT | $System |  |  | 70 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_1A_FT
NEL_FRONT_SILO_1A_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_1A.PCT
NEL_FRONT_SILO_1A_TONS | $System |  |  | 3315 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_1A_TONS
NEL_FRONT_SILO_2A_FT | $System |  |  | 70 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_2A_FT
NEL_FRONT_SILO_2A_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_2A.PCT
NEL_FRONT_SILO_2A_TONS | $System |  |  | 3315 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_2A_TONS
NEL_FRONT_SILO_3A_FT | $System |  |  | 70 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_3A_FT
NEL_FRONT_SILO_3A_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_3A.PCT
NEL_FRONT_SILO_3A_TONS | $System |  |  | 3315 | 0 | 0 | 0 | KILN1_BH_READ | NEL_FRONT_SILO_3A_TONS
NEL_HD1_DF0711_SPT | $System |  | HZ | 100 | 0 | 0 | 0 | USCNEL051 | NEL_HD1_DF0711_SPT | KILN 1 PERCENT OXYGEN
NEL_HD1_TK0711_LT_IND | $System | Hydrator Ducon Tank Level Percent % | % | 100 | 0 | 0 | 0 | USCNEL051 | NEL_HD1_TK0711_LT.IND
NEL_K1_BH_BN1318_IT_AH | $System |  | On | KILN1_BH_ALARM | NEL_K1_BH_BN1318_IT.AH | KILN 1 DUST BIN HIGH LEVEL 85%
NEL_K1_BH_BN1318_IT_AHH | $System |  | On | KILN1_BH_ALARM | NEL_K1_BH_BN1318_IT.AHH | KILN 1 DUST BIN HIGH HIGH LEVEL95%
NEL_K1_BH_BN1318_IT_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | NEL_K1_BH_BN1318_IT.PCT | Dust Bin Level
NEL_K1_BH_BN1318_PCT | $System |  | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | MCR_8_CN14:2:I.Ch11Data | KILN 1 PERCENT OXYGEN
NEL_K1_FN1312_ACFM | $System | Kiln 1 Cooler Air Flow ACFM | ACFM | 50000 | 0 | 0 | 0 | PLC_FLTREAD | F9:838
NEL_K1_FN1312_FT_IND | $System |  | % | 50000 | 0 | 0 | 0 | USCNEL101 | NEL_K1_FN1312_FT.IND | KILN 1 PERCENT OXYGEN
Nel_K1_LBS_STK | $System |  | LBS | 1000 | 0 | 0 | 0 | PLC_INTREAD | N112:39 | TE 700 TEMPERATURE
NEL_K1_LBS_STONE_STK | $System |  | LBS | 750 | 0 | 0 | 0 | PLC_INTREAD | N112:74
NEL_K1_LIME | $System |  | "WC | 1200 | 0 | 0 | 0 | PLC_INTREAD | F8:5
Nel_K1_LIME_DAY | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | N112:76 | TE 700 TEMPERATURE
Nel_K1_LIME_DAY_NEW | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | F27:42
NEL_K1_LIME_DAYLY | $System |  | "WC | 1200 | 0 | 0 | 0 | PLC_INTREAD | F27:32
NEL_K1_LIME_PRODUCED | $System |  | "WC | 1200 | 0 | 0 | 0 | PLC_INTREAD | N112:76
NEL_K1_REJECT_JUNK | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | F27:56
NEL_K1_REJECT_SILO3 | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | F27:58
NEL_K1_STONE_TOT | $System |  | "WC | 2500 | 0 | 0 | 0 | PLC_INTREAD | F27:44
NEL_K1_STONE_TOT_KILN | $System |  | TONS | 2500 | 0 | 0 | 0 | PLC_INTREAD | F27:46
NEL_K1_TONS_STONE_STK | $System |  | TONS | 1 | 0 | 0 | 0 | PLC_INTREAD | F27:38
NEL_K1_TONS_STONE_STK_live | $System |  | TONS | 1 | 0 | 0 | 0 | PLC_INTREAD | F27:37
Nel_K2_LBS_STK | $System |  | LBS | 1000 | 0 | 0 | 0 | PLC_INTREAD | N112:35
NEL_K2_LBS_STONE_STK | $System |  | LBS | 900 | 0 | 0 | 0 | PLC_INTREAD | N112:75
Nel_K2_LIME_DAY | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | N112:77
Nel_K2_LIME_DAY_NEW | $System |  | TONS | 1400 | 0 | 0 | 0 | PLC_INTREAD | F27:43
NEL_K2_LIME_DAYLY | $System |  | "WC | 2500 | 0 | 0 | 0 | PLC_INTREAD | F27:33
NEL_K2_LIME_PRODUCED | $System |  | "WC | 1200 | 0 | 0 | 0 | PLC_INTREAD | N112:77
NEL_K2_REJECT_JUNK | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | F27:57
NEL_K2_REJECT_SILO3 | $System |  | TONS | 1200 | 0 | 0 | 0 | PLC_INTREAD | F27:59
NEL_K2_STONE_TOT | $System |  | "WC | 2500 | 0 | 0 | 0 | PLC_INTREAD | F27:45
NEL_K2_STONE_TOT_KILN | $System |  | TONS | 2500 | 0 | 0 | 0 | PLC_INTREAD | F27:47
NEL_K2_TONS_STONE_STK | $System |  | TONS | 1 | 0 | 0 | 0 | PLC_INTREAD | F27:41
NEL_K2_TONS_STONE_STK_live | $System |  | TONS | 1 | 0 | 0 | 0 | PLC_INTREAD | F27:40
NEL_KN1_APC_Master_PB | $System | Kiln 1 APC Master HMI Pushbutton | None | USCNEL101 | NEL_KN1_APC_Master_PB
NEL_KN1_FH1309_FT_PID_SPT | $System |  | None | 1
NEL_KN1_FH1309_PT_AVG | $System | Kiln 1 Hood Draft Pressure | in/H20 | 2 | 0 | 0 | -2 | USCNEL101 | NEL_KN1_FH1309_PT_AVG | KILN 1 PERCENT OXYGEN
NEL_KN1_FH1309_PT_IND | $System | Kiln 1 Hood Draft Pressure Indication | in/H20 | 2 | 0 | 0 | -2 | USCNEL101 | NEL_KN1_FH1309_PT.IND | KILN 1 PERCENT OXYGEN
NEL_KN1_FH1309_PT_PID_MAXO | $System | K1 ID Fan Speed/Hood Draft PID Max Output | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | n80:11 | KILN 1 PERCENT OXYGEN
NEL_KN1_FH1309_PT_PID_MINO | $System | K1 ID Fan Speed/Hood Draft PID Min Output | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | n80:12 | KILN 1 PERCENT OXYGEN
NEL_KN1_FH1309_PT_PID_SEL_HMI | $System | K1 ID Fan Speed/Hood Draft APC HMI Auto Selector | None | USCNEL101 | NEL_KN1_FH1309_PT.PID_SEL_HMI | PH 2-305 START STROKE RAMP UP
NEL_KN1_FH1309_PT_PID_SSA_HMI | $System | K1 ID Fan Speed/Hood Draft PID HMI Auto Selector | None | USCNEL101 | NEL_KN1_FH1309_PT.PID_SSA_HMI | PH 2-305 START STROKE RAMP UP
NEL_KN1_FH1309_PT_SPT | $System | K1 ID Fan Speed/Hood Draft PID Setpoint | in/H20 | 2 | 0 | 0 | -2 | PLC_FLTWRITE | f71:4 | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1312_FT_IND | $System | #1 Cooler Fan Air Flow Indication | ACFM | 50000 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1312_FT.IND | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1312_FT_PID_MAXO | $System | K1 Cooler Fan Speed/Air Flow PID Max Output | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1312_FT.PID_MAXO | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1312_FT_PID_MINO | $System | K1 Cooler Fan Speed/Air Flow PID Min Output | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1312_FT.PID_MINO | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1312_FT_PID_SEL_HMI | $System | K1 Cooler Fan Speed/Air Flow APC HMI Auto Selector | None | USCNEL101 | NEL_KN1_FN1312_FT.PID_SEL_HMI
NEL_KN1_FN1312_FT_PID_SPT | $System | Cooler Air Fan Speed/Air Flow PID Setpoint | SCFM | 50000 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1312_FT.PID_SPT | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1312_FT_PID_SSA_HMI | $System | K1 Cooler Fan Speed/Air Flow PID HMI Auto Selector | None | USCNEL101 | NEL_KN1_FN1312_FT.PID_SSA_HMI
NEL_KN1_FN1312_FT_SPT | $System | K1 Cooler Air Fan Setpoint | % | 50000 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1312_FT.SPT | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1312_ST_SPT | $System | #1 Cooler Fan Speed Setpoint | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1312_ST.SPT | KILN 1 PERCENT OXYGEN
NEL_KN1_FN1314_ST_SPT | $System | #1 ID Fan Speed Indication | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_FN1314_ST.SPT | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_AT_CO_PID_SSA_HMI | $System |  | Off | USCNEL101 | NEL_KN1_KN1308_AT_CO.PID_SSA_HMI | KD 2-308-A Drive Alarm!
NEL_KN1_KN1308_AT_O2_IND | $System | Kiln 1 O2 Indication | % | 22.8 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_KN1308_AT_O2.IND | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_AT_O2_PID_MAXO | $System | K1 Cooler Air Flow/O2 PID Max Output | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_KN1308_AT_O2.PID_MAXO | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_AT_O2_PID_MINO | $System | K1 Cooler Air Flow/O2 PID Min Output | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_KN1308_AT_O2.PID_MINO | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_AT_O2_PID_SEL_HMI | $System | K1 Cooler Air Flow/O2 APC HMI Selector | None | USCNEL101 | NEL_KN1_KN1308_AT_O2.PID_SEL_HMI
NEL_KN1_KN1308_AT_O2_PID_SSA_HMI | $System | K1 Cooler Air Flow/O2 PID HMI Auto Selector | None | USCNEL101 | NEL_KN1_KN1308_AT_O2.PID_SSA_HMI
NEL_KN1_KN1308_AT_O2_SPT | $System | Kiln 1 Cooler Air Flow/O2 PID SPT | % | 22.8 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_KN1308_AT_O2.SPT | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_FT_IND | $System |  | ACFM | 50000 | 0 | 0 | 0 | USCNEL202 | NEL_KN1_KN1308_FT.IND | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_FT_PID_MAXO | $System |  | ACFM | 50000 | 0 | 0 | 0 | USCNEL202 | NEL_KN1_KN1308_FT_PID_MAXO | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_FT_PID_MINO | $System |  | ACFM | 50000 | 0 | 0 | 0 | USCNEL202 | NEL_KN1_KN1308_FT.PID_MINO | KILN 1 PERCENT OXYGEN
NEL_KN1_KN1308_FT_PID_SEL_HMI | $System |  | None | USCNEL101 | NEL_KN1_KN1308_FT.PID_SEL_HMI | PH 2-305 START STROKE RAMP UP
NEL_KN1_KN1308_FT_PID_SSA_HMI | $System |  | None | USCNEL101 | NEL_KN1_KN1308_FT.PID_SSA_HMI | PH 2-305 START STROKE RAMP UP
NEL_KN1_KN1308_FT_SPT | $System |  | ACFM | 50000 | 0 | 0 | 0 | USCNEL202 | NEL_KN1_KN1308_FT_SPT | KILN 1 PERCENT OXYGEN
NEL_KN1_OPTICAL_PYO_DAM | $System |  | HZ | 2552 | 0 | 0 | 1112 | PLC_INTREAD | N38:14 | KILN 1 PERCENT OXYGEN
NEL_KN1_OPTICAL_PYO_FLAME | $System |  | HZ | 4532 | 0 | 0 | 1472 | PLC_INTREAD | N38:15 | KILN 1 PERCENT OXYGEN
NEL_KN1_RA1317A_SS_BYPASS | $System |  | None | KILN1_BH_WRITE | NEL_KN1_RA1317A_SS_BYPASS
NEL_KN1_RACK_DOOR | $System |  | None | PLC_DISCREAD | B100/70
NEL_KN1_W1601_QT_SPT | $System |  | TPH | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_W1601_QT.SPT
NEL_KN1_WF1601_COAL_QT_SPT | $System |  | % | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_COAL_QT_SPT
NEL_KN1_WF1601_COKE_QT_SPT | $System |  | % | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_COKE_QT_SPT
NEL_KN1_WF1601_QT_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT_DAY
NEL_KN1_WF1601_QT_PERCENT | $System |  | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT_PERCENT
NEL_KN1_WF1601_QT_PID_SEL_HMI | $System | K1 Fuel APC HMI Selector | None | USCNEL101 | NEL_KN1_WF1601_QT.PID_SEL_HMI | PH 2-305 START STROKE RAMP UP
NEL_KN1_WF1601_QT_PID_SSA_HMI | $System |  | Off | USCNEL101 | NEL_KN1_WF1601_QT.PID_SSA_HMI | KD 2-308-A Drive Alarm!
NEL_KN1_WF1601_SPT_ENTER | $System |  | Off | USCNEL101 | NEL_KN1_WF1601_SPT_ENTER | KD 2-308-A Drive Alarm!
NEL_KN1_WF1601_TOTAL_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_TOTAL_DAY
NEL_KN1_WF1601_TOTAL_SPT | $System |  | % | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_TOTAL_SPT
NEL_KN1_WF1601_TOTAL_TPH | $System |  | % | 22.8 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_TOTAL_TPH | KILN 1 PERCENT OXYGEN
NEL_KN1_WF1601A_COKE_QT_SPT | $System |  | % | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601A_COKE_QT_SPT
NEL_KN1_WF1601A_QT_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601A_QT_DAY
NEL_KN1_WF1601A_QT_PID_SSA_HMI | $System |  | Off | USCNEL101 | NEL_KN1_WF1601A_QT.PID_SSA_HMI | KD 2-308-A Drive Alarm!
NEL_KN1_WF2601_QT_PERCENT_COKE | $System |  | % | 100 | 0 | 0 | 0 | USCNEL202 | NEL_KN1_WF2601_QT_PERCENT_COKE
NEL_KN2_FH2309_PT_PID_SEL_HMI | $System |  | None | USCNEL202 | NEL_KN2_FH2309_PT.PID_SEL_HMI
NEL_KN2_KD2308_E_STOP | $System | KILN 2 DRIVE E STOP | Off | USCNEL202 | NEL_KN2_KD2308_E_STOP | KILN 2 DRIVE E STOP
NEL_KN2_KD2308_PONYBOX_LIMIT_SW | $System |  | Off | USCNEL202 | NEL_KN2_KD2308_PONYBOX_LIMIT_SW | KILN 2 DRIVE PONYBOX OPEN
NEL_KN2_KN2308_AT_CO_PID_SO | $System |  | SEC | 15 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_KN2308_AT_CO.PID.SO | FN 2-312 AMPS
NEL_KN2_UREA_APC_AUTO_HMI | $System |  | None | USCNEL202 | NEL_KN2_UREA_APC_AUTO_HMI
NEL_KN2_UREA_APC_GPM_SPT | $System |  | in h2o | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_UREA_APC_GPM_SPT | Dust Bin Level
NEL_KN2_WF2601_FTS | $System |  | On | USCNEL202 | NEL_KN2_WF2601.FTS | WF2601 FAILED TO START
NEL_KN2_WF2601_IT_Percent | $System |  | % Amps | 9999 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_IT.PCT
NEL_KN2_WF2601_PBE | $System |  | None | USCNEL202 | NEL_KN2_WF2601.PBE
NEL_KN2_WF2601_PBS | $System |  | None | USCNEL202 | NEL_KN2_WF2601.PBS
NEL_KN2_WF2601_QT_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT_DAY
NEL_KN2_WF2601_QT_PERCENT | $System |  | TPH | 100 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT_PERCENT
NEL_KN2_WF2601_QT_PERCENT_COKE | $System |  | % | 100 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT_PERCENT_COKE
NEL_KN2_WF2601_QT_PID_SEL_HMI | $System |  | None | USCNEL202 | NEL_KN2_WF2601_QT.PID_SEL_HMI
NEL_KN2_WF2601_QT_PID_SSA_HMI | $System |  | Off | USCNEL202 | NEL_KN2_WF2601_QT.PID_SSA_HMI | WF2601A PID AUTO/MAN
NEL_KN2_WF2601_QT_RATIO | $System |  | TPH | 100 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT_RATIO
NEL_KN2_WF2601_QT_SPT | $System |  | TPH | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN2_WF2601_QT.SPT
NEL_KN2_WF2601_QT_TOT | $System |  | Tons | 10000 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT.TOT
NEL_KN2_WF2601_QT_TOT_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT_TOT_DAY
NEL_KN2_WF2601_QT_TOTAL_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT_TOTAL_DAY
NEL_KN2_WF2601_TOTAL_SPT | $System |  | % | 15 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_TOTAL_SPT
NEL_KN2_WF2601A_COAL_QT_SPT | $System |  | % | 15 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_COAL_QT_SPT
NEL_KN2_WF2601A_QT_DAY | $System |  | TONS | 9999 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT_DAY
NEL_KN2_WF2601A_QT_PID_SSA_HMI | $System |  | Off | USCNEL202 | NEL_KN2_WF2601A_QT.PID_SSA_HMI | WF2601A PID AUTO/MAN
NEL_LKD_DG460_HMI_SELECT | $System |  | None | PLC_DISCREAD | B3:97/0 | FN 4462 AUX FDBK
NEL_LKD_DG460_OPEN | $System |  | None | PLC_DISCREAD | I:23/2 | FN 4462 AUX FDBK
NEL_LKD_DR460_COIL | $System |  | None | PLC_DISCREAD | O:24/0 | FN 4462 AUX FDBK
NEL_LKD_DUST_SCALE_IND | $System |  | LBS. | 300000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_LKD_DUST_SCALE_IND | 2
NEL_PH1_PH2305_ST_PID_SEL_HMI | $System |  | None | 1
NEL_PH2_PH2305_ST_PID_SEL_HMI | $System |  | Off | USCNEL202 | NEL_PH2_PH2305_ST.PID_SEL_HMI
NEL_S1A_WF433_1A_AUX | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.AUX
NEL_S1A_WF433_1A_FTS_ALM | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.FLT
NEL_S1A_WF433_1A_IT_PCT | $System |  | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_S1A_WF433_1A_IT.PCT
NEL_S1A_WF433_1A_PBE_HMI | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.PBE_HMI
NEL_S1A_WF433_1A_PBS_HMI | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.PBS_HMI
NEL_S1A_WF433_1A_QT_IND | $System |  | TPH | 5 | 0 | 0 | 0 | USCNEL101 | NEL_S1A_WF433_1A_QT.IND
NEL_S1A_WF433_1A_QT_SPT | $System |  | TPH | 5 | 0 | 0 | 0 | USCNEL101 | NEL_S1A_WF433_1A_QT.SPT
NEL_S1A_WF433_1A_SSA | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.SSA_HMI
NEL_S1A_WF433_1A_ST_IND | $System | WF433 VFD % Speed Actual (100 = 60 Hz) | % | 100 | 0 | 0 | 0 | USCNEL101 | NEL_S1A_WF433_1A_ST.IND
NEL_SNCR_FA0001_IND | $System |  | On | USCNEL207 | NEL_SNCR_FA0001.IND | SNCR UREA FIRE ALARM
NEL_WF_433_1A_AUX | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.AUX
NEL_WF_433_1A_PLOCK | $System |  | Off | USCNEL101 | NEL_S1A_WF433_1A.PLOCK
NEL_WF_433_1A_QT_IND | $System |  | TPH | 5 | 0 | 0 | 0 | USCNEL101 | NEL_WF_433_1A_QT.IND
NEL_WF_433_1A_QT_SPT | $System |  | TPH | 5 | 0 | 0 | 0 | USCNEL101 | NEL_WF_433_1A_QT.SPT | FN 2-312 AMPS
NEL_WF_433_1A_WEIGHT_QT | $System |  | TPH | 5 | 0 | 0 | 0 | PLC_FLTREAD | F9:481 | FN 2-312 AMPS
NEL_WF_433_1A_WEIGHT_QT_SPT | $System |  | TPH | 5 | 0 | 0 | 0 | USCNEL101 | NEL_WF_433_1A_WEIGHT_QT_SPT | FN 2-312 AMPS
NEL_WF433_1A_AUX | $System |  | Off | USCNEL101 | NEL_WF433_1A.AUX
NEL_WF433_1A_PBE_HMI | $System |  | Off | USCNEL101 | NEL_WF433_1A.PBE_HMI
NEL_WF433_1A_QT_IND | $System |  | TPH | 5 | 0 | 0 | 0 | USCNEL101 | NEL_WF433_1A_QT.IND
NEL580_LASTCOMM | $System | COUNTER TO CHECK PLC 580E COMMS | sec | 32000 | 10 | 0 | LOST COMMUNICATION WITH KILN PLC!! | 0 | 0 | 0
NEL580_NEL1COMM | $System | BIT TXFR FROM NEL580 TO NELSON 1 TO CHECK COMMS | None | PLC_ALARM | B3/742
NEL580_NEL1NOTCOMM | $System | NELSON 1 IS NOT COMMUNICATING WITH KILN PLC!! | On | PLC_ALARM | B101/145 | NELSON 1 IS NOT COMMUNICATING WITH KILN PLC!!
NEL580_NEL2COMM | $System | BIT TXFR FROM NEL580 TO NELSON 2 TO CHECK COMMS | None | PLC_ALARM | B3/951
NEL580_NEL2NOTCOMM | $System | NELSON 2 IS NOT COMMUNICATING WITH KILN PLC!! | On | PLC_ALARM | B101/161 | NELSON 2 IS NOT COMMUNICATING WITH KILN PLC!!
NEL580_NEL3COMM | $System | BIT TXFR FROM NEL580 TO NELSON 3 TO CHECK COMMS | None | PLC_ALARM | B3/953
NEL580_NEL3NOTCOMM | $System | NELSON 3 IS NOT COMMUNICATING WITH KILN PLC!! | On | PLC_ALARM | B101/535 | NELSON 3 IS NOT COMMUNICATING WITH KILN PLC!!
NEL580_NEL4COMM | $System | BIT TXFR FROM NEL580 TO NELSON 4 TO CHECK COMMS | None | PLC_ALARM | B3/965
NEL580_NEL4NOTCOMM | $System | NELSON 4 IS NOT COMMUNICATING WITH KILN PLC!! | On | PLC_ALARM | B101/555 | NELSON 4 IS NOT COMMUNICATING WITH KILN PLC!!
NodeName | $System
NotUsedAnalog | $System | Not Used |  | 100 | 0 | 0 | Hours of Operation, 1st Shift | 0 | 0 | 0
NotUsedDiscrete | $System | Not Used | None | 0
O2_COOLING_TK | $System |  | % | 250 | 0 | 0 | 0 | HYD_INTREAD | N58:1 | KILN 1 PERCENT OXYGEN
O2_COOLOING_TK_AH | $System |  | Off | PLC_DISCREAD | I:23/5 | KILN 2 02 HIGH LEVEL
O2_COOLOING_TK_AL | $System |  | Off | PLC_DISCREAD | I:23/4 | KILN 2 02 LOW LEVEL
PEN#_1 | $System | Historical Pen #1 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #1 Decimal Places to Show | 0 | 0 | 0
PEN#_2 | $System | Historical Pen #2 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #2 Decimal Places to Show | 0 | 0 | 0
PEN#_3 | $System | Historical Pen #3 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #3 Decimal Places to Show | 0 | 0 | 0
PEN#_4 | $System | Historical Pen #4 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #4 Decimal Places to Show | 0 | 0 | 0
PEN#_5 | $System | Historical Pen #5 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #5 Decimal Places to Show | 0 | 0 | 0
PEN#_6 | $System | Historical Pen #6 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #6 Decimal Places to Show | 0 | 0 | 0
PEN#_7 | $System | Historical Pen #7 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #7 Decimal Places to Show | 0 | 0 | 0
PEN#_8 | $System | Historical Pen #8 Decimal Places to Show |  | 5 | 0 | 0 | Historical Pen #8 Decimal Places to Show | 0 | 0 | 0
Pen#01 | $System
Pen#02 | $System
Pen#03 | $System
Pen#04 | $System
Pen#05 | $System
Pen#06 | $System
Pen#07 | $System
Pen#08 | $System
Pen01 | $System | HISTORICAL TREND PEN #1
Pen02 | $System | HISTORICAL TREND PEN #2
Pen03 | $System | HISTORICAL TREND PEN #3
Pen04 | $System | HISTORICAL TREND PEN #4
Pen05 | $System | HISTORICAL TREND #2 PEN #1
Pen06 | $System | HISTORICAL TREND #2 PEN #2
Pen07 | $System | HISTORICAL TREND #2 PEN #3
Pen08 | $System | HISTORICAL TREND #2 PEN #4
RA23110FTS_ALM | $System |  | None | 0
RA23139MSF_BYP | $System |  | None | 0
range1 | $System | HISTORICAL TREND #1 PEN #1 TREND RANGE
range2 | $System | HIST TREND RANGE FOR PEN 2
range3 | $System | HIST TREND RANGE FOR PEN 3
range4 | $System | HIST TREND RANGE FOR PEN 4
range5 | $System | HISTORICAL TREND #2 PEN #1 TREND RANGE
range6 | $System | HISTORICAL TREND #2 PEN #2 TREND RANGE
range7 | $System | HISTORICAL TREND #2 PEN #3 TREND RANGE
range8 | $System | HISTORICAL TREND #2 PEN #4 TREND RANGE
RINGRING | $System | Notification | None | 0
SEC_COUNTER | $System | Security counter. |  | 1000 | 0 | 0 |  | 0 | 0 | 0
SEC_FACEPLATE | $System | Faceplate operator security. | None | 0
SEC_LEADMAN | $System | Leadman access granted. | None | 0
SEC_LOADOUT | $System | Loadout access granted. | None | 0
SEC_LOADOUT_MANAGER | $System | Loadout Manager access granted. | None | 0
SEC_PLANT_MANAGER | $System | Plant Manager access granted. | None | 0
SEC_PRODUCTION | $System | Production access granted. | None | 0
SEC_PRODUCTION_MANAGER | $System | Production Manager access granted. | None | 0
SEC_QUALITY | $System | Quality access granted. | None | 0
SEC_QUALITY_MANAGER | $System | Quality Manager access granted. | None | 0
SEC_QUARRY | $System | Quarry access granted. | None | 0
SEC_QUARRY_MANAGER | $System | Quarry Manager access granted. | None | 0
SEC-PLC | $System | PLC TIME - SEC | SEC | 60 | 1 | 0 | 0 | PLC_INTREAD | S:23 | PLC TIME - HOUR
SILO_1_4_2A_MEASTON | $System |  | % | 10000 | 0 | 0 | 0 | PLC_FLTREAD | F9:301 | FN 2-314 AMPS
SILO_1A_MEASTON | $System |  | % | 10000 | 0 | 0 | 0 | PLC_FLTREAD | F9:302 | FN 2-314 AMPS
SILO_1A_SCREWS_AUX | $System |  | Off | PLC_DISCREAD | I:231/1
SILO_1A_SCREWS_PLOCK | $System |  | Off | USCNEL101 | SILO_1A_SCREWS.PLOCK
SILO_1A_WF433_1A_INTERLOCK | $System |  | Off | USCNEL101 | SILO_1A_WF433_1A_INTERLOCK
SILO_LIME_MEASTON | $System |  | % | 10000 | 0 | 0 | 0 | PLC_FLTREAD | F9:303 | FN 2-314 AMPS
SILO_TOT_2_5_3A_MEASTON | $System |  | % | 10000 | 0 | 0 | 0 | PLC_FLTREAD | F9:300 | FN 2-314 AMPS
SPARE | $System | SPARE TAG |  | 1 | 3 | 0 | SPARE TAG | 0 | 0 | 0
Stone_Feed | $System |  | 0
title1 | $System | HISTORICAL TREND #1 PEN #1 TRENDED TAG
title2 | $System | HIST TREND PEN 2 TIITLE
title3 | $System | HIST TREND PEN 3 TITLE
title4 | $System | HIST TREND PEN 4 TITLE
title5 | $System | HISTORICAL TREND #2 PEN #1 TRENDED TAG
title6 | $System | HISTORICAL TREND #2 PEN #2 TRENDED TAG
title7 | $System | HISTORICAL TREND #2 PEN #3 TRENDED TAG
title8 | $System | HISTORICAL TREND #2 PEN #4 TRENDED TAG
units1 | $System | HISTORICAL TREND #1 PEN #1 ENG. UNITS
units2 | $System | HIST TREND - ENGINEERING UNITS FOR PEN 2
units3 | $System | HIST TREND - ENGINEERING UNITS FOR PEN 3
units4 | $System | HIST TREND - ENGINEERING UNITS FOR PEN 4
units5 | $System | HISTORICAL TREND #2 PEN #1 ENG. UNITS
units6 | $System | HISTORICAL TREND #2 PEN #2 ENG. UNITS
units7 | $System | HISTORICAL TREND #2 PEN #3 ENG. UNITS
units8 | $System | HISTORICAL TREND #2 PEN #4 ENG. UNITS
val1 | $System | HISTORICAL TREND #1 PEN #1 INST. VALUE |  | 9999 | 0 | 0 | HISTORICAL TREND #1 PEN #1 INST. VALUE | 0 | 0 | 0
val2 | $System | HIST TREND INSTANTANEOUS VALUE FOR PEN 2 |  | 5 | 0 | 0 | HIST TREND INSTANTANEOUS VALUE FOR PEN 2 | 0 | 0 | 0
val3 | $System | HIST TREND INSTANTANEOUS VALUE FOR PEN 3 |  | 5 | 0 | 0 | HIST TREND INSTANTANEOUS VALUE FOR PEN 3 | 0 | 0 | 0
val4 | $System | HIST TREND PEN #4 INSTANTANEOUS VALUE |  | 5 | 0 | 0 | HIST TREND PEN #4 INSTANTANEOUS VALUE | 0 | 0 | 0
val5 | $System | HISTORICAL TREND #2 PEN #1 INST. VALUE |  | 9999 | 0 | 0 | HISTORICAL TREND #2 PEN #1 INST. VALUE | 0 | 0 | 0
val6 | $System | HISTORICAL TREND #2 PEN #2 INST. VALUE |  | 5 | 0 | 0 | HISTORICAL TREND #2 PEN #2 INST. VALUE | 0 | 0 | 0
val7 | $System | HISTORICAL TREND #2 PEN #3 INST. VAL |  | 5 | 0 | 0 | HISTORICAL TREND #2 PEN #3 INST. VAL | 0 | 0 | 0
val8 | $System | HISTORICAL TREND #2 PEN #4 INST. VALUE |  | 5 | 0 | 0 | HISTORICAL TREND #2 PEN #4 INST. VALUE | 0 | 0 | 0
vega_silo_1 | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1_6 | 300001 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_1a | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1A_3A | 300001 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_2 | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1_6 | 300003 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_2a | $System |  | TONS | 32000 | 0 | 0 | 0 | VEGA_SILO_1A_3A | 300003 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_3 | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1_6 | 300005 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_3a | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1A_3A | 300005 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_4 | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1_6 | 300007 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_5 | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1_6 | 300009 | KILN 2 COAL TOTALIZER - DAILY
vega_silo_6 | $System |  | % | 10000 | 0 | 0 | 0 | VEGA_SILO_1_6 | 300011 | KILN 2 COAL TOTALIZER - DAILY
WEBPAGE | $System
Window | $System
WWDepartment | $System
WWNameNodeDDE | $System
WWNameNodeLocal | $System
XXX_AG0000_AUX | $System |  | None | 0
XXX_AG0000_FTS_ALM | $System |  | None | 0
XXX_AG0000_PBE_HMI | $System |  | None | 0
XXX_AG0000_PBS_HMI | $System |  | None | 0
XXX_AG0000_RDY | $System |  | None | 0
XXX_AG0000_RT_HRS | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_AG0000_RT_RST | $System |  | None | 0
XXX_AG0000_SS_ALM | $System |  | None | 0
XXX_AG0000_SS_BYP | $System |  | None | 0
XXX_AG0000_SS_BYP_PB | $System |  | None | 0
XXX_AG0000_SSA_HMI | $System |  | None | 0
XXX_DC0000_CO_PPM_AHH | $System |  | None | 0
XXX_DC0000_DP_WC_AH | $System |  | None | 0
XXX_DC0000_LSH_ALM_SD | $System |  | None | 0
XXX_DC0000_OP_PCT_AHH | $System |  | None | 0
XXX_DC0000_TT_DEGF_AHH | $System |  | None | 0
XXX_DD9999_SV1 | $System |  | None | 0
XXX_DD9999_SV1_ZSC | $System |  | None | 0
XXX_DD9999_SV1_ZSO | $System |  | None | 0
XXX_DD9999_SV2 | $System |  | None | 0
XXX_DD9999_SV2_ZSC | $System |  | None | 0
XXX_DD9999_SV2_ZSO | $System |  | None | 0
XXX_DG0000_ALM | $System |  | None | 0
XXX_DG0000_SEL_HMI | $System |  | None | 0
XXX_DG0000_ZSE | $System |  | None | 0
XXX_DG0000_ZSE_ALM | $System | Extending alarm. | None | 0
XXX_DG0000_ZSR | $System |  | None | 0
XXX_DG0000_ZSR_ALM | $System | Retracting alarm. | None | 0
XXX_FN0000_AUX | $System |  | None | 0
XXX_FN0000_FTS_ALM | $System |  | None | 0
XXX_FN0000_IT_PCT | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_FN0000_PBE_HMI | $System |  | None | 0
XXX_FN0000_PBS_HMI | $System |  | None | 0
XXX_FN0000_RDY | $System |  | None | 0
XXX_FN0000_RT_HRS | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_FN0000_RT_RST | $System |  | None | 0
XXX_FN0000_SS_ALM | $System |  | None | 0
XXX_FN0000_SS_BYP | $System |  | None | 0
XXX_FN0000_SS_BYP_PB | $System |  | None | 0
XXX_FN0000_SSA_HMI | $System |  | None | 0
XXX_FN0000_VFD_SI | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_FN0000_VFD_SPT | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_RV0000_AUX | $System |  | None | 0
XXX_RV0000_FTS_ALM | $System |  | None | 0
XXX_RV0000_PBE_HMI | $System |  | None | 0
XXX_RV0000_PBS_HMI | $System |  | None | 0
XXX_RV0000_RDY | $System |  | None | 0
XXX_RV0000_RT_HRS | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_RV0000_RT_RST | $System |  | None | 0
XXX_RV0000_SPT | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_RV0000_SS_ALM | $System |  | None | 0
XXX_RV0000_SS_BYP | $System |  | None | 0
XXX_RV0000_SS_BYP_PB | $System |  | None | 0
XXX_RV0000_SSA_HMI | $System |  | None | 0
XXX_RV0000_SSF_HMI | $System |  | None | 0
XXX_RV0000_VFD_SI | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_RV0000_VFD_SPT | $System |  |  | 100 | 0 | 0 |  | 0 | 0 | 0
XXX_SG0000_SEL_HMI | $System |  | None | 0
XXX_SG0000_ZS_ALM | $System |  | None | 0
XXX_SG0000_ZSC | $System |  | None | 0
XXX_SG0000_ZSC_ALM | $System |  | None | 0
XXX_SG0000_ZSO | $System |  | None | 0
XXX_SG0000_ZSO_ALM | $System |  | None | 0
VEGA_SILO_1A_3A | \\10.70.64.236\DASMBTCP | VEGA_SILO_1A_3A
APEX_BULK | \\10.97.100.224\DASABCIP | APEX_BULK | 10 | 10
HYD_ALARM | \\10.97.100.224\DASABCIP | HYD_ALARM | 10 | 10
HYD_DISCREAD | \\10.97.100.224\DASABCIP | HYD_DISCREAD | 10 | 10
HYD_DISCWRITE | \\10.97.100.224\DASABCIP | HYD_DISCWRITE | 10 | 10
HYD_FLTREAD | \\10.97.100.224\DASABCIP | HYD_FLTREAD | 10 | 10
HYD_FLTWRITE | \\10.97.100.224\DASABCIP | HYD_FLTWRITE | 10 | 10
HYD_INTREAD | \\10.97.100.224\DASABCIP | HYD_INTREAD | 10 | 10
HYD_INTWRITE | \\10.97.100.224\DASABCIP | HYD_INTWRITE | 10 | 10
KILN1_BH_ALARM | \\10.97.100.224\DASABCIP | KILN1_BH_ALARM | 0 | 0
KILN1_BH_READ | \\10.97.100.224\DASABCIP | KILN1_BH_READ | 0 | 0
KILN1_BH_WRITE | \\10.97.100.224\DASABCIP | KILN1_BH_WRITE | 0 | 0
USCNEL051 | \\10.97.100.224\DASABCIP | USCNEL051 | 0 | 0
USCNEL101 | \\10.97.100.224\DASABCIP | USCNEL101 | 0 | 0
USCNEL202 | \\10.97.100.224\DASABCIP | USCNEL202 | 0 | 0
USCNEL207 | \\10.97.100.224\DASABCIP | USCNEL207 | 0 | 0
PLC_ALARM | \\10.97.100.224\DASABTCP | PLC_ALARM | 5 | 5
PLC_DISCREAD | \\10.97.100.224\DASABTCP | PLC_DISCREAD | 5 | 5
PLC_DISCWRITE | \\10.97.100.224\DASABTCP | PLC_DISCWRITE | 5 | 5
PLC_FLTREAD | \\10.97.100.224\DASABTCP | PLC_FLTREAD | 5 | 5
PLC_FLTWRITE | \\10.97.100.224\DASABTCP | PLC_FLTWRITE | 5 | 5
PLC_INTREAD | \\10.97.100.224\DASABTCP | PLC_INTREAD | 5 | 5
PLC_INTWRITE | \\10.97.100.224\DASABTCP | PLC_INTWRITE | 5 | 5
VEGA_SILO_1_6 | \\10.97.100.224\DASMBTCP | VEGA_SILO_1_6 | 0 | 0
OPC | \\localhost\FSGateway | OPC_DeviceGroup
Galaxy | \\NA\NA | NA
BACKAUTOSHTDWN_ALM | Back_System | BACK SYSTEM AUTO SHUTDOWN IN 5 MIN | On | PLC_ALARM | B101:8/0 | BACK SYSTEM AUTO SHUTDOWN IN 5 MIN
BACKAUTOSHTDWN_PCRESET | Back_System | PC STOP BACK SYSTEM AUTO SHUTDOWN | On | PLC_ALARM | B100:3/12 | PC STOP BACK SYSTEM AUTO SHUTDOWN
BACKSYSJUNK_ALM | Back_System | BACK SYSTEM JUNKING | On | PLC_ALARM | I:120/03 | BACK SYSTEM JUNKING
BC4401_AUTO | Back_System | BC 4401 IN AUTO POSITION | None | PLC_DISCREAD | I:100/00 | BC 4401 IN AUTO POSITION
BC4401_BYP | Back_System | BC 4401 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/151 | BC 4401 MOTION SWITCH BYPASS
BC4401_DISCONNECT | Back_System | BC 401 DISCONNECT | None | PLC_DISCREAD | I:122/00 | BC 401 DISCONNECT
BC4401_FS | Back_System | BC 4401 FIELD STOP | None | PLC_DISCREAD | I:122/02 | BC 4401 FIELD STOP
BC4401_IM | Back_System | BC 401 INTERLOCKS MET | None | PLC_DISCREAD | B3/29 | BC 401 INTERLOCKS MET
BC4401_OVERLOADS | Back_System | BC 401 OVERLOADS | None | PLC_DISCREAD | I:100/02 | BC 401 OVERLOADS
BC4401_PBS | Back_System | BC 4401 PC START | None | PLC_DISCWRITE | B100/128 | BC 4401 PC START
BC4401_PBT | Back_System | BC 4401 PC STOP | None | PLC_DISCWRITE | B100/129 | BC 4401 PC STOP
BC4401_TT | Back_System | BC 401 TEMPERATURE | °F | 800 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:14 | BC 401 TEMPERATURE
BC4401BIN_ALM | Back_System | BC 401 BUTTERFLY BINDICATOR STOPPED | On | PLC_ALARM | I:121/14 | BC 401 BUTTERFLY BINDICATOR STOPPED
BC4401FTS_ALM | Back_System | BC 4401 FAILED TO START! | On | PLC_ALARM | B101/373 | BC 4401 FAILED TO START!
BC4401HITEMP_ALM | Back_System | BC 401 TEMP > 600 F | On | PLC_ALARM | B101/486 | BC 401 TEMP > 600 F
BC4401MS_X | Back_System | BC 4401 AUX FDBK | Off | PLC_DISCREAD | I:100/01 | BC 401 STOPPED
BC4401MSF_ALM | Back_System | BC 4401 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/374 | BC 4401 MOTION SWITCH FAILURE!
BC4402_AUTO | Back_System | BC 402 IN AUTO POSITION | None | PLC_DISCREAD | I:104/11 | BC 402 IN AUTO POSITION
BC4402_BYP | Back_System | BC 402 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/219 | BC 402 MOTION SWITCH BYPASS
BC4402_DEC | Back_System | BC 402 DECREASE VFD SPEED SETPOINT | None | PLC_DISCWRITE | B100/221 | BC 402 DECREASE VFD SPEED SETPOINT
BC4402_DIR | Back_System | BC 402 DIRECTION 0=HM 402-2 1=SC 411 | None | PLC_DISCWRITE | B100:0/15 | BC 402 DIRECTION 0=HM 402-2 1=SC 411
BC4402_DISCONNECT | Back_System | BC 402 DISCONNECT | None | PLC_DISCREAD | I:130/00 | BC 402 DISCONNECT
BC4402_FS | Back_System | BC 402 FIELD STOP | None | PLC_DISCREAD | I:130/02 | BC 402 FIELD STOP
BC4402_IM | Back_System | BC 402 INTERLOCKS MET | None | PLC_DISCREAD | B3/53 | BC 402 INTERLOCKS MET
BC4402_INC | Back_System | BC 402 INCREASE VFD SPEED SETPOINT | None | PLC_DISCWRITE | B100/220 | BC 402 INCREASE VFD SPEED SETPOINT
BC4402_OVERLOADS | Back_System | BC 402 OVERLOADS | None | PLC_DISCREAD | I:104/13 | BC 402 OVERLOADS
BC4402_PBS | Back_System | BC 4402 PC START | None | PLC_DISCWRITE | B100/107 | BC 4402 PC START
BC4402_PBT | Back_System | BC 4402 PC STOP | None | PLC_DISCWRITE | B100/119 | BC 4402 PC STOP
BC4402_SPD | Back_System | BC 402 VFD SPEED % | % | 100 | 0.2 | 0 | 0 | PLC_FLTWRITE | F27:13 | BC 402 VFD SPEED %
BC4402_ST | Back_System | BC 402 BELT VFD PERCENT LOAD | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F27:15 | BC 402 BELT VFD PERCENT LOAD
BC4402FAULT_ALM | Back_System | BC 402 VFD FAULT | On | PLC_ALARM | I:104/13 | BC 402 VFD FAULT
BC4402FTS_ALM | Back_System | BC 402 FAILED TO START | On | PLC_ALARM | B101/375 | BC 402 FAILED TO START
BC4402MS_X | Back_System | BC 4402 AUX FDBK | Off | PLC_DISCREAD | I:104/12 | BC 402 STOPPED
BC4402MSF_ALM | Back_System | BC 402 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/376 | BC 402 MOTION SWITCH FAILURE
BE4403_AUTO | Back_System | BE 4403 IN AUTO | None | PLC_DISCREAD | I:100/3 | BE 4403 IN AUTO
BE4403_BYP | Back_System | BE 403 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/158 | BE 403 MOTION SWITCH BYPASSED
BE4403_DISCONNECT | Back_System | BE 403 DISCONNECT | None | PLC_DISCREAD | I:122/04 | BE 403 DISCONNECT
BE4403_FS | Back_System | BE 403 FIELD STOP | None | PLC_DISCREAD | I:122/06 | BE 403 FIELD STOP
BE4403_IM | Back_System | BE 403 INTERLOCKS MET | None | PLC_DISCREAD | B3/30 | BE 403 INTERLOCKS MET
BE4403_IT | Back_System | BE 403 AMPS | A | 30 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:00 | BE 403 AMPS
BE4403_JOG | Back_System | BE 403 JOG PLUG INSERTED | On | PLC_ALARM | I:104/01 | BE 403 JOG PLUG INSERTED
BE4403_OVERLOADS | Back_System | BE 403 OVERLOADS | None | PLC_DISCREAD | I:100/05 | BE 403 OVERLOADS
BE4403_PBS | Back_System | BE 4403 PC START | None | PLC_DISCWRITE | B100/130 | BE 4403 PC START
BE4403_PBT | Back_System | BE 4403 PC STOP | None | PLC_DISCWRITE | B100/133 | BE 4403 PC STOP
BE4403AMP_ALM | Back_System | BE 403 HIGH AMPS | On | PLC_ALARM | B101/487 | BE 403 HIGH AMPS
BE4403FTS_ALM | Back_System | BE 403 FAILED TO START | On | PLC_ALARM | B101/378 | BE 403 FAILED TO START
BE4403MS_X | Back_System | BE 4403 AUX FDBK | Off | PLC_DISCREAD | I:100/04 | BE 403 STOPPED
BE4403MSF_ALM | Back_System | BE 403 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/379 | BE 403 MOTION SWITCH FAILURE
BE4406E_AUTO | Back_System | BE 406-E AUTO | None | PLC_DISCREAD | I:102/14 | BE 406-E AUTO
BE4406E_BYP | Back_System | BE 406-E MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/171 | BE 406-E MOTION SWITCH BYPASS
BE4406E_DISCONNECT | Back_System | BE 406-E DISCONNECT | None | PLC_DISCREAD | I:125/14 | BE 406-E DISCONNECT
BE4406E_FS | Back_System | BE 406-E FIELD STOP | None | PLC_DISCREAD | I:125/16 | BE 406-E FIELD STOP
BE4406E_IM | Back_System | BE 406-E INTERLOCKS MET | None | PLC_DISCREAD | B3/42 | BE 406-E INTERLOCKS MET
BE4406E_IT | Back_System | BE 406-E AMPS | A | 25 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:10 | BE 406-E AMPS
BE4406E_JOG | Back_System | BE 406-E JOG PLUG INSERTED | On | PLC_ALARM | I:104/06 | BE 406-E JOG PLUG INSERTED
BE4406E_OVERLOADS | Back_System | BE 406-E OVERLOADS | None | PLC_DISCREAD | I:102/16 | BE 406-E OVERLOADS
BE4406E_PBS | Back_System | BE 4406-E PC START | None | PLC_DISCWRITE | B100/136 | BE 4406-E PC START
BE4406E_PBT | Back_System | BE 4406-E PC STOP | None | PLC_DISCWRITE | B100/137 | BE 4406-E PC STOP
BE4406EAMP_ALM | Back_System | BE 406-E HIGH AMPS | On | PLC_ALARM | B101/490 | BE 406-E HIGH AMPS
BE4406EFTS_ALM | Back_System | BE 406-E FAILED TO START | On | PLC_ALARM | B101/383 | BE 406-E FAILED TO START
BE4406EMS_X | Back_System | BE 4406-E AUX FDBK | Off | PLC_DISCREAD | I:102/15 | BE 406-E STOPPED
BE4406EMSF_ALM | Back_System | BE 406-E MOTION SWITCH FAILURE | On | PLC_ALARM | B101/384 | BE 406-E MOTION SWITCH FAILURE
BE4406W_AUTO | Back_System | BE 406-W IN AUTO POSITION | None | PLC_DISCREAD | I:102/03 | BE 406-W IN AUTO POSITION
BE4406W_BYP | Back_System | BE 406-W MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/172 | BE 406-W MOTION SWITCH BYPASS
BE4406W_DISCONNECT | Back_System | BE 406-W DISCONNECT | None | PLC_DISCREAD | I:125/00 | BE 406-W DISCONNECT
BE4406W_IM | Back_System | BE 406-W INTERLOCKS MET | None | PLC_DISCREAD | B3/43 | BE 406-W INTERLOCKS MET
BE4406W_IT | Back_System | BE 406-W AMPS | A | 25 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:9 | BE 406-W AMPS
BE4406W_JOG | Back_System | BE 406-W JOG PLUG INSERTED | On | PLC_ALARM | I:104/10 | BE 406-W JOG PLUG INSERTED
BE4406W_OVERLOADS | Back_System | BE 406-W OVERLOADS | None | PLC_DISCREAD | I:102/05 | BE 406-W OVERLOADS
BE4406W_PBS | Back_System | BE 4406-W PC START | None | PLC_DISCWRITE | B100/138 | BE 4406-W PC START
BE4406W_PBT | Back_System | BE 4406-W PC STOP | None | PLC_DISCWRITE | B100/139 | BE 4406-W PC STOP
BE4406WAMP_ALM | Back_System | BE 406-W HIGH AMPS | On | PLC_ALARM | B101/30 | BE 406-W HIGH AMPS
BE4406WFTS_ALM | Back_System | BE 406-W FAILED TO START | On | PLC_ALARM | B101/385 | BE 406-W FAILED TO START
BE4406WMS_X | Back_System | BE 4406-W AUX FDBK | Off | PLC_DISCREAD | I:102/04 | BE 406-W STOPPED
BE4406WMSF_ALM | Back_System | BE 406-W MOTION SWITCH FAILURE | On | PLC_ALARM | B101/386 | BE 406-W MOTION SWITCH FAILURE
BE4446_AUTO | Back_System | BE 446 AUTO | None | PLC_DISCREAD | I:101/03 | BE 446 AUTO
BE4446_BYP | Back_System | BE 446 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/169 | BE 446 MOTION SWITCH BYPASS
BE4446_DISCONNECT | Back_System | BE 446 DISCONNECT | None | PLC_DISCREAD | I:123/13 | BE 446 DISCONNECT
BE4446_FS | Back_System | BE 446 FIELD STOP | None | PLC_DISCREAD | I:123/15 | BE 446 FIELD STOP
BE4446_IM | Back_System | BE 446 INTERLOCKS MET | None | PLC_DISCREAD | B3/37 | BE 446 INTERLOCKS MET
BE4446_IT | Back_System | BE 446 AMPS | A | 55 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:12 | BE 446 AMPS
BE4446_JOG | Back_System | BE 446 JOG PLUG INSERTED | On | PLC_ALARM | I:107/06 | BE 446 JOG PLUG INSERTED
BE4446_OVERLOADS | Back_System | BE 446 OVERLOADS | None | PLC_DISCREAD | I:101/05 | BE 446 OVERLOADS
BE4446_PBS | Back_System | BE 4446 PC START | None | PLC_DISCWRITE | B100/145 | BE 4446 PC START
BE4446_PBT | Back_System | BE 4446 PC STOP | None | PLC_DISCWRITE | B100/146 | BE 4446 PC STOP
BE4446AMP_ALM | Back_System | BE 446 HIGH AMPS | On | PLC_ALARM | B101/495 | BE 446 HIGH AMPS
BE4446FTS_ALM | Back_System | BE446 FAILED TO START | On | PLC_ALARM | B101/411 | BE446 FAILED TO START
BE4446MS_X | Back_System | BE 446 AUX CONTACT | Off | PLC_DISCREAD | I:101/04 | BE 446 STOPPED
BE4446MSF_ALM | Back_System | BE446 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/412 | BE446 MOTION SWITCH FAILURE
DC414_DIFF_PRESSURE_ALM | Back_System | DC 414 DIFF PRESSURE ALARM | On | USCNEL051 | DC414_DIFF_PRESSURE_ALM | DC414 Diff Pressure Out Of Range!!!
DG44421_TOBE4403 | Back_System | DG 442-1 SET TO BE 403 | None | PLC_DISCREAD | I:120/00 | DG 442-1 SET TO BE 403
DG44421_TODG4448 | Back_System | DG 442-1 SET TO DG 448 | None | PLC_DISCREAD | I:120/01 | DG 442-1 SET TO DG 448
DG444210_SETSC408 | Back_System | DG 442-10 SET TO SC 408 | None | PLC_DISCWRITE | B100/579 | DG 442-10 SET TO SC 408
DG444210_SETSC408A | Back_System | DG 442-10 SET TO SC 408-A | None | PLC_DISCWRITE | B100/578 | DG 442-10 SET TO SC 408-A
DG444210_TOSC408 | Back_System | DG 442-10 TO SC 408 (SILO 1) | None | PLC_DISCREAD | I:121/16
DG444210_TOSC408A | Back_System | DG 442-10 TO SC 408-A (SILO 4) | None | PLC_DISCREAD | I:121/15
DG444210STUCK_ALM | Back_System | DG 442-10 IS STUCK!! | On | PLC_ALARM | B101/144 | DG 442-10 IS STUCK!!
DG44422_SC4443 | Back_System | DG 442-2 SET TO SC 443 | None | PLC_DISCREAD | I:120/02 | DG 442-2 SET TO SC 443
DG44422_SETTOJUNK | Back_System | DG 4442-2 TO JUNK | None | PLC_DISCWRITE | B100/160 | DG 4442-2 TO JUNK
DG44422_TOJUNK | Back_System | DG 442-2 SET TO JUNK CHUTE | On | PLC_DISCREAD | I:120/03 | DG 442-2 SET TO JUNK CHUTE
DG44423_BE4406E | Back_System | DG 442-3 TO BE 406-E | None | PLC_DISCREAD | I:120/04 | DG 442-3 TO BE 406-E
DG44423_BE4406W | Back_System | DG 442-3 SET TO BE 406-W | None | PLC_DISCREAD | I:120/05 | DG 442-3 SET TO BE 406-W
DG44423_SETBE4406W | Back_System | DG 4442-3 SET TO BE 4406-W | None | PLC_DISCWRITE | B100/161 | DG 4442-3 SET TO BE 4406-W
DG44424_BE4406E | Back_System | DG 442-4 SET TO BE 406-E | None | PLC_DISCREAD | I:120/07 | DG 442-4 SET TO BE 406-E
DG44424_BE4406W | Back_System | DG 442-4 SET TO BE 406-W | None | PLC_DISCREAD | I:120/06 | DG 442-4 SET TO BE 406-W
DG44424_SETBE4406E | Back_System | DG 4442-4 SET TO BE 4406-E | None | PLC_DISCWRITE | B100/162 | DG 4442-4 SET TO BE 4406-E
DG44425_TODG44426 | Back_System | DG 4442-5 SET TO DG 4442-6 | None | PLC_DISCREAD | I:120/11 | DG 4442-5 SET TO DG 4442-6
DG44425_TOSC4408 | Back_System | DG 4442-5 SET TO SC 4408 (NOT POSSIBLE) | None | PLC_DISCREAD | I:120/10 | DG 4442-5 SET TO SC 4408 (NOT POSSIBLE)
DG44426_SETSC4408C | Back_System | DG 4442-6 SET TO SC 4408-C | None | PLC_DISCWRITE | B100/163 | DG 4442-6 SET TO SC 4408-C
DG44426_TODG44429 | Back_System | DG 4442-6 SET TO DG 4442-9 | None | PLC_DISCREAD | I:120/12 | DG 4442-6 SET TO DG 4442-9
DG44426_TOSC4408C | Back_System | DG 4442-6 SET TO SC 4408-C | None | PLC_DISCREAD | I:120/13 | DG 4442-6 SET TO SC 4408-C
DG44427_SETDG44428 | Back_System | DG 4442-7 SET TO DG 4442-8 | None | PLC_DISCWRITE | B100/164 | DG 4442-7 SET TO DG 4442-8
DG44427_TODG44428 | Back_System | DG 4442-7 SET TO DG 4442-8 | None | PLC_DISCREAD | I:120/14 | DG 4442-7 SET TO DG 4442-8
DG44427_TOSC408A | Back_System | DG 4442-7 SET TO SC 4408 AND SC 4408-A | None | PLC_DISCREAD | I:120/15 | DG 4442-7 SET TO SC 4408 AND SC 4408-A
DG44428_DG44429 | Back_System | DG 4442-8 TO DG 4442-9 (SET SO IMPOSSIBLE) | None | PLC_DISCREAD | I:120/17 | DG 4442-8 TO DG 4442-9 (SET SO IMPOSSIBLE)
DG44428_TOSC4408C | Back_System | DG 4442-8 SET TO SC 4408-C | None | PLC_DISCREAD | I:120/16 | DG 4442-8 SET TO SC 4408-C
DG44429_SETSC408B | Back_System | DG 4442-9 SET TO SC 408-C | None | PLC_DISCWRITE | B100/165 | DG 4442-9 SET TO SC 408-C
DG44429_TOSC4408B | Back_System | DG 4442-9 SET TO SC 4408-B | None | PLC_DISCREAD | I:121/01 | DG 4442-9 SET TO SC 4408-B
DG44429_TOSILO2 | Back_System | DG 4442-9 SET TO SILO 2 | None | PLC_DISCREAD | I:121/00 | DG 4442-9 SET TO SILO 2
DG4448_BE4406E | Back_System | DG 448 SET TO BE 406-E | None | PLC_DISCREAD | I:121/05 | DG 448 SET TO BE 406-E
DG4448_BE4406W | Back_System | DG 448 SET TO BE 406-W | None | PLC_DISCREAD | I:121/04 | DG 448 SET TO BE 406-W
FN44141_AUTO | Back_System | FN 414-1 AUTO | None | PLC_DISCREAD | I:103/6 | FN 414-1 AUTO
FN44141_DISCONNECT | Back_System | FN 414-1 DISCONNECT | None | PLC_DISCREAD | I:126/10 | FN 414-1 DISCONNECT
FN44141_IM | Back_System | FN 414-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/45 | FN 414-1 INTERLOCKS MET
FN44141_OVERLOADS | Back_System | FN 414-1 OVERLOADS | None | PLC_DISCREAD | I:103/10 | FN 414-1 OVERLOADS
FN44141_PBS | Back_System | FN 4414-1 PC START | None | PLC_DISCWRITE | B100/32 | FN 4414-1 PC START
FN44141_PBT | Back_System | FN 4414-1 PC STOP | None | PLC_DISCWRITE | B100/33 | FN 4414-1 PC STOP
FN44141FTS_ALM | Back_System | FN 414-1 FAILED TO START | On | PLC_ALARM | B101/398 | FN 414-1 FAILED TO START
FN44141MS_X | Back_System | FN 414-1 AUX CONTACT | Off | PLC_DISCREAD | I:103/7 | FN 414-1 STOPPED
HM4022_PCBYP | Back_System | HM 402-2 PC BYPASS | On | PLC_DISCWRITE | B100/477 | HM 402-2 PC BYPASSED - MAKE SURE DIVERTER GATES SET!
HM44022_FS | Back_System | HM 402-2 FIELD STOP | None | PLC_DISCREAD | I:130/06 | HM 402-2 FIELD STOP
HM44022_IM | Back_System | HM 402-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/52 | HM 402-2 INTERLOCKS MET
HM44022_PBS | Back_System | HM 404-2 PC START | None | PLC_DISCWRITE | B100/125 | HM 404-2 PC START
HM44022_PBT | Back_System | HM 4402-2 PC STOP | None | PLC_DISCWRITE | B100/127 | HM 4402-2 PC STOP
HM44022FTS_ALM | Back_System | HM 402-2 FAILED TO START | On | PLC_ALARM | B101/377 | HM 402-2 FAILED TO START
HM44022MS_X | Back_System | HM 402-2 AUX FDBK | Off | PLC_DISCREAD | I:130/07 | HM 402-2 STOPPED!!
HM44051_ACC | Back_System | HM 4405-1 DIRECTION TIMER ACCUMULATIVE TIME | SEC | 400 | 0 | 0 | 0 | PLC_INTREAD | T4:318.ACC | HM 4405-1 DIRECTION TIMER ACCUMULATIVE TIME
HM44051_FS | Back_System | HM 405-1 FIELD STOP | None | PLC_DISCREAD | I:124/03 | HM 405-1 FIELD STOP
HM44051_FWD | Back_System | HM 4405-1 AUTO IN FORWARD (-1/8) POSITION | None | PLC_DISCREAD | I:103/00 | HM 4405-1 AUTO IN FORWARD (-1/8) POSITION
HM44051_IT | Back_System | HAMMERMILL 405-1 AMPS | Amps | 240 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:06 | HAMMERMILL 405-1 AMPS
HM44051_PBS | Back_System | HM 4405-1 PC START | None | PLC_DISCWRITE | B100/134 | HM 4405-1 PC START
HM44051_PBT | Back_System | HM 4405-1 PC STOP | None | PLC_DISCWRITE | B100/135 | HM 4405-1 PC STOP
HM44051_PRE | Back_System | HM 4405-1 DIRECTION SWITCH TIMER PRESET | SEC | 400 | 0 | 0 | 0 | PLC_INTREAD | T4:318.PRE | HM 4405-1 DIRECTION SWITCH TIMER PRESET
HM44051_REV | Back_System | HM 4405-1 AUTO IN REVERSE (-3/8) POSITION | None | PLC_DISCREAD | I:101/13 | HM 4405-1 AUTO IN REVERSE (-3/8) POSITION
HM44051_TT | Back_System | HM 4405-1 DIRECTIONAL TIMER TIMING | None | PLC_DISCREAD | T4:318.TT | HM 4405-1 DIRECTIONAL TIMER TIMING
HM44051AMP_ALM | Back_System | HM 405-1 HIGH AMPS | On | PLC_ALARM | B101/489 | HM 405-1 HIGH AMPS
HM44051FWD_IM | Back_System | HM 405-1 FORWARD INTERLOCKS MET | None | PLC_DISCREAD | B3/39 | HM 405-1 FORWARD INTERLOCKS MET
HM44051FWDFTS_ALM | Back_System | HM 405-1 FORWARD FAILED TO START! | On | PLC_ALARM | B101/381 | HM 405-1 FORWARD FAILED TO START!
HM44051FWDMS_X | Back_System | HM 4405-1 FDBK IN FORWARD (-1/8) | Off | PLC_DISCREAD | I:101/07 | HM 405-1 Stopped!!
HM44051REV_IM | Back_System | HM 405-1 REVERSE INTERLOCKS MET | None | PLC_DISCREAD | B3/40 | HM 405-1 REVERSE INTERLOCKS MET
HM44051REVFTS_ALM | Back_System | HM 405-1 REVERSE FAILED TO START! | On | PLC_ALARM | B101/382 | HM 405-1 REVERSE FAILED TO START!
HM44051REVMS_X | Back_System | HM 4405-1 FDBK IN REVERSE (-3/8) | Off | PLC_DISCREAD | I:101/11 | HM 405-1 STOPPED!!
RA44144_AUTO | Back_System | RA 414-4 AUTO | None | PLC_DISCREAD | I:104/3 | RA 414-4 AUTO
RA44144_BYP | Back_System | RA 4414-4 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/218 | RA 4414-4 MOTION SWITCH BYPASS
RA44144_DISCONNECT | Back_System | RA 414-4 DISCONNECT | None | PLC_DISCREAD | I:127/10 | RA 414-4 DISCONNECT
RA44144_FS | Back_System | RA 414-4 FIELD STOP | None | PLC_DISCREAD | I:127/12 | RA 414-4 FIELD STOP
RA44144_IM | Back_System | RA 414-4 INTERLOCKS MET | None | PLC_DISCREAD | B3/47 | RA 414-4 INTERLOCKS MET
RA44144_OVERLOADS | Back_System | RA 414-4 OVERLOADS | None | PLC_DISCREAD | I:104/05 | RA 414-4 OVERLOADS
RA44144_PBS | Back_System | RA 4414-4 PC START | None | PLC_DISCWRITE | B100/108 | RA 4414-4 PC START
RA44144_PBT | Back_System | RA 4414-4 PC STOP | None | PLC_DISCWRITE | B100/109 | RA 4414-4 PC STOP
RA44144FTS_ALM | Back_System | RA 414-4 FAILED TO START | On | PLC_ALARM | B101/401 | RA 414-4 FAILED TO START
RA44144MS_X | Back_System | RA 414-4 AUX CONTACT | Off | PLC_DISCREAD | I:104/04 | RA 414-1 STOPPED
RA44144MSF_ALM | Back_System | RA 414-4 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/402 | RA 414-4 MOTION SWITCH FAILURE
RC4444_PBS | Back_System | RC 4444 START | None | PLC_DISCWRITE | B100/156 | RC 4444 START
RC4444_PBT | Back_System | RC 4444 STOP | None | PLC_DISCWRITE | B100/157 | RC 4444 STOP
RC44441_AUTO | Back_System | RC 444-1 AUTO | None | PLC_DISCREAD | I:100/11 | RC 444-1 AUTO
RC44441_BYP | Back_System | RC 444-1 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/166 | RC 444-1 MOTION SWITCH BYPASSED
RC44441_DISCONNECT | Back_System | RC 444-1 DISCONNECT | None | PLC_DISCREAD | I:123/00 | RC 444-1 DISCONNECT
RC44441_FS | Back_System | RC 444-1 FIELD STOP | None | PLC_DISCREAD | I:123/03 | RC 444-1 FIELD STOP
RC44441_IM | Back_System | RC 444-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/32 | RC 444-1 INTERLOCKS MET
RC44441_IT | Back_System | RC 444-1 AMPS | Amps | 60 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:02 | RC 444-1 AMPS
RC44441_OVERLOADS | Back_System | RC 444-1 OVERLOADS | None | PLC_DISCREAD | I:100/13 | RC 444-1 OVERLOADS
RC44441AMP_ALM | Back_System | RC 444-1 HIGH AMPS | On | PLC_ALARM | B101/491 | RC 444-1 HIGH AMPS
RC44441FTS_ALM | Back_System | RC 444-1 FAILED TO START | On | PLC_ALARM | B101/405 | RC 444-1 FAILED TO START
RC44441MS_X | Back_System | RC 444-1 RUNNING | Off | PLC_DISCREAD | I:100/12 | RC 444-1 STOPPED
RC44441MSF_ALM | Back_System | RC 444-1 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/406 | RC 444-1 MOTION SWITCH FAILURE
RC44442_AUTO | Back_System | RC 444-1 AUTO | None | PLC_DISCREAD | I:100/16 | RC 444-1 AUTO
RC44442_BYP | Back_System | RC 444-2 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/167 | RC 444-2 MOTION SWITCH BYPASS
RC44442_DISCONNECT | Back_System | RC 444-2 DISCONNECT | None | PLC_DISCREAD | I:123/01 | RC 444-2 DISCONNECT
RC44442_FS | Back_System | RC 444-2 FIELD STOP | None | PLC_DISCREAD | I:123/03 | RC 444-2 FIELD STOP
RC44442_IM | Back_System | RC 444-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/35 | RC 444-2 INTERLOCKS MET
RC44442_IT | Back_System | RC 444-2 AMPS | Amps | 60 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:03 | RC 444-2 AMPS
RC44442_OVERLOADS | Back_System | RC 444-2 OVERLOADS | None | PLC_DISCREAD | I:100/15 | RC 444-2 OVERLOADS
RC44442AMP_ALM | Back_System | RC 444-2 HIGH AMPS | On | PLC_ALARM | B101/492 | RC 444-2 HIGH AMPS
RC44442FTS_ALM | Back_System | RC 444-2 FAILED TO START | On | PLC_ALARM | B101/407 | RC 444-2 FAILED TO START
RC44442MS_X | Back_System | RC 444-2 RUNNING | Off | PLC_DISCREAD | I:100/14 | RC 444-2 STOPPED
RC44442MSF_ALM | Back_System | RC 444-2 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/408 | RC 444-2 MOTION SWITCH FAILURE
RECYCLEGATE_TOG | Back_System | RECYCLE GATE 1=SC411 0=HM 402-2 | None | PLC_DISCWRITE | B100/15 | RECYCLE GATE 1=SC411 0=HM 402-2
SC4408_BYP | Back_System | SC 408 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/209 | SC 408 MOTION SWITCH BYPASS
SC4408_IM | Back_System | SC 408 INTERLOCKS MET | None | PLC_DISCREAD | B3/248 | SC 408 INTERLOCKS MET
SC4408_PBS | Back_System | SC 4408 PC START | None | PLC_DISCWRITE | B100/20 | SC 4408 PC START
SC4408_PBT | Back_System | SC 4408 PC STOP | None | PLC_DISCWRITE | B100/21 | SC 4408 PC STOP
SC4408A_BYP | Back_System | SC 408-A MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/173 | SC 408-A MOTION SWITCH BYPASS
SC4408A_IM | Back_System | SC 408-A INTERLOCKS MET | None | PLC_DISCREAD | B3/245 | SC 408-A INTERLOCKS MET
SC4408A_PBS | Back_System | SC 4408-A PC START | None | PLC_DISCWRITE | B100/7 | SC 4408-A PC START
SC4408A_PBT | Back_System | SC 4408-A PC STOP | None | PLC_DISCWRITE | B100/42 | SC 4408-A PC STOP
SC4408AFTS_ALM | Back_System | SC 408-A FAILED TO START | On | PLC_ALARM | B101/389 | SC 408-A FAILED TO START
SC4408AMS_X | Back_System | SC 408-A AUX CONTACT | Off | PLC_DISCREAD | I:102/07 | SC 408-A STOPPED
SC4408AMSF_ALM | Back_System | SC 408-A MOTION SWITCH FAILURE | On | PLC_ALARM | B101/390 | SC 408-A MOTION SWITCH FAILURE
SC4408B_BYP | Back_System | SC 408-B MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/174 | SC 408-B MOTION SWITCH BYPASS
SC4408B_IM | Back_System | SC 408-B INTERLOCKS MET | None | PLC_DISCREAD | B3/246 | SC 408-B INTERLOCKS MET
SC4408B_PBS | Back_System | SC 4408-B PC START | None | PLC_DISCWRITE | B100/16 | SC 4408-B PC START
SC4408B_PBT | Back_System | SC 4408-B PC STOP | None | PLC_DISCWRITE | B100/17 | SC 4408-B PC STOP
SC4408BFTS_ALM | Back_System | SC 408-B FAILED TO START | On | PLC_ALARM | B101/391 | SC 408-B FAILED TO START
SC4408BMS_X | Back_System | SC 408-B AUX CONTACT | Off | PLC_DISCREAD | I:102/12 | SC 408-B STOPPED
SC4408BMSF_ALM | Back_System | SC 408-B MOTION SWITCH FAILURE | On | PLC_ALARM | B101/392 | SC 408-B MOTION SWITCH FAILURE
SC4408C_AUTO | Back_System | SC 408-C AUTO | None | PLC_DISCREAD | I:103/03 | SC 408-C AUTO
SC4408C_BYP | Back_System | SC 408-C MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/175 | SC 408-C MOTION SWITCH BYPASS
SC4408C_DISCONNECT | Back_System | SC 408-C DISCONNECT | None | PLC_DISCREAD | I:126/04 | SC 408-C DISCONNECT
SC4408C_FS | Back_System | SC 408-C FIELD STOP | None | PLC_DISCREAD | I:126/06 | SC 408-C FIELD STOP
SC4408C_IM | Back_System | SC 408-C INTERLOCKS MET | None | PLC_DISCREAD | B3/44 | SC 408-C INTERLOCKS MET
SC4408C_OVERLOADS | Back_System | SC 408-C OVERLOADS | None | PLC_DISCREAD | I:103/5 | SC 408-C OVERLOADS
SC4408C_PBS | Back_System | SC 4408-C PC START | None | PLC_DISCWRITE | B100/18 | SC 4408-C PC START
SC4408C_PBT | Back_System | SC 4408-C PC STOP | None | PLC_DISCWRITE | B100/19 | SC 4408-C PC STOP
SC4408CFTS_ALM | Back_System | SC 408-C FAILED TO START | On | PLC_ALARM | B101/393 | SC 408-C FAILED TO START
SC4408CMS_X | Back_System | SC 4408-C AUX CONTACT | Off | PLC_DISCREAD | I:103/4 | SC 408-C STOPPED
SC4408CMSF_ALM | Back_System | SC 408-C MOTION SWITCH FAILURE | On | PLC_ALARM | B101/394 | SC 408-C MOTION SWITCH FAILURE
SC4408FTS_ALM | Back_System | SC 408 FAILED TO START | On | PLC_ALARM | B101/387 | SC 408 FAILED TO START
SC4408MS_X | Back_System | SC 408 AUX CONTACT | Off | PLC_DISCREAD | I:103/1 | SC 408 STOPPED
SC4408MSF_ALM | Back_System | SC 408 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/388 | SC 408 MOTION SWITCH FAILURE
SC4411_IM | Back_System | SC 411 INTERLOCKS MET | None | PLC_DISCREAD | B3/342 | SC 411 INTERLOCKS MET
SC4411_PBS | Back_System | SC 411 PC START | None | PLC_DISCWRITE | B100/04 | SC 411 PC START
SC4411_PBT | Back_System | SC 411 PC STOP | None | PLC_DISCWRITE | B100/5 | SC 411 PC STOP
SC4411FTS_ALM | Back_System | SC 411 FAILED TO START!! | On | PLC_ALARM | B101/395 | SC 411 FAILED TO START!!
SC4411MS_BYP | Back_System | SC 411 BYPASS MOTION SWITCH | On | PLC_DISCWRITE | B100/2 | SC 411 BYPASS MOTION SWITCH
SC4411MS_X | Back_System | SC 411 AUX FDBK | Off | PLC_DISCREAD | I:106/11 | SC 411 STOPPED!!
SC4411MSF_ALM | Back_System | SC 411 MOTION SWITCH FAILURE!! | On | PLC_ALARM | B101/396 | SC 411 MOTION SWITCH FAILURE!!
SC4412_FS | Back_System | SC 4-412 FIELD STOP | None | PLC_DISCREAD | I:101/17 | SC 4-412 FIELD STOP
SC4412_IM | Back_System | SC 4-412 INTERLOCKS MET | None | PLC_DISCREAD | B3/57 | SC 4-412 INTERLOCKS MET
SC4412_PBS | Back_System | SC 4412 PC START | None | PLC_DISCWRITE | B100/223 | SC 4412 PC START
SC4412_PBT | Back_System | SC 4412 PC STOP | None | PLC_DISCWRITE | B100/222 | SC 4412 PC STOP
SC4412FTS_ALM | Back_System | SC 412 FAILED TO START | On | PLC_ALARM | B101/397 | SC 412 FAILED TO START
SC4412MS_X | Back_System | SC 4-412 AUX FDBK | Off | PLC_DISCREAD | I:100/17 | SC 412 STOPPED
SC44142_AUTO | Back_System | SC 414-2 AUTO | None | PLC_DISCREAD | I:103/11 | SC 414-2 AUTO
SC44142_BYP | Back_System | SC 414-2 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/217 | SC 414-2 MOTION SWITCH BYPASS
SC44142_DISCONNECT | Back_System | SC 414-2 DISCONNECT | None | PLC_DISCREAD | I:126/14 | SC 414-2 DISCONNECT
SC44142_FS | Back_System | SC 414-2 FIELD STOP | None | PLC_DISCREAD | I:126/16 | SC 414-2 FIELD STOP
SC44142_IM | Back_System | SC 414-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/46 | SC 414-2 INTERLOCKS MET
SC44142_OVERLOADS | Back_System | SC 414-2 OVERLOADS | None | PLC_DISCREAD | I:103/13 | SC 414-2 OVERLOADS
SC44142_PBS | Back_System | SC 4414-2 PC START | None | PLC_DISCWRITE | B100/34 | SC 4414-2 PC START
SC44142_PBT | Back_System | SC 4414-2 PC STOP | None | PLC_DISCWRITE | B100/35 | SC 4414-2 PC STOP
SC44142FTS_ALM | Back_System | SC 414-2 FAILED TO START | On | PLC_ALARM | B101/399 | SC 414-2 FAILED TO START
SC44142MS_X | Back_System | SC 414-2 SCREW CONVEYOR AUX CONTACT | Off | PLC_DISCREAD | I:103/12 | SC 414-2 STOPPED
SC44142MSF_ALM | Back_System | SC 414-2 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/400 | SC 414-2 MOTION SWITCH FAILURE
SC4425_PBT | Back_System | SC 4425 PC STOP | None | PLC_DISCWRITE | B100/195 | SC 4425 PC STOP
SC4427_PBS | Back_System | SC 427 PC START | None | PLC_DISCWRITE | B100/176 | SC 427 PC START
SC4443_AUTO | Back_System | SC 443 AUTO | None | PLC_DISCREAD | I:100/06 | SC 443 AUTO
SC4443_BYP | Back_System | SC 443 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/159 | SC 443 MOTION SWITCH BYPASS
SC4443_DISCONNECT | Back_System | SC 443 DISCONNECT | None | PLC_DISCREAD | I:122/10 | SC 443 DISCONNECT
SC4443_FS | Back_System | SC 443 FIELD STOP | None | PLC_DISCREAD | I:122/12 | SC 443 FIELD STOP
SC4443_IM | Back_System | SC 443 INTERLOCKS MET | None | PLC_DISCREAD | B3/31 | SC 443 INTERLOCKS MET
SC4443_IT | Back_System | SC 443 AMPS | Amps | 40 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:01 | SC 443 AMPS
SC4443_OVERLOADS | Back_System | SC 443 OVERLOADS | None | PLC_DISCREAD | I:100/10 | SC 443 OVERLOADS
SC4443_PBS | Back_System | SC 443 PC START | None | PLC_DISCWRITE | B100/152 | SC 443 PC START
SC4443_PBT | Back_System | SC 4443 PC STOP | None | PLC_DISCWRITE | B100/153 | SC 4443 PC STOP
SC4443AMP_ALM | Back_System | SC 443 HIGH AMPS | On | PLC_ALARM | B101/493 | SC 443 HIGH AMPS
SC4443FTS_ALM | Back_System | SC 443 FAILED TO START | On | PLC_ALARM | B101/403 | SC 443 FAILED TO START
SC4443MS_X | Back_System | SC 4443 AUX FDBK | Off | PLC_DISCREAD | I:100/07 | SC 443 STOPPED
SC4443MSF_ALM | Back_System | SC 443 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/404 | SC 443 MOTION SWITCH FAILURE
SC4445_AUTO | Back_System | SC 445 AUTO | None | PLC_DISCREAD | I:101/00 | SC 445 AUTO
SC4445_BYP | Back_System | SC 445 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/168 | SC 445 MOTION SWITCH BYPASS
SC4445_DISCONNECT | Back_System | SC 445 DISCONNECT | None | PLC_DISCREAD | I:123/07 | SC 445 DISCONNECT
SC4445_FS | Back_System | SC 445 FIELD STOP | None | PLC_DISCREAD | I:123/11 | SC 445 FIELD STOP
SC4445_IM | Back_System | SC 445 INTERLOCKS MET | None | PLC_DISCREAD | B3/36 | SC 445 INTERLOCKS MET
SC4445_IT | Back_System | SC 445 AMPS | Amps | 25 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:4 | SC 445 AMPS
SC4445_OVERLOADS | Back_System | SC 445 OVERLOADS | None | PLC_DISCREAD | I:101/02 | SC 445 OVERLOADS
SC4445_PBS | Back_System | SC 445 PC START | None | PLC_DISCWRITE | B100/143 | SC 445 PC START
SC4445_PBT | Back_System | SC 4445 PC STOP | None | PLC_DISCWRITE | B100/144 | SC 4445 PC STOP
SC4445AMP_ALM | Back_System | SC 445 HIGH AMPS | On | PLC_ALARM | B101/494 | SC 445 HIGH AMPS
SC4445FTS_ALM | Back_System | SC 445 FAILED TO START | On | PLC_ALARM | B101/409 | SC 445 FAILED TO START
SC4445MS_X | Back_System | 445 SCREW CONV. RUN INDICATOR | Off | PLC_DISCREAD | I:101/01 | SC 445 STOPPED
SC4445MSF_ALM | Back_System | SC 445 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/410 | SC 445 MOTION SWITCH FAILURE
SC4447_AUTO | Back_System | SC 447 AUTO | None | PLC_DISCREAD | I:102/00 | SC 447 AUTO
SC4447_BYP | Back_System | SC 447 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/170 | SC 447 MOTION SWITCH BYPASS
SC4447_DISCONNECT | Back_System | SC 447 DISCONNECT | None | PLC_DISCREAD | I:124/13 | SC 447 DISCONNECT
SC4447_FS | Back_System | SC 447 FIELD STOP | None | PLC_DISCREAD | I:124/15 | SC 447 FIELD STOP
SC4447_IM | Back_System | SC 447 INTERLOCKS MET | None | PLC_DISCREAD | B3/41 | SC 447 INTERLOCKS MET
SC4447_IT | Back_System | SC 447 AMPS | A | 20 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:08 | SC 447 AMPS
SC4447_OVERLOADS | Back_System | SC 447 OVERLOADS | None | PLC_DISCREAD | I:102/02 | SC 447 OVERLOADS
SC4447_PBS | Back_System | SC 4447 PC START | None | PLC_DISCWRITE | B100/140 | SC 4447 PC START
SC4447_PBT | Back_System | SC 4447 PC STOP | None | PLC_DISCWRITE | B100/141 | SC 4447 PC STOP
SC4447AMP_ALM | Back_System | SC 447 HIGH AMPS | On | PLC_ALARM | B101/496 | SC 447 HIGH AMPS
SC4447FTS_ALM | Back_System | SC 447 FAILED TO START | On | PLC_ALARM | B101/413 | SC 447 FAILED TO START
SC4447MS_X | Back_System | 447 SCREW CONV. RUN INDICATOR | Off | PLC_DISCREAD | I:102/01 | SC 447 STOPPED
SC4447MSF_ALM | Back_System | SC 447 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/414 | SC 447 MOTION SWITCH FAILURE
SILO1_Meas | Back_System | SILO 1 LEVEL MEASUREMENT (FT) | ft | 54 | 1 | 0 | 1 | PLC_INTWRITE | N102:66 | SILO 1 LEVEL MEASUREMENT (FT)
SILO1_MEASTON | Back_System | SILO 1 TON MEASUREMENT | ton | 950 | 1 | 0 | 0 | PLC_FLTREAD | F9:263 | SILO 1 TON MEASUREMENT
SILO1HIGH_ALM | Back_System | SILO #1 HIGH LEVEL | On | PLC_ALARM | I:121/06 | SILO #1 HIGH LEVEL
SILO2_Meas | Back_System | SILO 2 LEVEL MEASUREMENT (FT) | ft | 54 | 1 | 0 | 1 | PLC_INTWRITE | N102:67 | SILO 2 LEVEL MEASUREMENT (FT)
SILO2_MEASTON | Back_System | SILO 2 TON MEASUREMENT | ton | 950 | 1 | 0 | 0 | PLC_FLTREAD | F9:264 | SILO 2 TON MEASUREMENT
SILO2HIGH_ALM | Back_System | SILO #2 HIGH LEVEL | On | PLC_ALARM | I:121/07 | SILO #2 HIGH LEVEL
SILO3_Meas | Back_System | SILO 3 LEVEL MEASUREMENT (FT) | ft | 54 | 1 | 0 | 1 | PLC_INTWRITE | N102:68 | SILO 3 LEVEL MEASUREMENT (FT)
SILO3_MEASTON | Back_System | SILO 3 TON MEASUREMENT | ton | 950 | 1 | 0 | 0 | PLC_FLTREAD | F9:265 | SILO 3 TON MEASUREMENT
SILO3HIGH_ALM | Back_System | SILO #3 HIGH LEVEL | On | PLC_ALARM | I:121/10 | SILO #3 HIGH LEVEL
SILO4_Meas | Back_System | SILO 4 LEVEL MEASUREMENT (FT) | ft | 54 | 1 | 0 | 1 | PLC_INTWRITE | N102:69 | SILO 4 LEVEL MEASUREMENT (FT)
SILO4_MEASTON | Back_System | SILO 4 TON MEASUREMENT | ton | 950 | 1 | 0 | 0 | PLC_FLTREAD | F9:266 | SILO 4 TON MEASUREMENT
SILO4HIGH_ALM | Back_System | SILO #4 HIGH LEVEL | On | PLC_ALARM | I:121/11 | SILO #4 HIGH LEVEL
SILO5_Meas | Back_System | SILO 5 LEVEL MEASUREMENT (FT) | ft | 54 | 1 | 0 | 1 | PLC_INTWRITE | N102:70 | SILO 5 LEVEL MEASUREMENT (FT)
SILO5_MEASTON | Back_System | SILO 5 TON MEASUREMENT | ton | 950 | 1 | 0 | 0 | PLC_FLTREAD | F9:267 | SILO 5 TON MEASUREMENT
SILO5HIGH_ALM | Back_System | SILO #5 HIGH LEVEL | On | PLC_ALARM | I:121/12 | SILO #5 HIGH LEVEL
SILO6_AVGMEAS | Back_System | SILO 6 AVERAGE LEVEL MEASUREMENT #1 (FT) | ft | 41 | 1 | 0 | 0 | PLC_FLTREAD | F9:259 | SILO 6 AVERAGE LEVEL MEASUREMENT #1 (FT)
SILO6_Meas1 | Back_System | SILO 6 LEVEL MEASUREMENT #1 (FT) | ft | 41 | 1 | 0 | 0 | PLC_INTWRITE | N102:71 | SILO 6 LEVEL MEASUREMENT #1 (FT)
SILO6_Meas2 | Back_System | SILO 6 LEVEL MEASUREMENT #2 (FT) | ft | 41 | 1 | 0 | 0 | PLC_INTWRITE | N102:72 | SILO 6 LEVEL MEASUREMENT #2 (FT)
SILO6_MEASTON | Back_System | SILO 6 TON MEASUREMENT | ton | 500 | 1 | 0 | 0 | PLC_FLTREAD | F9:268 | SILO 6 TON MEASUREMENT
VS4404_AUTO | Back_System | VS 404 AUTO | None | PLC_DISCREAD | I:101/14 | VS 404 AUTO
VS4404_BYPTT | Back_System | VS 404 INTERLOCK BYPASS FOR START UP TIMING | None | PLC_DISCREAD | T4:200.TT | VS 404 INTERLOCK BYPASS FOR START UP TIMING
VS4404_DISCONNECT | Back_System | VS 404 DISCONNECT | None | PLC_DISCREAD | I:124/07 | VS 404 DISCONNECT
VS4404_FS | Back_System | VS 404 FIELD STOP | None | PLC_DISCREAD | I:124/11 | VS 404 FIELD STOP
VS4404_IM | Back_System | VS 404 INTERLOCKS MET | None | PLC_DISCREAD | B3/38 | VS 404 INTERLOCKS MET
VS4404_IT | Back_System | VS 404 AMPS | A | 30 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:05 | VS 404 AMPS
VS4404_OVERLOADS | Back_System | VS 404 OVERLOADS | None | PLC_DISCREAD | I:101/16 | VS 404 OVERLOADS
VS4404_PBS | Back_System | VS 4404 PC START | None | PLC_DISCWRITE | B100/154 | VS 4404 PC START
VS4404_PBT | Back_System | VS 4404 PC STOP | None | PLC_DISCWRITE | B100/155 | VS 4404 PC STOP
VS4404_SBYP | Back_System | VS 404 INTERLOCK BYPASS TO START ENABLED | None | PLC_DISCREAD | T4:200.EN | VS 404 INTERLOCK BYPASS TO START ENABLED
VS4404AMP_ALM | Back_System | VS 404 HIGH AMPS | On | PLC_ALARM | B101/488 | VS 404 HIGH AMPS
VS4404FTS_ALM | Back_System | VS 404 FAILED TO START | On | PLC_ALARM | B101/380 | VS 404 FAILED TO START
VS4404MS_X | Back_System | VS 4404 AUX FDBK | Off | PLC_DISCREAD | I:101/15 | VS 404 STOPPED
FIRE_SNCR_UREA_ALM | BP1 | FIRE IN SNCR UREA Room | On | USCNEL207 | NEL_BP1_FireAlarm | FIRE ALARM ! SNCR Urea Room
NEL_BP1_AG02016_AUX | BP1 | BP1 AG02016 Tank Agitator AUX | Off | USCNEL207 | NEL_BP1_AG02016.AUX | BP1 AG02016 Tank Agitator AUX Stopped
NEL_BP1_AG02016_MODE_AUTO | BP1 | BP1 AG02016 Tank Agitator AUTO | On | USCNEL207 | NEL_BP1_AG02016.MODE_AUTO | BP1 AG02016 Tank Agitator Mode Auto
NEL_BP1_AG02016_PBE_HMI | BP1 | BP1 AG02016 Tank Agitator PBE | Off | USCNEL207 | NEL_BP1_AG02016.PBE_HMI
NEL_BP1_AG02016_PBS_HMI | BP1 | BP1 AG02016 Tank Agitator PBS | Off | USCNEL207 | NEL_BP1_AG02016.PBS_HMI
NEL_BP1_BD02003_IND | BP1 | BP1 BD02003 Tank Burst Disc IND | On | USCNEL207 | NEL_BP1_BD02003.IND | BP1 BD02003 Tank Burst Disc Indicator
NEL_BP1_FS009_IND | BP1 | BP1 FS009 Circ Flow Switch | Off | USCNEL207 | NEL_BP1_FS009.IND | BP1 FS009 Circ Flow Switch Low Flow
NEL_BP1_FS010_IND | BP1 | BP1 FS010 Transfer Flow Switch | Off | USCNEL207 | NEL_BP1_FS010.IND | BP1 FS010 Transfer Flow Switch Low Flow
NEL_BP1_FT03010_IND | BP1 | BP1 FT03010 TOT GAL | GPM | 50 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_FT03010.IND
NEL_BP1_FT03010_QT_CTU_ACC | BP1 | BP1 FT03010 TOT GAL | GAL | 15000 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_FT03010_QT_CTU.ACC
NEL_BP1_FT03010_QT_RST_BTN | BP1 | BP1 FT0310 TOT RST TOGGLE | On | USCNEL207 | NEL_BP1_FT03010_QT_RST_BTN | BP1 FT0310 TOT RST TOGGLE
NEL_BP1_FT03010_TOT | BP1 | NEL_BP1_FT03010_TOT | GAL | 12000 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_FT03010.TOT
NEL_BP1_FV01017_PBC_HMI | BP1 | BP1 FV01017 Transfer Valve CLOSE CMD | None | USCNEL207 | NEL_BP1_FV01017.PBC_HMI
NEL_BP1_FV01017_PBO_HMI | BP1 | BP1 FV01017 Transfer Valve OPEN CMD | None | USCNEL207 | NEL_BP1_FV01017.PBO_HMI
NEL_BP1_FV01017_ZSC | BP1 | BP1 FV01017 Transfer Valve CLOSED | On | USCNEL207 | NEL_BP1_FV01017.ZSC | BP1 FV01017 Transfer Valve CLOSED
NEL_BP1_FV01017_ZSO | BP1 | BP1 FV01017 Batch Transfer Valve OPEN | On | USCNEL207 | NEL_BP1_FV01017.ZSO | BP1 FV01017 Batch Transfer Valve OPEN
NEL_BP1_FV02009_PBC_HMI | BP1 | BP1 FV02009 Tank Vent Valve CLOSE CMD | Off | USCNEL207 | NEL_BP1_FV02009.PBC_HMI
NEL_BP1_FV02009_PBO_HMI | BP1 | BP1 FV02009 Tank Vent Valve OPEN CMD | Off | USCNEL207 | NEL_BP1_FV02009.PBO_HMI
NEL_BP1_FV02009_ZSC | BP1 | BP1 FV02009 Tank Vent Valve CLOSED | On | USCNEL207 | NEL_BP1_FV02009.ZSC | BP1 FV02009 Tank Vent Valve CLOSED
NEL_BP1_FV02009_ZSO | BP1 | BP1 FV02009 Flow Valve OPEN | On | USCNEL207 | NEL_BP1_FV02009.ZSO | BP1 FV02009 Flow Valve OPEN
NEL_BP1_FV02015_PBC_HMI | BP1 | BP1 FV02015 3 Way Valve CLOSE CMD | Off | USCNEL207 | NEL_BP1_FV02015.PBC_HMI
NEL_BP1_FV02015_PBO_HMI | BP1 | BP1 FV02015 3 Way Valve OPEN CMD | Off | USCNEL207 | NEL_BP1_FV02015.PBO_HMI
NEL_BP1_FV02015_ZSC | BP1 | BP1 FV02015 2 Way Valve CLOSED (OPEN to Circ) | On | USCNEL207 | NEL_BP1_FV02015.ZSC | BP1 FV02015 2 Way Valve CLOSED (OPEN to Circ)
NEL_BP1_FV02015_ZSO | BP1 | BP1 FV02015 3 Way Valve OPEN (to Transfer Tank) | On | USCNEL207 | NEL_BP1_FV02015.ZSO | BP1 FV02015 3 Way Valve OPEN (to Transfer Tank)
NEL_BP1_FV03008_PBC_HMI | BP1 | BP1 FV03008 Circulation Valve CLOSE CMD | Off | USCNEL207 | NEL_BP1_FV03008.PBC_HMI
NEL_BP1_FV03008_PBO_HMI | BP1 | BP1 FV03008 Circulation Valve OPEN CMD | Off | USCNEL207 | NEL_BP1_FV03008.PBO_HMI
NEL_BP1_FV03008_ZSC | BP1 | BP1 FV03008 Circulation Valve CLOSED | On | USCNEL207 | NEL_BP1_FV03008.ZSC | BP1 FV03008 Circulation Valve CLOSED
NEL_BP1_FV03008_ZSO | BP1 | BP1 FV03008 Circulation Valve OPEN | On | USCNEL207 | NEL_BP1_FV03008.ZSO | BP1 FV03008 Circulation Valve OPEN
NEL_BP1_HT02001_AUX | BP1 | BP1 HT02001 Tank Heater Aux | Off | USCNEL207 | NEL_BP1_HT02001.AUX | BP1 HT02001 Tank Heater Aux Stopped
NEL_BP1_HT02001_PBE_HMI | BP1 | BP1 HT02001 Tank Heater PBE | Off | USCNEL207 | NEL_BP1_HT02001.PBE_HMI
NEL_BP1_HT02001_PBS_HMI | BP1 | BP1 HT02001 Tank Heater PBS | Off | USCNEL207 | NEL_BP1_HT02001.PBS_HMI
NEL_BP1_HT03002_AUX | BP1 | BP1 HT03002 In-Line Heater AUX | Off | USCNEL207 | NEL_BP1_HT03002.AUX | BP1 HT03002 In-Line Heater AUX Stopped
NEL_BP1_HT03002_CYCLE_MODE | BP1 | BP1 HT03002 In-Line Heater in Cycle Mode | On | USCNEL207 | NEL_BP1_HT03002_CYCLE_MODE | BP1 HT03002 In-Line Heater in Cycle Mode
NEL_BP1_HT03002_CYCLE_OFF | BP1 |  | MIN | 60 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_HT03002_CYCLE_OFF
NEL_BP1_HT03002_CYCLE_ON | BP1 |  | MIN | 180 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_HT03002_CYCLE_ON
NEL_BP1_HT03002_MODE_AUTO | BP1 | BP1 HT03002 In-Line Heater Auto | On | USCNEL207 | NEL_BP1_HT03002.MODE_AUTO | BP1 HT03002 In-Line Heater Auto
NEL_BP1_HT03002_PBE_HMI | BP1 | BP1 HT03002 In-Line Heater PBE | Off | USCNEL207 | NEL_BP1_HT03002.PBE_HMI
NEL_BP1_HT03002_PBS_HMI | BP1 | BP1 HT03002 In-Line Heater PBS | Off | USCNEL207 | NEL_BP1_HT03002.PBS_HMI
NEL_BP1_LT02006_ENG | BP1 | BP1 LT02006 Tank Level Inches | IN" | 164.5 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_LT02006.ENG
NEL_BP1_LT02006_PCT | BP1 | BP1 LT02006 Tank Level Percent | PCT | 100 | 0 | 0 | 0 | USCNEL207 | NEL_BP1_LT02006.PCT | BP1 LT02006 Tank Level Alarm
NEL_BP1_PU002_AUX | BP1 | BP1 PU002 Circ Pump AUX | Off | USCNEL207 | NEL_BP1_PU002.AUX | BP1 PU002 Circ Pump AUX Stopped
NEL_BP1_PU002_MODE_AUTO | BP1 | BP1 PU002 Circ Pump AUTO | On | USCNEL207 | NEL_BP1_PU002.MODE_AUTO | BP1 PU002 Circ Pump AUTO
NEL_BP1_PU002_PBE_HMI | BP1 | BP1 PU002 Circ Pump PBE | Off | USCNEL207 | NEL_BP1_PU002.PBE_HMI
NEL_BP1_PU002_PBS_HMI | BP1 | BP1 PU002 Circ Pump PBS | Off | USCNEL207 | NEL_BP1_PU002.PBS_HMI
NEL_BP1_PU013_AUX | BP1 | BP1 PU013 Transfer Pump AUX | Off | USCNEL207 | NEL_BP1_PU013.AUX | BP1 PU013 Transfer Pump AUX Stopped
NEL_BP1_PU013_MODE_AUTO | BP1 | BP1 PU013 Transfer Pump AUTO | On | USCNEL207 | NEL_BP1_PU013.MODE_AUTO | BP1 PU013 Transfer Pump AUTO
NEL_BP1_PU013_PBE_HMI | BP1 | BP1 PU013 Transfer Pump PBE | Off | USCNEL207 | NEL_BP1_PU013.PBE_HMI
NEL_BP1_PU013_PBS_HMI | BP1 | BP1 PU013 Transfer Pump PBS | Off | USCNEL207 | NEL_BP1_PU013.PBS_HMI
NEL_BP1_TS02013_IND | BP1 | BP1 TS02013 Temp Switch at 135 | On | USCNEL207 | NEL_BP1_TS02013.IND | BP1 TS02013 Temp Switch at 135
B_PETCOKE_AL2O3 | Coal_Feed | BAKERSFIELD PET COKE % AL2O3 IN ASH | % | 50 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:17
B_PETCOKE_ASH | Coal_Feed | Bakersfield Pet Coke % Ash | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F71:7
B_PETCOKE_COKEBLEND% | Coal_Feed | BAKERSFIELD PET COKE % BLEND IN COKE BLEND | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F71:18
B_PETCOKE_MMBTUTON | Coal_Feed | BAKERSFIELD PET. COKE MMBTU/ton | MMBTU/ton | 40 | 0.1 | 0 | 5 | PLC_FLTWRITE | F71:8
BC4504C_ACT | Coal_Feed | BC 504-C ACTUAL SPEED | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:187 | BC 504-C ACTUAL SPEED
BC4504C_ACTBLEND | Coal_Feed | BC 504-C ACTUAL COKE BLEND % | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:243 | BC 504-C ACTUAL COKE BLEND %
BC4504C_BLENDHIGHALM | Coal_Feed | BC 504-C COKE BLEND % ABOVE SETPOINT > 2 MIN | On | PLC_ALARM | B101/223 | BC 504-C COKE BLEND % ABOVE SETPOINT > 2 MIN
BC4504C_BLENDLOWALM | Coal_Feed | BC 504-C COKE BLEND % BELOW SETPOINT > 2 MIN | On | PLC_ALARM | B101/133 | BC 504-C COKE BLEND % BELOW SETPOINT > 2 MIN
BC4504C_IM | Coal_Feed | BC 4-504-C INTERLOCKS MET | None | PLC_DISCREAD | B3/293 | BC 4-504-C INTERLOCKS MET
BC4504C_PIDSP | Coal_Feed | BC 504-C PID SP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N81:2 | BC 504-C PID SP
BC4504C_SP | Coal_Feed | BC 4-504-C SPEED SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:27 | BC 4-504-C SPEED SETPOINT
BC4504C_SPD | Coal_Feed | BC 504-C VFD SPEED | % | 100 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:65 | BC 504-C VFD SPEED
BC4504C_TOG | Coal_Feed | BC 504-C AUTO TOGGLE | None | PLC_DISCWRITE | B100/225 | BC 504-C AUTO TOGGLE
BC4504C_WEIGHSCALE | Coal_Feed | BC 504-C ACTUAL TPH COKE | TPH | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:68 | BC 504-C ACTUAL TPH COKE
BC4504CACT_ALM | Coal_Feed | BC 504-C VFD AT 100% - SLOW DOWN COAL FEED | On | PLC_ALARM | B101/263 | BC 504-C VFD AT 100% - SLOW DOWN COAL FEED
BC4504CFAULT_ALM | Coal_Feed | BC 504-C VFD FAULT | Off | PLC_ALARM | I:105/7 | BC 504-C VFD FAULT
BC4504CFTS_ALM | Coal_Feed | BC 504-C FAILED TO START | On | PLC_ALARM | B101/185 | BC 504-C FAILED TO START
BC4504CMS_X | Coal_Feed | BC 504-C AUX FDBK | None | PLC_DISCREAD | I:105/04 | BC 504-C AUX FDBK
BC4504CPC_AM | Coal_Feed | BC 504-C PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100:4/15 | BC 504-C PID AUTO MANUAL 1=AUTO 0=MANUAL
BC4504CPID_CV | Coal_Feed | BC 504-C CONTROL VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N81:24 | BC 504-C CONTROL VARIABLE
BC4504CPID_DB | Coal_Feed | BC 504-C PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTWRITE | N81:9 | BC 504-C PID DEADBAND
BC4504CPID_DR | Coal_Feed | BC 504-C PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTWRITE | N81:5 | BC 504-C PID DR
BC4504CPID_ER | Coal_Feed | BC 504-C PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N81:15 | BC 504-C PID ERROR
BC4504CPID_PG | Coal_Feed | BC 504-C PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTWRITE | N81:3 | BC 504-C PID PG
BC4504CPID_PV | Coal_Feed | BC 504-C PROCESS VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N81:23 | BC 504-C PROCESS VARIABLE
BC4504CPID_RT | Coal_Feed | BC 504-C PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTWRITE | N81:4 | BC 504-C PID RT
BC4504CPID_TB | Coal_Feed | BC 504-C TIEBACK VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N81:25 | BC 504-C TIEBACK VARIABLE
BC4504CPID_UT | Coal_Feed | BC 504-C PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTWRITE | T4:275.PRE | BC 504-C PID UPDATE TIME
BC4506_IM | Coal_Feed | BC 506 INTERLOCKS MET | None | PLC_DISCREAD | B3/224 | BC 506 INTERLOCKS MET
BC4506_PBS | Coal_Feed | BC 506 PC START | None | PLC_DISCWRITE | B100/560 | BC 506 PC START
BC4506_PBT | Coal_Feed | BC 506 PC STOP | None | PLC_DISCWRITE | B100/561 | BC 506 PC STOP
BC4506_PCSP | Coal_Feed | BC 506 TPH PC SP | TPH | 200 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:11 | BC 506 TPH PC SP
BC4506_SP | Coal_Feed | BC 506 TPH SP | TPH | 200 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:432 | BC 506 TPH SP
BC4506_WEIGHSCALE | Coal_Feed | BC 506 TPH | TPH | 200 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:67 | BC 506 TPH
BC4506C_PIDSP | Coal_Feed | COKE % FEED SP TO CONTROL BC 506-C | % | 100 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:5 | COKE % FEED SP TO CONTROL BC 506-C
BC4506FTS_ALM | Coal_Feed | BC 506 FAILED TO START | On | PLC_ALARM | B101/188 | BC 506 FAILED TO START
BC4506HORN_ALM | Coal_Feed | BC 506 START-UP HORN | None | PLC_ALARM | O:116/11 | BC 506 START-UP HORN
BC4506MS_X | Coal_Feed | BC 4506 AUX FDBK | Off | PLC_DISCREAD | I:107/01 | BC 506 STOPPED!!
BC4506PLUGGED_ALM | Coal_Feed | BC4-506 PLUGGED CHUTE ALARM | On | PLC_ALARM | B101/269 | BC 4-506 PLUGGED CHUTE ALARM
BC4506PLUGGED_BYP | Coal_Feed | BC4-506 PLUGGED CHUTE BYPASS | On | PLC_DISCWRITE | B100/541 | BC 4-506 PLUGGED CHUTE BYPASS
BC4506PLUGGED_TMR | Coal_Feed | BC4-506 PLUGGED CHUTE ALARM TIMER DONE | On | PLC_DISCREAD | T4:632.DN | BC 506 PLUGGED CHUTE TIMER DONE
BC4514_IM | Coal_Feed | BC 514 INTERLOCKS MET | None | PLC_DISCREAD | B3/226 | BC 514 INTERLOCKS MET
BC4514_PBS | Coal_Feed | BC 514 PC START | None | PLC_DISCWRITE | B100/562 | BC 514 PC START
BC4514_PBT | Coal_Feed | BC 514 PC STOP | None | PLC_DISCWRITE | B100/563 | BC 514 PC STOP
BC4514FTS_ALM | Coal_Feed | BC 514 FAILED TO START | On | PLC_ALARM | B101/189 | BC 514 FAILED TO START
BC4514MS_X | Coal_Feed | BC 514 AUX FDBK | Off | PLC_DISCREAD | I:107/04 | BC 514 STOPPED!!
BC4516_AUTOS | Coal_Feed | BC 516 AUTO STOP | None | PLC_DISCREAD | B3/477 | BC 516 AUTO STOP
BC4516_IM | Coal_Feed | BC 516 INTERLOCKS MET | None | PLC_DISCREAD | B3/236 | BC 516 INTERLOCKS MET
BC4516_PBS | Coal_Feed | BC 516 PC START | None | PLC_DISCWRITE | B100/572 | BC 516 PC START
BC4516_PBT | Coal_Feed | BC 516 PC STOP | None | PLC_DISCWRITE | B100/573 | BC 516 PC STOP
BC4516FTS_ALM | Coal_Feed | BC 516 COAL SYSTEM BELT CONVEYOR FAILED TO START | On | PLC_ALARM | B101/190 | BC 516 COAL SYSTEM BELT CONVEYOR FAILED TO START
BC4516HORN_ALM | Coal_Feed | BC 516 & 514 START-UP HORN | None | PLC_ALARM | O:16/12 | BC 516 & 514 START-UP HORN
BC4516MS_X | Coal_Feed | BC 516 AUX FDBK | Off | PLC_DISCREAD | I:221/13 | BC 516 STOPPED!!
BC506MS_BYP | Coal_Feed | BC 506 ZERO SPEED BYPASS | On | PLC_DISCWRITE | B100/533 | BC 506 ZERO SPEED BYPASSED
BC506MSF_ALM | Coal_Feed | BC 506 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/574 | BC 506 MOTION SWITCH FAILURE
BE4521_IM | Coal_Feed | BE 521 INTERLOCKS MET | None | PLC_DISCREAD | B3/64 | BE 521 INTERLOCKS MET
BE4521_JOG | Coal_Feed | BE 521 JOG SWITCH INSERTED | On | PLC_ALARM | I:15/12 | BE 521 JOG SWITCH INSERTED
BE4521_PBS | Coal_Feed | BE 521 PC START | None | PLC_DISCWRITE | B100/565 | BE 521 PC START
BE4521_PBT | Coal_Feed | BE 521 PC STOP | None | PLC_DISCWRITE | B100/564 | BE 521 PC STOP
BE4521FTS_ALM | Coal_Feed | BE 521 FAILED TO START | On | PLC_ALARM | B101/191 | BE 521 FAILED TO START
BE4521MS_BYP | Coal_Feed | BE 521 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/525 | BE 521 MOTION SWITCH BYPASSED
BE4521MS_X | Coal_Feed | BE 521 AUX FDBK | Off | PLC_DISCREAD | I:221/11 | BE 521 STOPPED!!
BE4521MSF_ALM | Coal_Feed | BE 521 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/536 | BE 521 MOTION SWITCH FAILURE
BE521_IT_ALARM | Coal_Feed |  | On | PLC_DISCREAD | B33/244 | BE-521 High Amps
BE521_IT_AMPS | Coal_Feed |  | Amps | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:84
COAL_AL2O3 | Coal_Feed | COAL % AL2O3 IN ASH | % | 50 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:14
COAL_ASH | Coal_Feed | Coal % Ash | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F71:9
COAL_MMBTUTON | Coal_Feed | COAL MMBTU/ton | MMBTU/ton | 40 | 0.1 | 0 | 5 | PLC_FLTWRITE | F9:251
COALAUTOSHTDWN_ALM | Coal_Feed | COAL SYSTEM AUTO SHUTDOWN IN 5 MIN | On | PLC_ALARM | B101/127 | COAL SYSTEM AUTO SHUTDOWN IN 5 MIN
COALAUTOSHTDWN_PCRESET | Coal_Feed | PC STOP COAL SYSTEM AUTO SHUTDOWN | On | PLC_DISCWRITE | B100/52 | PC STOP COAL SYSTEM AUTO SHUTDOWN
COALBINFILL_PBT | Coal_Feed | COAL BIN FILL AUTO STOP | None | PLC_DISCWRITE | B100/182 | COAL BIN FILL AUTO STOP
COALBINFILLK2ONLY_PBT | Coal_Feed | COAL BIN FILL CONTROL KILN 2 ONLY | None | PLC_DISCWRITE | B100/198 | COAL BIN FILL CONTROL KILN 2 ONLY
COKEBLEND_AL2O3 | Coal_Feed | PET COKE BLEND % AL2O3 IN ASH | % | 50 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:448
COKEBLEND_ASH | Coal_Feed | Pet Coke Blend % Ash | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:447
COKEBLEND_MMBTUTON | Coal_Feed | PET. COKE BLEND MMBTU/ton | MMBTU/ton | 40 | 0.1 | 0 | 5 | PLC_FLTREAD | F9:446
DG4514_SWITCHTIMER | Coal_Feed | DG 514 TIMER TO ALLOW GATE TO SWITCH FOR INTERLOCK | None | PLC_DISCREAD | T4:66.TT | DG 514 TIMER TO ALLOW GATE TO SWITCH FOR INTERLOCK
DG4514_TOBC514 | Coal_Feed | DG 514 TO BC 514 | None | PLC_DISCWRITE | B100/566 | DG 514 TO BC 514
DG4514_TORC522 | Coal_Feed | DG 514 TO RC 522 | None | PLC_DISCWRITE | B100/567 | DG 514 TO RC 522
DG4514STUCK_ALM | Coal_Feed | DG 514 IS STUCK | On | PLC_ALARM | B101/27 | DG 514 IS STUCK
DG4514TOBC514MS_X | Coal_Feed | DG 514 IS SET TO BC 514 | None | PLC_DISCREAD | I:221/00 | DG 514 IS SET TO BC 514
DG4514TORC522MS_X | Coal_Feed | DG 514 IS SET TO RC 522 | None | PLC_DISCREAD | I:221/01 | DG 514 IS SET TO RC 522
DIESEL_MMBTUGAL | Coal_Feed | #2 DIESEL MMBTU/gal | MMBTU/gal | 1 | 0.001 | 0 | 0 | PLC_FLTWRITE | F9:388
FN4527_IM | Coal_Feed | FN 527 INTERLOCKS MET | None | PLC_DISCREAD | B3/238 | FN 527 INTERLOCKS MET
FN4527_PBS | Coal_Feed | START FN 527 | None | PLC_DISCWRITE | B100/574 | START FN 527
FN4527_PBT | Coal_Feed | STOP FN 527 | None | PLC_DISCWRITE | B100/575 | STOP FN 527
FN4527FTS_ALM | Coal_Feed | FN 527 FAILED TO START | On | PLC_ALARM | B101/194 | FN 527 FAILED TO START
FN4527INT_BYP | Coal_Feed | FN 527 INTERLOCK BYPASS ON | On | PLC_DISCWRITE | B3/229 | FN 527 INTERLOCK BYPASS ON
FN4527MS_X | Coal_Feed | FN 527 FUEL BIN DUST COLLECTOR FAN | Off | PLC_DISCREAD | I:220/14 | FN 527 STOPPED!!
FUELSTARTBINS_PBS | Coal_Feed | SYSTEM START FOR SOLID FUEL SYSTEM TO BOTH SILOS | None | PLC_DISCWRITE | B100/530
FUELSTARTK1_PBS | Coal_Feed | SYSTEM START FOR SOLID FUEL SYSTEM TO KILN 1 SILO | None | PLC_DISCWRITE | B100/526
FUELSTARTK2_PBS | Coal_Feed | SYSTEM START FOR SOLID FUEL SYSTEM TO KILN 2 SILO | None | PLC_DISCWRITE | B100/527
FUELSTARTSTOCK_PBS | Coal_Feed | SYSTEM START FOR SOLID FUEL SYSTEM TO STOCKPILE | None | PLC_DISCWRITE | B100/522
K1COALBINHIGH_ALM | Coal_Feed | KILN 1 COAL BIN HIGH LEVEL!! | On | PLC_ALARM | B101/162 | KILN 1 COAL BIN HIGH LEVEL!!
K1FUELBIN_MEAS | Coal_Feed | KILN 1 FUEL BIN LEVEL MEASUREMENT (FT) | ft | 44 | 1 | 0 | 0 | PLC_INTWRITE | N102:73 | KILN 1 FUEL BIN LEVEL MEASUREMENT (FT)
K1FUELBIN_MEASTON | Coal_Feed | KILN 1 FUEL BIN TON MEASUREMENT | ton | 500 | 1 | 0 | 0 | PLC_FLTREAD | F9:269 | KILN 1 FUEL BIN TON MEASUREMENT
K2COALBINHIGH_ALM | Coal_Feed | KILN #2 COAL BIN HIGH LEVEL!! | On | PLC_ALARM | B101/163 | KILN #2 COAL BIN HIGH LEVEL!!
K2COALBINLOW_ALM | Coal_Feed | KILN 2 COAL BIN LOW LEVEL | On | PLC_ALARM | I:17/02 | KILN 2 COAL BIN LOW LEVEL
K2FUELBIN_MEAS | Coal_Feed | KILN 2 FUEL BIN LEVEL MEASUREMENT (FT) | ft | 36 | 1 | 0 | 0 | PLC_INTWRITE | N102:74 | KILN 2 FUEL BIN LEVEL MEASUREMENT (FT)
K2FUELBIN_MEASTON | Coal_Feed | KILN 2 FUEL BIN TON MEASUREMENT | ton | 650 | 1 | 0 | 0 | PLC_FLTREAD | F9:270 | KILN 2 FUEL BIN TON MEASUREMENT
PETCOKE_AL2O3 | Coal_Feed | PET COKE % AL2O3 IN ASH | % | 50 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:16
PETCOKE_ASH | Coal_Feed | Pet Coke % Ash | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F71:10
PETCOKE_COKEBLEND% | Coal_Feed | PET COKE % BLEND IN COKE BLEND | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:30
PETCOKE_MMBTUTON | Coal_Feed | PET. COKE MMBTU/ton | MMBTU/ton | 40 | 0.1 | 0 | 5 | PLC_FLTWRITE | F9:250
RA527MS_X | Coal_Feed | RA 527 AUX FDBK | Off | PLC_DISCREAD | I:220/16 | RA 527 STOPPED!!
RC4505_IM | Coal_Feed | RC 505 INTERLOCKS MET | None | PLC_DISCREAD | B3/233 | RC 505 INTERLOCKS MET
RC4505_PBS | Coal_Feed | START RC 505 | None | PLC_DISCWRITE | B100/580 | START RC 505
RC4505_PBT | Coal_Feed | STOP RC 505 | None | PLC_DISCWRITE | B100/581 | STOP RC 505
RC45051FTS_ALM | Coal_Feed | RC 505-1 FAILED TO START | On | PLC_ALARM | B101/186 | RC 505-1 FAILED TO START
RC45051MS_X | Coal_Feed | FDBK RC 505-1 | Off | PLC_DISCREAD | I:106/16 | RC 505 MOTOR #1 STOPPED!!
RC45052FTS_ALM | Coal_Feed | RC 505-2 FAILED TO START | On | PLC_ALARM | B101/187 | RC 505-2 FAILED TO START
RC45052MS_X | Coal_Feed | FDBK RC 505-2 | Off | PLC_DISCREAD | I:107/00 | RC 505 MOTOR #2 STOPPED!!
RC4522_IM | Coal_Feed | RC 522 INTERLOCKS MET | None | PLC_DISCREAD | B3/230 | RC 522 INTERLOCKS MET
RC4522_PBS | Coal_Feed | START RC 522 | None | PLC_DISCWRITE | B100/568 | START RC 522
RC4522_PBT | Coal_Feed | STOP RC 522 | None | PLC_DISCWRITE | B100/569 | STOP RC 522
RC45221_IT | Coal_Feed | RC 522-1 AMPS | Amps | 50 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:83 | RC 522-1 AMPS
RC45221FTS_ALM | Coal_Feed | RC 522-1 FAILED TO START | On | PLC_ALARM | B101/192 | RC 522-1 FAILED TO START
RC45221MS_X | Coal_Feed | FDBK RC 522-1 | Off | PLC_DISCREAD | I:221/05 | RC 522-1 STOPPED!!
RC45222_IT | Coal_Feed | RC 522-2 AMPS | Amps | 50 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:85 | RC 522-2 AMPS
RC45222FTS_ALM | Coal_Feed | RC 522-2 FAILED TO START | On | PLC_ALARM | B101/193 | RC 522-2 FAILED TO START
RC45222MS_X | Coal_Feed | FDBK RC 522-2 | Off | PLC_DISCREAD | I:221/07 | RC 522-2 STOPPED!!
RC4522AMP_ALM | Coal_Feed | RC 522 HIGH AMPS!! | On | PLC_ALARM | B101/26 | RC 522 HIGH AMPS!!
SFS_BAKECOKESTOCK | Coal_Feed | Bakersfield Coke to Stockpile | None | PLC_DISCWRITE | B100/546
SFS_COAL_PRIMARY | Coal_Feed |  | None | PLC_DISCWRITE | B100/540 | CA1 345 PC STOP
SFS_COKE_PRIMARY | Coal_Feed |  | None | PLC_DISCWRITE | B100/539 | CA1 345 PC STOP
SFS_COKEHOPPER_ALM | Coal_Feed | COKE HOPPER IS EMPTY - SYSTEM SHUTDOWN! | On | PLC_ALARM | B101/564 | COKE HOPPER IS EMPTY OR PLUGGED - MAIN FEED STOPPED!!
SFS_PETCOKESTOCK | Coal_Feed | Pet Coke to the Stockpile | None | PLC_DISCWRITE | B100/548
SFS_PURGECOKEHOPPER | Coal_Feed | Purge the Coke Hopper to the Stockpile | None | PLC_DISCWRITE | B100/549
SFS_STARTCONFIG | Coal_Feed | Solid Fuel System Start Configuration Code # |  | 20 | 0 | 0 | 0 | PLC_INTWRITE | N102:120
VB504DMS_X | Coal_Feed | FDBK VB504CMS_X | None | PLC_DISCREAD | O:115/11 | FDBK VB504CMS_X
VF4504_AUTOS | Coal_Feed | VF 504-A&B AUTO STOP | None | PLC_DISCREAD | B3/476 | VF 504-A&B AUTO STOP
VF4504_PBS | Coal_Feed | START VF 504A & B | None | PLC_DISCWRITE | B100/576 | START VF 504A & B
VF4504_PBT | Coal_Feed | STOP VF 504 A & B | None | PLC_DISCWRITE | B100/577 | STOP VF 504 A & B
VF4504A_AUTO | Coal_Feed | VF 504 A IN AUTO | None | PLC_DISCREAD | I:107/10 | VF 504 A IN AUTO
VF4504A_DISCONNECT | Coal_Feed | VF 504 A DISCONNECT UP | None | PLC_DISCREAD | I:107/11 | VF 504 A DISCONNECT UP
VF4504A_IM | Coal_Feed | VF 504 A INTERLOCKS MET | None | PLC_DISCREAD | B3/240 | VF 504 A INTERLOCKS MET
VF4504A_SP | Coal_Feed | VF 504-A VFD SP | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:433 | VF 504-A VFD SP
VF4504AFTS_ALM | Coal_Feed | VF 504-A FAILED TO START | On | PLC_ALARM | B101/39 | VF 504-A FAILED TO START
VF4504AMS_X | Coal_Feed | FDBK VF 504A RUNNING | None | PLC_DISCREAD | I:106/12 | FDBK VF 504A RUNNING
VF4504B_AUTO | Coal_Feed | VF 504-B IN AUTO | None | PLC_DISCREAD | I:107/12 | VF 504-B IN AUTO
VF4504B_DISCONNECT | Coal_Feed | VF 504-B DISCONNECT UP | None | PLC_DISCREAD | I:107/13 | VF 504-B DISCONNECT UP
VF4504B_IM | Coal_Feed | VF 504-B INTERLOCKS MET | None | PLC_DISCREAD | B3/713 | VF 504-B INTERLOCKS MET
VF4504B_SP | Coal_Feed | VF 504-B VFD SP | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:434 | VF 504-B VFD SP
VF4504BFTS_ALM | Coal_Feed | VF 504-B FAILED TO START | On | PLC_ALARM | B101/184 | VF 504-B FAILED TO START
VF4504BMS_X | Coal_Feed | FDBK 504B RUNNING | None | PLC_DISCREAD | I:106/14 | FDBK 504B RUNNING
VF504A_HIGHSP | Coal_Feed | VF 504-A PC High % Speed SP | % | 100 | 1 | 0 | 5 | PLC_INTWRITE | N102:115
VF504A_LOWSP | Coal_Feed | VF 504-A PC Low % Speed SP | % | 95 | 1 | 0 | 0 | PLC_INTWRITE | N102:114
VF504B_HIGHSP | Coal_Feed | VF 504-B PC High % Speed SP | % | 100 | 1 | 0 | 5 | PLC_INTWRITE | N102:117
VF504B_LOWSP | Coal_Feed | VF 504-B PC Low % Speed SP | % | 95 | 1 | 0 | 0 | PLC_INTWRITE | N102:116
DB2HRSWOHL_ALM | Dust_Blending | 2 Hours Runtime w/o High Level at Blending Bin | On | PLC_ALARM | B101/573 | Dust Blending 2 Hours Runtime without High Level! Check for Plugged Line!
DUSTAUTO_ACC | Dust_Blending | TIME UNTIL DUST BLEND AUTO START ACCUMULATED | sec | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:209.ACC | TIME UNTIL DUST BLEND AUTO START ACCUMULATED
DUSTAUTO_PRE | Dust_Blending | PRESET TIME TILL DUST BLEND AUTO START | sec | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:209.PRE | PRESET TIME TILL DUST BLEND AUTO START
DUSTAUTO_TT | Dust_Blending | DUST BLEND AUTO START TIMER TIMING | None | PLC_DISCREAD | T4:209.TT | DUST BLEND AUTO START TIMER TIMING
DUSTBLEND_AUTO | Dust_Blending | DUST BLENDING SYSTEM IN AUTO FILL MODE | Off | PLC_DISCREAD | B100/242 | DUST BLENDING AUTO CONTROL OFF
DUSTBLEND_MANUAL | Dust_Blending | DUST BLENDING SYSTEM MANUAL CONTROL | Off | PLC_DISCREAD | B100/243 | DUST BLENDING MANUAL CONTROL OFF
DUSTBLEND_PBS | Dust_Blending | PC START DUST BLENDING SYSTEM | None | PLC_DISCWRITE | B100/238 | PC START DUST BLENDING SYSTEM
DUSTBLEND_PBT | Dust_Blending | PC STOP DUST BLENDING SYSTEM | None | PLC_DISCWRITE | B100/239 | PC STOP DUST BLENDING SYSTEM
DUSTBLENDAUTO_PBS | Dust_Blending | DUST BLENDING SYSTEM AUTO MODE ON | None | PLC_DISCWRITE | B100/240 | DUST BLENDING SYSTEM AUTO MODE ON
DUSTBLENDAUTO_PBT | Dust_Blending | DUST BLENDING AUTO MODE OFF | None | PLC_DISCWRITE | B100/241 | DUST BLENDING AUTO MODE OFF
DUSTBLENDHI_ALM | Dust_Blending | DUST BLENDING BIN HIGH LEVEL! | On | PLC_ALARM | I:17/01 | DUST BLENDING BIN HIGH LEVEL!
FN4452FTS_ALM | Dust_Blending | FN 452 FAILED TO START | On | PLC_ALARM | B101/497 | FN 452 FAILED TO START
FN4452MS_X | Dust_Blending | FN 4462 AUX FDBK | None | PLC_DISCREAD | I:17/00 | FN 4462 AUX FDBK
FN4452STOP_ACC | Dust_Blending | FN 452 STOP TIMER ACCUMULITIVE |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:220.ACC | FN 452 STOP TIMER ACCUMULITIVE
FN4452STOP_PRE | Dust_Blending | FN 452 STOP TIMER PRESET |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:220.PRE | FN 452 STOP TIMER PRESET
FN4452STOP_TT | Dust_Blending | FN 452 STOP TIMER TIMING | None | PLC_DISCREAD | T4:220.TT | FN 452 STOP TIMER TIMING
NEL_LKD_BL460_XT_PSI | Dust_Blending |  | PSI | 20 | 0 | 0 | 0 | PLC_FLTREAD | F9:19 | 2
NEL_LKD_DG460_ALM | Dust_Blending |  | On | PLC_DISCREAD | B3:97/1 | LKD_DG460_FAULT
NEL_LKD_DG460_CLOSE | Dust_Blending |  | None | PLC_DISCREAD | I:23/3
NEL_LKD_PC460_PLUGGED_ALARM | Dust_Blending | PC 460_LINE PLUGGED_ALARM | On | PLC_DISCREAD | B101/584 | DUST CONVEYING LINE PLUGGED
NEL_LKD_PC460_PLUGGED_RESET | Dust_Blending | PC 460_LINE PLUGGED - RESET | On | PLC_DISCWRITE | B100/864 | PC 460 LINE PLUGGED - RESET
NEL_LKD_PLUGGED_LINE_PC_RESET | Dust_Blending | PC 460_PLUGGED_LINE_PC_RESET | None | PLC_DISCREAD | B101/585 | PC 460 LINE PLUGGED - RESET
PC4460_IT | Dust_Blending | PC 4460 Current Reading | Amps | 150 | 0 | 0 | 0 | KILN1_BH_READ | NEL_LKD_PC0460_IT | PC0460 High Amps!
PC4460FTS_ALM | Dust_Blending | PC 460 FAILED TO START | On | PLC_ALARM | B101/498 | PC 460 FAILED TO START
PC4460MS_X | Dust_Blending | PC 4460 AUX FDBK | None | KILN1_BH_READ | NEL_LKD_PC0460_AUX | PC 4460 AUX FDBK
PC4460STOP_ACC | Dust_Blending | PC 460 STOP TIMER ACCUMULATIVE |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:215.ACC | PC 460 STOP TIMER ACCUMULATIVE
PC4460STOP_PRE | Dust_Blending | PC 460 STOP TIMER PRESET |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:215.PRE | PC 460 STOP TIMER PRESET
PC4460STOP_TT | Dust_Blending | PC 460 STOP TIMER TIMING | None | PLC_DISCREAD | T4:215.TT | PC 460 STOP TIMER TIMING
PM4461_INT | Dust_Blending | PN 461 INTERLOCKS MET | None | PLC_DISCREAD | B100/248 | PN 461 INTERLOCKS MET
PM4461FTS_ALM | Dust_Blending | PM 461 FAILED TO START | On | PLC_ALARM | B101/499 | PM 461 FAILED TO START
PM4461MS_X | Dust_Blending | SCREW PUMP 461 AUX FDBK | None | PLC_DISCREAD | I:57/01 | SCREW PUMP 461 AUX FDBK
PM4461START_ACC | Dust_Blending | PM 461 START TIMER ACCUMULATIVE |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:210.ACC | PM 461 START TIMER ACCUMULATIVE
PM4461START_PRE | Dust_Blending | PM 461 START TIMER PRESET |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:210.PRE | PM 461 START TIMER PRESET
PM4461START_TT | Dust_Blending | PM 461 START TIMER TIMING | None | PLC_DISCREAD | T4:210.TT | PM 461 START TIMER TIMING
PM4461STOP_ACC | Dust_Blending | PM 461 STOP TIMER ACCUMULATIVE |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:214.ACC | PM 461 STOP TIMER ACCUMULATIVE
PM4461STOP_PRE | Dust_Blending | PM 461 STOP TIMER PRESET |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:214.PRE | PM 461 STOP TIMER PRESET
PM4461STOP_TT | Dust_Blending | PM 461 STOP TIMER TIMING | None | PLC_DISCREAD | T4:214.TT | PM 461 STOP TIMER TIMING
SG4462_INT | Dust_Blending | SG 462 INTERLOCKS MET | None | PLC_DISCREAD | B100/249 | SG 462 INTERLOCKS MET
SG4462CLOSE_ACC | Dust_Blending | SG 462 CLOSE TIMER ACCUMULATIVE | SEC | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:212.ACC | SG 462 CLOSE TIMER ACCUMULATIVE
SG4462CLOSE_PRE | Dust_Blending | SG 462 CLOSE TIMER PRESET | SEC | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:212.PRE | SG 462 CLOSE TIMER PRESET
SG4462CLOSE_TT | Dust_Blending | SG 462 CLOSE TIMER TIMING | None | PLC_DISCREAD | T4:212.TT | SG 462 CLOSE TIMER TIMING
SG4462MS_X | Dust_Blending | KNIFE GATE OPEN (OUTPUT SIGNAL) | None | PLC_DISCREAD | O:57/3 | KNIFE GATE OPEN (OUTPUT SIGNAL)
SG4462OPEN_ACC | Dust_Blending | SG 462 OPEN TIMER ACCUMULATIVE | SEC | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:213.ACC | SG 462 OPEN TIMER ACCUMULATIVE
SG4462OPEN_PRE | Dust_Blending | SG 462 OPEN TIMER PRESET | SEC | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:213.PRE | SG 462 OPEN TIMER PRESET
SG4462OPEN_TT | Dust_Blending | SG 462 OPEN TIMER TIMING | None | PLC_DISCREAD | T4:213.TT | SG 462 OPEN TIMER TIMING
SG4462OPENTIME | Dust_Blending | TIME SG 462 OPEN | HRS | 1000 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:102 | TIME SG 462 OPEN
SG4462OPENTIME-DAY | Dust_Blending | SG 462 TIME OPEN - DAILY | HRS | 1000 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:126 | SG 462 TIME OPEN - DAILY
SG4462START_ACC | Dust_Blending | SG 462 START SEQUENCE TIMER ACCUMULATIVE | SEC | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:211.ACC | SG 462 START SEQUENCE TIMER ACCUMULATIVE
SG4462START_PRE | Dust_Blending | SG 462 START SEQUENCE TIMER PRESET |  | 30000 | 0 | 0 | 0 | PLC_INTREAD | T4:211.PRE | SG 462 START SEQUENCE TIMER PRESET
SG4462START_TT | Dust_Blending | SG 462 START SEQUENCE TIMER TIMING | None | PLC_DISCREAD | T4:211.TT | SG 462 START SEQUENCE TIMER TIMING
BE4423_BYP | Front_System | BE 423 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/516 | BE 423 MOTION SWITCH BYPASS ON
BE4423_IM | Front_System | BE 423 INTERLOCKS MET | None | PLC_DISCREAD | B3/206 | BE 423 INTERLOCKS MET
BE4423_IT | Front_System | BE 423 AMPS | A | 40 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:81 | BE 423 AMPS
BE4423_JP | Front_System | BE 423 JOG PLUG INSERTED | On | PLC_ALARM | I:220/10 | BE 423 JOG PLUG INSERTED
BE4423_PBS | Front_System | BE 423 PC START | None | PLC_DISCWRITE | B100/185 | BE 423 PC START
BE4423_PBT | Front_System | BE 423 PC STOP | None | PLC_DISCWRITE | B100/201 | BE 423 PC STOP
BE4423FTS_ALM | Front_System | BE 423 FAILED TO START | On | PLC_ALARM | B101/351 | BE 423 FAILED TO START
BE4423HIAMP_ALM | Front_System | BE 423 HIGH AMPS | On | PLC_ALARM | B101/485 | BE 423 HIGH AMPS
BE4423MS_X | Front_System | BE 423 AUX CONTACT | Off | PLC_DISCREAD | I:15/07 | BE 423 STOPPED
BE4423MSF_ALM | Front_System | BE 423 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/530 | BE 423 MOTION SWITCH FAILURE
BE44241_BYP | Front_System | BE 424-1 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/76 | BE 424-1 MOTION SWITCH BYPASSED
BE44241_IM | Front_System | BE 424-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/62 | BE 424-1 INTERLOCKS MET
BE44241_IT | Front_System | BE 424-1 AMPS | A | 75 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:185 | BE 424-1 AMPS
BE44241_JP | Front_System | BE 424-1 JOG PLUG INSERTED | On | PLC_ALARM | I:220/07 | BE 424-1 JOG PLUG INSERTED
BE44241_PBS | Front_System | BE 424-1 PC START | None | PLC_DISCWRITE | B100/180 | BE 424-1 PC START
BE44241_PBT | Front_System | BE 424-1 PC STOP | None | PLC_DISCWRITE | B100/196 | BE 424-1 PC STOP
BE44241FTS_ALM | Front_System | BE 424-1 FAILED TO START | On | PLC_ALARM | B101/352 | BE 424-1 FAILED TO START
BE44241MS_X | Front_System | BE 424-1 AUX CONTACT | Off | PLC_DISCREAD | I:15/03 | BE 424-1 STOPPED
BE44241MSF_ALM | Front_System | BE 424-1 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/353 | BE 424-1 MOTION SWITCH FAILURE
BE44242_BYP | Front_System | BE 424-2 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/77 | BE 424-2 MOTION SWITCH BYPASSED
BE44242_IM | Front_System | BE 424-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/63 | BE 424-2 INTERLOCKS MET
BE44242_IT | Front_System | BE 424-2 AMPS | A | 75 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:186 | BE 424-2 AMPS
BE44242_JP | Front_System | BE 424-2 JOG PLUG INSERTED | On | PLC_ALARM | I:220/02 | BE 424-2 JOG PLUG INSERTED
BE44242_PBS | Front_System | BE 424-2 PC START | None | PLC_DISCWRITE | B100/181 | BE 424-2 PC START
BE44242_PBT | Front_System | BE 424-2 PC STOP | None | PLC_DISCWRITE | B100/197 | BE 424-2 PC STOP
BE44242FTS_ALM | Front_System | BE 424-2 FAILED TO START | On | PLC_ALARM | B101/354 | BE 424-2 FAILED TO START
BE44242MS_X | Front_System | BE 424-2 AUX CONTACT | Off | PLC_DISCREAD | I:15/04 | BE 424-2 STOPPED
BE44242MSF_ALM | Front_System | BE 424-2 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/355 | BE 424-2 MOTION SWITCH FAILURE
BE44242OFF_BYP | Front_System | FRONT SYSTEM SET TO MAKE ONLY -1/2 MATERIAL | On | PLC_DISCWRITE | B100/343 | FRONT SYSTEM SET TO MAKE ONLY -1/2 MATERIAL
BE4424C_AUTO | Front_System | BE 424-C IN AUTO | None | PLC_DISCREAD | I:230/01 | BE 424-C IN AUTO
BE4424C_BYP | Front_System | BE 424-C MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/305 | BE 424-C MOTION SWITCH BYPASSED
BE4424C_DISCONNECT | Front_System | BE 424-C DISCONNECT THROWN | None | PLC_DISCREAD | I:230/04 | BE 424-C DISCONNECT THROWN
BE4424C_IM | Front_System | BE 424-C INTERLOCKS MET | None | PLC_DISCREAD | B3/480 | BE 424-C INTERLOCKS MET
BE4424C_IT | Front_System | BE 424-C AMPS | A | 65 | 0.5 | 0 | 0 | PLC_FLTREAD | F8:123 | BE 424-C AMPS
BE4424C_JOG | Front_System | BE 424-C JOG PLUG INSERTED | On | PLC_ALARM | I:231/10 | BE 424-C JOG PLUG INSERTED
BE4424C_MSF | Front_System | BE 424-C MOTION SWITCH FAILURE | On | PLC_ALARM | B101/357 | BE 424-C MOTION SWITCH FAILURE
BE4424C_OVERLOADS | Front_System | BC 424-C OVERLOADS OUT | None | PLC_DISCREAD | I:230/03 | BC 424-C OVERLOADS OUT
BE4424C_PBS | Front_System | BE 424-C PC START | None | PLC_DISCWRITE | B100/304 | BE 424-C PC START
BE4424C_PBT | Front_System | BE 424-C PC STOP | None | PLC_DISCWRITE | B100/303 | BE 424-C PC STOP
BE4424CFTS_ALM | Front_System | BE 424-C FAILED TO START | On | PLC_ALARM | B101/356 | BE 424-C FAILED TO START
BE4424CMS_X | Front_System | BE 424-C AUX FDBK | Off | PLC_DISCREAD | I:230/02 | BE 424-C STOPPED
CA1_345_PBT | Front_System | CA 1 345 PC STOP | None | KILN1_BH_WRITE | CA1_345_PBT | CA1 345 PC STOP
CA4441_IM | Front_System | CA 441 INTERLOCKS MET | None | PLC_DISCREAD | B3/213 | CA 441 INTERLOCKS MET
CA4441_PBS | Front_System | CA 441 PC START | None | PLC_DISCWRITE | B100/191 | CA 441 PC START
CA4441_PBT | Front_System | CA 441 PC STOP | None | PLC_DISCWRITE | B100/207 | CA 441 PC STOP
CA4441FTS_ALM | Front_System | CA 441 FAILED TO START | On | PLC_ALARM | B101/370 | CA 441 FAILED TO START
CA4441MS_X | Front_System | CA 441 AUX CONTACT | Off | PLC_DISCREAD | I:14/10 | CA 441 STOPPED
DG4381MOVE_ALM | Front_System | DG 448-1 Gate Moved Alarm | None | PLC_ALARM | B101/556
DG4382MOVE_ALM | Front_System | DG 448-2 Gate Moved Alarm | None | PLC_ALARM | B101/557
DG4383MOVE_ALM | Front_System | DG 448-3 Gate Moved Alarm | None | PLC_ALARM | B101/558
DG4384MOVE_ALM | Front_System | DG 448-4 Gate Moved Alarm | None | PLC_ALARM | B101/559
DG4385MOVE_ALM | Front_System | DG 448-5 Gate Moved Alarm | None | PLC_ALARM | B101/560
DG4386MOVE_ALM | Front_System | DG 448-6 Gate Moved Alarm | None | PLC_ALARM | B101/561
DG4387MOVE_ALM | Front_System | DG 448-7 Gate Moved Alarm | None | PLC_ALARM | B101/562
DG4388MOVE_ALM | Front_System | DG 448-8 Gate Moved Alarm | None | PLC_ALARM | B101/568
DG438MOVE_PCACK | Front_System | PC Acknowledge that DG 448-1-8 Moved | None | PLC_DISCWRITE | B100/559
DG4422_PBO | Front_System | Change HM4422 to 3/8 mode | None | PLC_DISCWRITE | B105:10/3
DG4422_ZSC | Front_System | HM4422 in -1/8 mode | None | PLC_DISCWRITE | B105:10/6
DG4422_ZSO | Front_System | HM4422 in 3/8 mode | None | PLC_DISCWRITE | B105:10/5
DG4423_PBC | Front_System | Change HM4422 to-1/8 mode | None | PLC_DISCWRITE | B105:10/4
DG44381_TODG44382 | Front_System | DG 438-1 SET TO DG 438-2 | None | PLC_DISCREAD | I:35/10 | DG 438-1 SET TO DG 438-2
DG44381_TOVS4432 | Front_System | DG 438-1 SET TO VS 432 | None | PLC_DISCREAD | I:36/10 | DG 438-1 SET TO VS 432
DG44382_TOBE44241 | Front_System | DG 438-2 SET TO BE 424-1 | None | PLC_DISCREAD | I:36/11 | DG 438-2 SET TO BE 424-1
DG44382_TOBE44242 | Front_System | DG 438-1 SET TO BE 424-2 | None | PLC_DISCREAD | I:35/11 | DG 438-1 SET TO BE 424-2
DG44383_TODG44385 | Front_System | DG 438-3 SET TO DG 438-5 | None | PLC_DISCREAD | I:35/12 | DG 438-3 SET TO DG 438-5
DG44383_TODG44388 | Front_System | DG 438-3 SET TO DG 438-8 | None | PLC_DISCREAD | I:36/12 | DG 438-3 SET TO DG 438-8
DG44384_TODG44383 | Front_System | DG 438-4 SET TO DG 438-3 | None | PLC_DISCREAD | I:36/13 | DG 438-4 SET TO DG 438-3
DG44384_TODG44385 | Front_System | DG 438-4 SET TO DG 438-5 | None | PLC_DISCREAD | I:35/13 | DG 438-4 SET TO DG 438-5
DG44385_TOSC4426 | Front_System | DG 438-5 SET TO SC 426 | None | PLC_DISCREAD | I:36/14 | DG 438-5 SET TO SC 426
DG44385_TOSC4427 | Front_System | DG 438-5 SET TO SC 427 | None | PLC_DISCREAD | I:35/14 | DG 438-5 SET TO SC 427
DG44386_TODG44382 | Front_System | DG 438-6 SET TO DG 438-2 | None | PLC_DISCREAD | I:36/15 | DG 438-6 SET TO DG 438-2
DG44386_TODG44387 | Front_System | DG 438-6 SET TO DG 438-7 | None | PLC_DISCREAD | I:35/15 | DG 438-6 SET TO DG 438-7
DG44387_TOBE44241 | Front_System | DG 438-7 SET TO BE 424-1 | None | PLC_DISCREAD | I:35/16 | DG 438-7 SET TO BE 424-1
DG44387_TORC4422 | Front_System | DG 438-7 SET TO RC 422 | None | PLC_DISCREAD | I:36/16 | DG 438-7 SET TO RC 422
DG44388_TOJUNK | Front_System | DG 438-8 SET TO JUNK | None | PLC_DISCREAD | I:36/17 | DG 438-8 SET TO JUNK
DG44388_TOSC4425 | Front_System | DG 438-8 SET TO SC 425 | None | PLC_DISCREAD | I:35/17 | DG 438-8 SET TO SC 425
DOLO_Meas | Front_System | DOLO SILO LEVEL MEASUREMENT (FT) | ft | 22 | 1 | 0 | 1 | PLC_INTWRITE | N102:166 | DOLO SILO LEVEL MEASUREMENT (FT)
DOLO_MEASTON | Front_System | DOLO SILO TON MEASUREMENT | ton | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:852 | DOLO SILO TON MEASUREMENT
FN44195MS_X | Front_System | FN 419-5 AUX CONTACT | Off | PLC_DISCREAD | I:17/12 | FN 419-5 STOPPED
FN4430_BYP | Front_System | FN 430 INTERLOCK BYPASS ON | On | PLC_DISCWRITE | B100/300 | FN 430 INTERLOCK BYPASS ON
FN4430_IM | Front_System | FN 430 INTERLOCKS MET | None | PLC_DISCREAD | B3/211 | FN 430 INTERLOCKS MET
FN4430_PBS | Front_System | FN 430 PC START | None | PLC_DISCWRITE | B100/189 | FN 430 PC START
FN4430_PBT | Front_System | FN 430 PC STOP | None | PLC_DISCWRITE | B100/205 | FN 430 PC STOP
FN4430FTS_ALM | Front_System | FN 430 FAILED TO START | On | PLC_ALARM | B101/366 | FN 430 FAILED TO START
FN4430MS_X | Front_System | FN 430 AUX CONTACT | Off | PLC_DISCREAD | I:17/11 | FN 430 STOPPED
FN4437B_BYP | Front_System | FN 437-1 INTERLOCK BYPASS ON | On | PLC_DISCWRITE | B100/342 | FN 437-1 INTERLOCK BYPASS ON
FN4437B_IM | Front_System | FN 437-B INTERLOCKS MET | None | PLC_DISCREAD | B3/212 | FN 437-B INTERLOCKS MET
FN4437B_PBS | Front_System | FN 437-B PC START | None | PLC_DISCWRITE | B100/190 | FN 437-B PC START
FN4437B_PBT | Front_System | FN 4437-B PC STOP | None | PLC_DISCWRITE | B100/206 | FN 4437-B PC STOP
FN4437BFTS_ALM | Front_System | FN 437-B FAILED TO START | On | PLC_ALARM | B101/369 | FN 437-B FAILED TO START
FN4437BMS_X | Front_System | FN 437-B AUX CONTACT | Off | PLC_DISCREAD | I:16/15 | FN 437-B STOPPED
FRONTAUTOSHTDWN_ALM | Front_System | FRONT SYSTEM AUTO SHUTDOWN IN 5 MIN | On | PLC_ALARM | B101:8/1 | FRONT SYSTEM AUTO SHUTDOWN IN 5 MIN
FRONTAUTOSHTDWN_PCRESET | Front_System | PC STOP FRONT SYSTEM AUTO SHUTDOWN | On | PLC_DISCWRITE | B100:3/13 | PC STOP FRONT SYSTEM AUTO SHUTDOWN
HM4422_AUTO | Front_System | HM 422 IN AUTO | None | PLC_DISCREAD | I:230/13 | HM 422 IN AUTO
HM4422_DISCONNECT | Front_System | HM 422 DISCONNECT | Off | PLC_DISCREAD | I:230/16 | HM 422 DISCONNECT
HM4422_IM | Front_System | HM 422 INTERLOCKS MET | None | PLC_DISCREAD | B3/482 | HM 422 INTERLOCKS MET
HM4422_IT | Front_System | HM 422 AMPS | AMPS | 250 | 0 | 0 | 0 | PLC_FLTREAD | F8:125 | HM 422 AMPS
HM4422_OVERLOADS | Front_System | HM 422 OVERLOADS OUT | Off | PLC_DISCREAD | I:230/15 | HM 422 OVERLOADS OUT
HM4422_PBS | Front_System | HM 422 PC START | None | PLC_DISCWRITE | B100/310 | HM 422 PC START
HM4422_PBT | Front_System | HM 422 PC STOP | None | PLC_DISCWRITE | B100/309 | HM 422 PC STOP
HM4422_STOP_Tmr | Front_System | HM 422 Hold after Stop Timer | Seconds | 300 | 0 | 0 | 0 | PLC_FLTREAD | N12:0
HM4422FTS_ALM | Front_System | HM 422 FAILED TO START | On | PLC_ALARM | B101/350 | HM 422 FAILED TO START
HM4422MS_X | Front_System | HM 422 AUX FDBK | Off | PLC_DISCREAD | I:230/14 | HM 422 STOPPED
NEL_LH1_DG4438MG_TOBE4242 | Front_System | Front System Manual Diverter Gate 4438 to 2A 3A | None | PLC_DISCREAD | I:035/3
NEL_LH1_DG4438MG_TOHM4422 | Front_System | Front System Manual Diverter Gate 4438 to 1A 2A 3A | None | PLC_DISCREAD | I:035/2
PC4420_BYP | Front_System | PC 420 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/237 | PC 420 MOTION SWITCH BYPASS ON
PC4420_IM | Front_System | PC 420 INTERLOCKS MET | None | PLC_DISCREAD | B3/209 | PC 420 INTERLOCKS MET
PC4420_PBS | Front_System | PC 420 PC START | None | PLC_DISCWRITE | B100/188 | PC 420 PC START
PC4420_PBT | Front_System | PC 420 PC STOP | None | PLC_DISCWRITE | B100/204 | PC 420 PC STOP
PC4420FTS_ALM | Front_System | PC 420 FAILED TO START | On | PLC_ALARM | B101/346 | PC 420 FAILED TO START
PC4420MS_X | Front_System | PC 420 AUX CONTACT | Off | PLC_DISCREAD | I:16/00 | PC 420 STOPPED
PC4420MSF_ALM | Front_System | PC 420 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/347 | PC 420 MOTION SWITCH FAILURE
PC4421_BYP | Front_System | PC 421 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/236 | PC 421 MOTION SWITCH BYPASS ON
PC4421_IM | Front_System | PC 421 INTERLOCKS MET | None | PLC_DISCREAD | B3/208 | PC 421 INTERLOCKS MET
PC4421_PBS | Front_System | PC 421 PC START | None | PLC_DISCWRITE | B100/187 | PC 421 PC START
PC4421_PBT | Front_System | PC 421 PC STOP | None | PLC_DISCWRITE | B100/203 | PC 421 PC STOP
PC4421FTS_ALM | Front_System | PC 421 FAILED TO START | On | PLC_ALARM | B101/348 | PC 421 FAILED TO START
PC4421MS_X | Front_System | PC 421 AUX CONTACT | Off | PLC_DISCREAD | I:16/12 | PC 421 STOPPED
PC4421MSF_ALM | Front_System | PC 421 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/349 | PC 421 MOTION SWITCH FAILURE
RA4437B1MS_X | Front_System | RA 437B-1 RUNNING | Off | PLC_DISCREAD | I:220/05 | RA 437B-1 STOPPED
SC425_SCBYP | Front_System | SC 425 BYPASSED - MATERIAL FED DIRECT TO SILO 1A | On | PLC_DISCWRITE | B100/558 | SC 425 BYPASSED - MATERIAL FED DIRECT TO SILO 1A
SC426_SCBYP | Front_System | SC 426 BYPASSED - MATERIAL FED DIRECT TO SILO 2A | On | PLC_DISCWRITE | B100/557 | SC 426 BYPASSED - MATERIAL FED DIRECT TO SILO 2A
SC4413_BYP | Front_System | SC 413 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/235 | SC 413 MOTION SWITCH BYPASS ON
SC4413_IM | Front_System | SC 413 INTERLOCKS MET | None | PLC_DISCREAD | B3/205 | SC 413 INTERLOCKS MET
SC4413_IT | Front_System | SC 413 AMPS | Amps | 35 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:86 | SC 413 AMPS
SC4413_PBS | Front_System | SC 413 PC START | None | PLC_DISCWRITE | B100/184 | SC 413 PC START
SC4413_PBT | Front_System | SC 413 PC STOP | None | PLC_DISCWRITE | B100/200 | SC 413 PC STOP
SC4413FTS_ALM | Front_System | SC 413 FAILED TO START | On | PLC_ALARM | B101/344 | SC 413 FAILED TO START
SC4413HIAMP_ALM | Front_System | SC 413 HIGH AMPS | On | PLC_ALARM | B101/484 | SC 413 HIGH AMPS
SC4413MS_X | Front_System | SC 413 AUX CONTACT | Off | PLC_DISCREAD | I:16/17 | SC 413 STOPPED
SC4413MSF_ALM | Front_System | SC 413 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/345 | SC 413 MOTION SWITCH FAILURE
SC4425_BYP | Front_System | SC 445 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/358 | SC 445 MOTION SWITCH BYPASS ON
SC4425_IM | Front_System | SC 425 INTERLOCKS MET | None | PLC_DISCREAD | B3/61 | SC 425 INTERLOCKS MET
SC4425_PBS | Front_System | SC 4425 PC START | None | PLC_DISCWRITE | B100/179 | SC 4425 PC START
SC4425FTS_ALM | Front_System | SC 425 FAILED TO START | On | PLC_ALARM | B101/358 | SC 425 FAILED TO START
SC4425MS_X | Front_System | SC 425 AUX CONTACT | Off | PLC_DISCREAD | I:17/17 | SC 425 STOPPED
SC4425MSF_ALM | Front_System | SC 425 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/359 | SC 425 MOTION SWITCH FAILURE
SC4426_BYP | Front_System | SC 426 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/234 | SC 426 MOTION SWITCH BYPASS ON
SC4426_IM | Front_System | SC 426 INTERLOCKS MET | None | PLC_DISCREAD | B3/60 | SC 426 INTERLOCKS MET
SC4426_PBS | Front_System | SC 4426 PC START | None | PLC_DISCWRITE | B100/178 | SC 4426 PC START
SC4426_PBT | Front_System | SC 4426 PC STOP | None | PLC_DISCWRITE | B100/194 | SC 4426 PC STOP
SC4426FTS_ALM | Front_System | SC 426 FAILED TO START | On | PLC_ALARM | B101/360 | SC 426 FAILED TO START
SC4426MS_X | Front_System | SC 426 AUX CONTACT | Off | PLC_DISCREAD | I:15/17 | SC 426 STOPPED
SC4426MSF_ALM | Front_System | SC 426 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/361 | SC 426 MOTION SWITCH FAILURE
SC4427_AUTO | Front_System | SC 427 IN AUTO | None | PLC_DISCREAD | I:231/05 | SC 427 IN AUTO
SC4427_BYP | Front_System | SC 427 MOTION SWITCH BYPASS ON | On | PLC_DISCWRITE | B100/233 | SC 427 MOTION SWITCH BYPASS ON
SC4427_DISCONNECT | Front_System | SC 427 DISCONNECT | None | PLC_DISCREAD | I:231/07 | SC 427 DISCONNECT
SC4427_IM | Front_System | SC 427-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/27 | SC 427-1 INTERLOCKS MET
SC4427_OVERLOADS | Front_System | SC 427 OVERLOADS | None | PLC_DISCREAD | I:231/06 | SC 427 OVERLOADS
SC4427_PBT | Front_System | SC 427 PC STOP | None | PLC_DISCWRITE | B100/192 | SC 427 PC STOP
SC4427FTS_ALM | Front_System | SC 427 FAILED TO START | On | PLC_ALARM | B101/362 | SC 427 FAILED TO START
SC4427MS_X | Front_System | SC 427 AUX FDBK | Off | PLC_DISCREAD | I:232/01 | SC 427 STOPPED
SC4427MSF_ALM | Front_System | SC 427 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/363 | SC 427 MOTION SWITCH FAILURE
SC4428_AUTO | Front_System | SC 428 IN AUTO | None | PLC_DISCREAD | I:230/06 | SC 428 IN AUTO
SC4428_BYP | Front_System | SC 428 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/308 | SC 428 MOTION SWITCH BYPASSED
SC4428_DISCONNECT | Front_System | SC 428 DISCONNECT | Off | PLC_DISCREAD | I:230/11 | SC 428 DISCONNECT
SC4428_IM | Front_System | SC 428 INTERLOCKS MET | None | PLC_DISCREAD | B3/481 | SC 428 INTERLOCKS MET
SC4428_IT | Front_System | SC 428 AMPS | AMPS | 65 | 0.5 | 0 | 0 | PLC_FLTREAD | F8:124 | SC 428 AMPS
SC4428_OVERLOADS | Front_System | SC 428 OVERLOADS | Off | PLC_DISCREAD | I:230/10 | SC 428 OVERLOADS
SC4428_PBS | Front_System | SC 428 PC START | None | PLC_DISCWRITE | B100/307 | SC 428 PC START
SC4428_PBT | Front_System | SC 428 PC STOP | None | PLC_DISCWRITE | B100/306 | SC 428 PC STOP
SC4428FTS_ALM | Front_System | SC 428 FAILED TO START | On | PLC_ALARM | B101/364 | SC 428 FAILED TO START
SC4428MS_X | Front_System | SC 428 AUX FDBK | Off | PLC_DISCREAD | I:230/07 | SC 428 STOPPED
SC4428MSF_ALM | Front_System | SC 428 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/365 | SC 428 MOTION SWITCH FAILURE
SC4430A_AUTO | Front_System | SC 430-A IN AUTO | None | PLC_DISCREAD | I:231/00 | SC 430-A IN AUTO
SC4430A_DISCONNECT | Front_System | SC 430-A DISCONNECT | None | PLC_DISCREAD | I:231/04 | SC 430-A DISCONNECT
SC4430A_IM | Front_System | SC 430-A INTERLOCKS MET | None | PLC_DISCREAD | B3/483 | SC 430-A INTERLOCKS MET
SC4430A_OVERLOADS | Front_System | SC 430-A OVERLOADS | None | PLC_DISCREAD | I:231/03 | SC 430-A OVERLOADS
SC4430A_PBS | Front_System | SC 430-A PC START | None | PLC_DISCWRITE | B100/313 | SC 430-A PC START
SC4430A_PBT | Front_System | SC 430-A PC STOP | None | PLC_DISCWRITE | B100/312 | SC 430-A PC STOP
SC4430AFTS_ALM | Front_System | SC 430-A FAILED TO START | On | PLC_ALARM | B101/367 | SC 430-A FAILED TO START
SC4430AMS_X | Front_System | SC 430-A AUX FDBK | Off | PLC_DISCREAD | I:231/02 | SC 430-A STOPPED
SILO1A_AVGMEAS | Front_System | SILO 1A AVERAGE LEVEL MEASUREMENT #1(FT) | ft | 70 | 1 | 0 | 1 | PLC_FLTREAD | F9:260 | SILO 1A AVERAGE LEVEL MEASUREMENT #1(FT)
SILO1A_MEAS1 | Front_System | SILO 1A LEVEL MEASUREMENT #1(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:75 | SILO 1A LEVEL MEASUREMENT #1(FT)
SILO1A_MEAS2 | Front_System | SILO 1A LEVEL MEASUREMENT #2(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:76 | SILO 1A LEVEL MEASUREMENT #2(FT)
SILO1A_MEAS3 | Front_System | SILO 1A LEVEL MEASUREMENT #3(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:77 | SILO 1A LEVEL MEASUREMENT #3(FT)
SILO1A_MEAS4 | Front_System | SILO 1A LEVEL MEASUREMENT #4(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:78 | SILO 1A LEVEL MEASUREMENT #4(FT)
SILO1A_MEASTON | Front_System | SILO 1A TON MEASUREMENT | ton | 3300 | 1 | 0 | 0 | PLC_FLTREAD | F9:271 | SILO 1A TON MEASUREMENT
SILO1AHIGH_ALM | Front_System | SILO 1A HIGH LEVEL | On | PLC_ALARM | I:14/04 | SILO 1A HIGH LEVEL
SILO2A_AVGMEAS | Front_System | SILO 2A AVERAGE LEVEL MEASUREMENT #1(FT) | ft | 70 | 1 | 0 | 1 | PLC_FLTREAD | F9:261 | SILO 2A AVERAGE LEVEL MEASUREMENT #1(FT)
SILO2A_MEAS1 | Front_System | SILO 2A LEVEL MEASUREMENT #1(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:79 | SILO 2A LEVEL MEASUREMENT #1(FT)
SILO2A_MEAS2 | Front_System | SILO 2A LEVEL MEASUREMENT #2(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:80 | SILO 2A LEVEL MEASUREMENT #2(FT)
SILO2A_MEAS3 | Front_System | SILO 2A LEVEL MEASUREMENT #3(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:81 | SILO 2A LEVEL MEASUREMENT #3(FT)
SILO2A_MEAS4 | Front_System | SILO 2A LEVEL MEASUREMENT #4(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:82 | SILO 2A LEVEL MEASUREMENT #4(FT)
SILO2A_MEASTON | Front_System | SILO 2A TON MEASUREMENT | ton | 3300 | 1 | 0 | 0 | PLC_FLTREAD | F9:272 | SILO 2A TON MEASUREMENT
SILO2AHIGH_ALM | Front_System | SILO 2A HIGH LEVEL | On | PLC_ALARM | I:14/05 | SILO 2A HIGH LEVEL
SILO3A_AVGMEAS | Front_System | SILO 3A AVERAGE LEVEL MEASUREMENT #1(FT) | ft | 70 | 1 | 0 | 1 | PLC_FLTREAD | F9:262 | SILO 3A AVERAGE LEVEL MEASUREMENT #1(FT)
SILO3A_MEAS1 | Front_System | SILO 3A LEVEL MEASUREMENT #1(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:83 | SILO 3A LEVEL MEASUREMENT #1(FT)
SILO3A_MEAS2 | Front_System | SILO 3A LEVEL MEASUREMENT #2(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:84 | SILO 3A LEVEL MEASUREMENT #2(FT)
SILO3A_MEAS3 | Front_System | SILO 3A LEVEL MEASUREMENT #3(FT) | ft | 70 | 1 | 0 | 1 | PLC_INTWRITE | N102:85 | SILO 3A LEVEL MEASUREMENT #3(FT)
SILO3A_MEASTON | Front_System | SILO 3A TON MEASUREMENT | ton | 3300 | 1 | 0 | 0 | PLC_FLTREAD | F9:273 | SILO 3A TON MEASUREMENT
SILO3A_SOUNDLVL | Front_System | SILO 3A LEVEL IN FEET | FT | 100 | 0.02 | 0 | 0 | PLC_FLTREAD | F8:122 | SILO 3A LEVEL IN FEET
SILO3A_SOUNDTONS | Front_System | SILO 3A PRODUCT TONS FROM SOUND LEVEL | FT | 3300 | 3 | 0 | 0 | PLC_FLTREAD | F8:119 | SILO 3A PRODUCT TONS FROM SOUND LEVEL
SILO3AHIGH_ALM | Front_System | SILO 3A HIGH LEVEL | On | PLC_ALARM | I:14/06 | SILO 3A HIGH LEVEL
VS4432_IM | Front_System | VS 432 INTERLOCKS MET | None | PLC_DISCREAD | B3/207 | VS 432 INTERLOCKS MET
VS4432_IT | Front_System | VS 432 AMPS | A | 50 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:184 | VS 432 AMPS
VS4432_PBS | Front_System | VS 432 PC START | None | PLC_DISCWRITE | B100/186 | VS 432 PC START
VS4432_PBT | Front_System | VS 432 PC STOP | None | PLC_DISCWRITE | B100/202 | VS 432 PC STOP
VS4432_STARTALM | Front_System | VS 432 START-UP ALARM | None | PLC_ALARM | O:15/13 | VS 432 START-UP ALARM
VS4432FTS_ALM | Front_System | VS 432 FAILED TO START | On | PLC_ALARM | B101/368 | VS 432 FAILED TO START
VS4432MS_X | Front_System | VS 432 AUX CONTACT | Off | PLC_DISCREAD | I:16/16 | VS 432 STOPPED!
VS8328FTS_ALM | Front_System | VS 328 FAILED TO START! | On | PLC_ALARM | B101/178 | VS 328 FAILED TO START!
Acknowledge | General_Plant | ACKNOWLEDGE ALARMS BUTTON | None | PLC_DISCWRITE | B100/277 | ACKNOWLEDGE ALARMS BUTTON
BP1 | General_Plant | Urea Batching Plant | 0
DC4762-1_PBS | General_Plant | FN 762-1 & RA 762-1 PC START | None | PLC_DISCWRITE | B100/208 | FN 762-1 & RA 762-1 PC START
DC4762-1_PBT | General_Plant | FN 762-1 & RA 762-1 PC STOP | None | PLC_DISCWRITE | B100/224 | FN 762-1 & RA 762-1 PC STOP
FIRE_CAPRM_ALM | General_Plant | FIRE IN CAPACITOR ROOM! | On | PLC_ALARM | I:056/16 | FIRE ALARM ! MCR5A
FIRE_K2DRV_ALM | General_Plant | FIRE IN KILN 2 DRIVE ROOM! | On | PLC_ALARM | I:056/07 | FIRE IN KILN 2 DRIVE ROOM!
FIRE_MCR1_ALM | General_Plant | FIRE IN MCR #1 | On | PLC_ALARM | I:104/14 | FIRE IN MCR #1
FIRE_MCR2_ALM | General_Plant | FIRE IN MCR #2 | On | PLC_ALARM | I:027/14 | FIRE IN MCR #2
FIRE_MCR3_ALM | General_Plant | FIRE IN MCR #3 | On | PLC_ALARM | I:024/16 | FIRE IN MCR #3
FIRE_MCR4_ALM | General_Plant | FIRE IN MCR #4 | On | PLC_ALARM | I:035/04 | FIRE IN MCR #4
FIRE_MCR5_ALM | General_Plant | FIRE IN MCR #5 | On | PLC_ALARM | I:056/15 | FIRE IN MCR #5
FIRE_MCR6_ALM | General_Plant | FIRE IN MCR #6 | On | PLC_ALARM | I:035/6 | FIRE Alarm ! MCR #6
FIRE_MCR7_ALM | General_Plant | FIRE IN MCR #7 | On | USCNEL051 | NEL_HD1_MCR07_FIREALM.ALM | FIRE IN MCR #7
FIRE_MCR8_ALM | General_Plant | FIRE IN MCR #8 | On | KILN1_BH_ALARM | MCR_8_FIRE | FIRE IN MCR #8
FN47621_BYP | General_Plant | FN 762-1 INTERLOCK BYPASS ON | On | PLC_DISCWRITE | B100/302 | FN 762-1 INTERLOCK BYPASS ON
FN47621_IM | General_Plant | FN 762-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/210 | FN 762-1 INTERLOCKS MET
FN47621FTS_ALM | General_Plant | FN 4762-1 FAILED TO START | On | PLC_ALARM | B101/371 | FN 4762-1 FAILED TO START
FN47621MS_X | General_Plant | FN 4762-1 AUX CONTACT | Off | PLC_DISCREAD | I:17/13 | FN 762-1 STOPPED
FN6112_IM | General_Plant | FN 611-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/1221 | FN 611-2 INTERLOCKS MET
FN6112_PBS | General_Plant | FN 611-2 PC START | None | PLC_DISCWRITE | B100/614 | FN 611-2 PC START
FN6112_PBT | General_Plant | FN6112-2 PC STOP | None | PLC_DISCWRITE | B100/613 | FN6112-2 PC STOP
FN6112_SSA_HMI | General_Plant | FN 611-2 Diesel blower #2 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1335 | FN 611-2 Diesel blower #2 0=Auto 1=Manual
FN6112FTS_ALM | General_Plant | FN 611-2 FAILED TO START | On | PLC_ALARM | B101/576 | FN 611-2 FAILED TO START
FN6112MS_X | General_Plant | FN 611-2 AUX FDBK | Off | PLC_DISCREAD | I:15/16 | FN 611-2 STOPPED
GEN1_BKR | General_Plant | Generator #1 Breaker Closed | None | PLC_DISCREAD | I:170/01 | Generator #1 Breaker Closed
GEN1_RDY | General_Plant | Generator #! Ready | None | PLC_DISCREAD | I:170/13 | Generator #! Ready
GEN1_RPWR | General_Plant | Generator #1 Reverse Power | On | PLC_ALARM | I:170/14 | Generator #1 Reverse Power
GEN12_DEMAND | General_Plant | PLANT UTILITY DEMAND | kW | 7000 | 10 | 0 | 0 | PLC_FLTREAD | F9:133 | PLANT UTILITY DEMAND
GEN12_MAIN_BKR | General_Plant | PLANT MAIN BREAKER OPEN | Off | PLC_ALARM | I:171/16 | PLANT MAIN BREAKER OPEN
GEN12_PBS | General_Plant | Generators Start PB | None | PLC_DISCWRITE | B100/470 | Generators Start PB
GEN12_PBT | General_Plant | Generators Stop PB | None | PLC_DISCWRITE | B100/462 | Generators Stop PB
GEN12LT | General_Plant | Generator Diesel Fuel Tank Level | % | 100 | 2 | 0 | 0 | PLC_FLTREAD | F9:132 | Generator Diesel Fuel Tank Level
GEN1ET_H_L | General_Plant | Generator #1 HI/LO Bat. Voltage | On | PLC_ALARM | B101/538 | Generator #1 HI/LO Bat. Voltage
GEN1IDT | General_Plant | Generator #1 Diff. Current | On | PLC_ALARM | B101/537 | Generator #1 Diff. Current
GEN1IT_H | General_Plant | Generator #1 Overcurrent | On | PLC_ALARM | B101/544 | Generator #1 Overcurrent
GEN1LT_L | General_Plant | Generator #1 LO Water Level | On | PLC_ALARM | B101/541 | Generator #1 LO Water Level
GEN1MS_X | General_Plant | Generator #1 Run Indication | Off | PLC_DISCREAD | I:170/15 | GENERATOR #1 STOPPED
GEN1PT_L | General_Plant | Generator #1 LO Oil Pressure | On | PLC_ALARM | B101/540 | Generator #1 LO Oil Pressure
GEN1QT_H | General_Plant | Generator #1 Overcrank | On | PLC_ALARM | B101/543 | Generator #1 Overcrank
GEN1RUN_HRS | General_Plant | Generator #1 Run Hours | % | 100 | 2 | 0 | 0 | PLC_INTREAD | N48:30 | Generator Diesel Fuel Tank Level
GEN1ST_H | General_Plant | Generator #1 Overspeed | On | PLC_ALARM | B101/545 | Generator #1 Overspeed
GEN1TT_H | General_Plant | Generator #1 HI Water Temp. | On | PLC_ALARM | B101/539 | Generator #1 HI Water Temp.
GEN1TT_L | General_Plant | Generator #1 LO Water Temp | On | PLC_ALARM | B101/542 | Generator #1 LO Water Temp
GEN2_BKR | General_Plant | Generator #2 Breaker Closed | None | PLC_DISCREAD | I:171/01 | Generator #2 Breaker Closed
GEN2_RDY | General_Plant | Generator #! Ready | None | PLC_DISCREAD | I:171/13 | Generator #! Ready
GEN2_RPWR | General_Plant | Generator #2 Reverse Power | On | PLC_ALARM | I:171/14 | Generator #2 Reverse Power
GEN2ET_H_L | General_Plant | Generator #2 HI/LO Bat. Voltage | On | PLC_ALARM | B101/547 | Generator #2 HI/LO Bat. Voltage
GEN2IDT | General_Plant | Generator #2 Diff. Current | On | PLC_ALARM | B101/546 | Generator #2 Diff. Current
GEN2IT_H | General_Plant | Generator #2 Overcurrent | On | PLC_ALARM | B101/553 | Generator #2 Overcurrent
GEN2LT_L | General_Plant | Generator #2 LO Water Level | On | PLC_ALARM | B101/550 | Generator #2 LO Water Level
GEN2MS_X | General_Plant | Generator #2 Run Indication | Off | PLC_DISCREAD | I:171/15 | GENERATOR #2 STOPPED
GEN2PT_L | General_Plant | Generator #2 LO Oil Pressure | On | PLC_ALARM | B101/549 | Generator #2 LO Oil Pressure
GEN2QT_H | General_Plant | Generator #2 Overcrank | On | PLC_ALARM | B101/552 | Generator #2 Overcrank
GEN2RUN_HRS | General_Plant | Generator #2 Run Hours | % | 100 | 2 | 0 | 0 | PLC_INTREAD | N48:31 | Generator Diesel Fuel Tank Level
GEN2ST_H | General_Plant | Generator #2 Overspeed | On | PLC_ALARM | B101/554 | Generator #2 Overspeed
GEN2TT_H | General_Plant | Generator #2 HI Water Temp. | On | PLC_ALARM | B101/548 | Generator #2 HI Water Temp.
GEN2TT_L | General_Plant | Generator #2 LO Water Temp | On | PLC_ALARM | B101/551 | Generator #2 LO Water Temp
KILN_LIME_FACTOR | General_Plant | Kiln lime factor multiple | TONS/HR | 1 | 0 | 0 | 0 | PLC_FLTREAD | F8:169
KILN_START_HORN | General_Plant | Kiln #1 & #2 Drive Start-up Horn Sounding | None | PLC_DISCREAD | O:47/17
LIMEHORN_ALM | General_Plant | FRONT & BACK SYSTEM START-UP HORN | None | PLC_ALARM | O:16/17 | FRONT & BACK SYSTEM START-UP HORN
LOWAIRPRESSURE_ALM | General_Plant | LOW PLANT AIR PRESSURE! | On | PLC_ALARM | I:14/15 | LOW PLANT AIR PRESSURE!
LUBE_KILN_TIRES | General_Plant | Lube Kiln Tires | On | PLC_ALARM | B101/597 | LUBE KILN TIRES THEN RESET TIMER
LUBE_KILN_TIRES_RESET | General_Plant | Lube Kiln Tires Reset | None | PLC_ALARM | B100:43/1
MCR1N_MCC | General_Plant | MCR 1 N MCC HIGHLIGHT BUCKET # | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR1S_MCC | General_Plant | MCR 1 S MCC HIGHLIGHT BUCKET # | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR2_FN314 | General_Plant | MCR4 SHOW FN314 | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR2_FN331 | General_Plant | MCR4 SHOW FN331 | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR2_MCC3 | General_Plant | MCR2 MCC3 HIGHLIGHT UNIT | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR2_MCC4 | General_Plant | MCR2 MCC4 HIGHLIGHT UNIT | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR4_BM602 | General_Plant | MCR4 SHOW BM602 | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR4_FN312 | General_Plant | MCR4 SHOW FN312 | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR4_MCC10 | General_Plant | MCR 4 MCC10 HIGHLIGHT UNIT | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR4_MCC8 | General_Plant | MCR 4 MCC 8 HIGHLIGHT UNIT | # | 500 | 0 | 0 |  | 0 | 0 | 0
MCR4_MCC9 | General_Plant | MCR 4 MCC9 HIGHLIGHT UNIT | # | 500 | 0 | 0 |  | 0 | 0 | 0
NEL_SNCR_FT6001A_IND | General_Plant | SNCR KILN 1 ATOMIZING AIR SCFM | SCFM | 100 | 0 | 0 | 0 | PLC_FLTREAD | F28:10 | SNCR K1 ATOMIZING AIR
NEL_SNCR_FT6001B_IND | General_Plant | SNCR KILN 2 ATOMIZING AIR SCFM | SCFM | 100 | 0 | 0 | 0 | PLC_FLTREAD | F84:23 | SNCR K2 ATOMIZING AIR
NEL_SNCR_HT6001_AUX | General_Plant | SNCR HT6001 LEVEL 1 PAD HEATER AUX | Off | PLC_DISCREAD | N103:9/15 | SNCR HT6001 LVL 1 HTR STOPPED
NEL_SNCR_HT6002_AUX | General_Plant | SNCR HT6002 LEVEL 2 HEATER PAD AUX | Off | PLC_DISCREAD | N103:10/0 | SNCR HT6002 LVL 2 HTR STOPPED
NEL_SNCR_TK1900_LT | General_Plant | SNCR TANK LEVEL | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F84:28 | SNCR TANK LEVEL
NEL_SNCR_TK1900_TT1 | General_Plant | SNCR TANK TEMPERATURE | F | 200 | 0 | 0 | 0 | PLC_FLTREAD | F84:29 | SNCR TANK TEMP
NEL_SNCR_TK1900_VT | General_Plant | SNCR TANK VOLUME (GAL) | GAL | 40000 | 0 | 0 | 0 | PLC_FLTREAD | F84:30 | SNCR TANK VOLUME
O2PROBEFANSTOP_ALM | General_Plant | O2 PROBE COOLING FAN STOPPED | None | PLC_ALARM | I:27/12 | O2 PROBE COOLING FAN STOPPED
PASSWORD | General_Plant | PASSWORD
PLANT_UTIL_PULSE | General_Plant | Plant Utility Pulse!!!!!!!! | None | PLC_DISCREAD | I:170/16 | Plant Utility Pulse!!!!!!!!
PLANTDEMAND_DAY | General_Plant | PLANT TOTAL UTILITY DEMAND - YESTERDAY | kWh | 200000 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:410 | PLANT TOTAL UTILITY DEMAND - YESTERDAY
PM46101_IM | General_Plant | PM 4610-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/377 | PM 4601-1 INTERLOCKS MET
PM46101_PBS | General_Plant | PM 4-610-1 PC START | None | PLC_DISCWRITE | B100/338 | PM 4-610-1 PC START
PM46101_PBT | General_Plant | PM 4610-1 PC STOP | None | PLC_DISCWRITE | B100/339 | PM 4610-1 PC STOP
PM46101_SSA_HMI | General_Plant | PM 4610-1 diesel fuel pump 0=Auto 1=Man | None | PLC_DISCWRITE | B3/1325 | PM 4610-1 diesel fuel pump 0=Auto 1=Man
PM46101FTS_ALM | General_Plant | PM 4610-1 FAILED TO START | On | PLC_ALARM | B101/195 | PM 610-1 FAILED TO START
PM46101MS_X | General_Plant | PM 4-610-1 AUX FDBK | Off | PLC_DISCREAD | I:15/00 | PM 610-1 STOPPED
PM46102_IM | General_Plant | PM 4610-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/379 | PM 4610-2 INTERLOCKS MET
PM46102_PBS | General_Plant | PM 46102 PC START | None | PLC_DISCWRITE | B100/336 | PM 46102 PC START
PM46102_PBT | General_Plant | PM 4610-2 PC STOP | None | PLC_DISCWRITE | B100/337 | PM 4610-2 PC STOP
PM46102_SSA_HMI | General_Plant | PM 4610-2 diesel fuel pump 0=Auto 1=Man | None | PLC_DISCWRITE | B3/1330 | PM 4610-2 diesel fuel pump 0=Auto 1=Man
PM46102FTS_ALM | General_Plant | PM 610-2 FAILED TO START | On | PLC_ALARM | B101/196 | PM 610-2 FAILED TO START
PM46102MS_X | General_Plant | PM 4610-2 AUX FDBK | Off | PLC_DISCREAD | I:15/01 | PM 610-2 STOPPED
RA47621_IM | General_Plant | RA 762-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/214 | RA 762-1 INTERLOCKS MET
RA47621FTS_ALM | General_Plant | RA 762-1 FAILED TO START | On | PLC_ALARM | B101/372 | RA 762-1 FAILED TO START
RA47621MS_X | General_Plant | RA 762-1 AUX CONTACT | Off | PLC_DISCREAD | I:220/12 | RA 762-1 STOPPED
RACK1_ALM | General_Plant | RACK 1 IN MCR 4 FAULTED!! | On | PLC_ALARM | S:7/001 | RACK 1 IN MCR 4 FAULTED!!
RACK10_ALM | General_Plant | RACK 10 IN MCR 1 FAULTED!! | On | PLC_ALARM | S:32/0 | RACK 10 IN MCR 1 FAULTED!!
RACK11_ALM | General_Plant | RACK 11 IN MCR 1 FAULTED!! | On | PLC_ALARM | S:32/001 | RACK 11 IN MCR 1 FAULTED!!
RACK12_ALM | General_Plant | RACK 12 ON THE BACK SYSTEM FAULTED!! | On | PLC_ALARM | S:32/2 | RACK 12 ON THE BACK SYSTEM FAULTED!!
RACK13_ALM | General_Plant | RACK 13 ON THE BACK SYSTEM FAULTED!! | On | PLC_ALARM | S:32/003 | RACK 13 ON THE BACK SYSTEM FAULTED!!
RACK17_ALM | General_Plant | RACK 17 IN THE GENERATORS FAULTED!! | On | PLC_ALARM | S:32/007 | RACK 17 IN THE GENERATORS FAULTED!!
RACK2_ALM | General_Plant | RACK 2 IN MCR 2 FAULTED!! | On | PLC_ALARM | S:7/2 | RACK 2 IN MCR 2 FAULTED!!
RACK20_ALM | General_Plant | RACK 20 IN THE CAPACITOR ROOM FAULTED!! | On | PLC_ALARM | S:34/0 | RACK 20 IN THE CAPACITOR ROOM FAULTED!!
RACK21_ALM | General_Plant | RACK 21 IN THE CAPACITOR ROOM FAULTED!! | On | PLC_ALARM | S:34/001 | RACK 21 IN THE CAPACITOR ROOM FAULTED!!
RACK22_ALM | General_Plant | RACK 22 IN MCR 4 FAULTED!! | On | PLC_ALARM | S:34/2 | RACK 22 IN MCR 4 FAULTED!!
RACK23_ALM | General_Plant | RACK 23 IN MCR 4 FAULTED!! | On | PLC_ALARM | S:34/3 | RACK 23 IN MCR 4 FAULTED!!
RACK3_ALM | General_Plant | RACK 3 IN THE SAMPLE ROOM FAULTED!! | On | PLC_ALARM | S:7/003 | RACK 3 IN THE SAMPLE ROOM FAULTED!!
RACK4_ALM | General_Plant | RACK 4 ON PREHEATER 2 FAULTED!! | On | PLC_ALARM | S:7/4 | RACK 4 ON PREHEATER 2 FAULTED!!
RACK5_ALM | General_Plant | RACK 5 IN MCR 5 FAULTED!! | On | PLC_ALARM | S:7/005 | RACK 5 IN MCR 5 FAULTED!!
RACK6_ALM | General_Plant | Rack 6 In Kiln Drive Room Faulted | On | PLC_ALARM | S:7/06 | Rack 6 In Kiln Drive Room Faulted!
RACK7_ALM | General_Plant | RACK 7 IN MCR 2 FAULTED!! | On | PLC_ALARM | S:7/7 | RACK 7 IN MCR 2 FAULTED!!
TOT_DAY_PLANTLIME | General_Plant | PLANT TOT TON LIME YESTERDAY | TON | 2100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:239 | PLANT TOT TON LIME YESTERDAY
UTIL_MAIN_BKR | General_Plant | Utility Main Breaker Closed | None | PLC_DISCREAD | I:171/17 | Utility Main Breaker Closed
UTILITY_AVAIL | General_Plant | Utility Available | None | PLC_DISCREAD | I:170/00 | Utility Available
WP3083_AUTO | General_Plant | WP 308-3 H/O/A in Auto | None | PLC_DISCREAD | I:26/01
WP3083_CP | General_Plant | WP 308-3 Control Power On | None | PLC_DISCREAD | I:026/00
WP3083_IM | General_Plant | WP 308-3 Interlocks Met | None | PLC_DISCREAD | B3/1211
WP3083_LAST | General_Plant | Last O2 Probe Cooling Pump On 1=WP 308-3 0=WP369 | None | PLC_DISCREAD | B3/1213
WP3083_PBS | General_Plant | WP 308-3 PC Start | None | PLC_DISCWRITE | B100/536
WP3083_PBT | General_Plant | WP 308-3 PC Stop | None | PLC_DISCWRITE | B100/535
WP3083FTS_ALM | General_Plant | WP 308-3 FAILED TO START! | On | PLC_ALARM | B101/265 | WP 308-3 FAILED TO START!
WP3083MS_X | General_Plant | WP 308-3 Aux Fdbk | Off | PLC_DISCREAD | I:026/02 | WP 308-3 Stopped!
WP4369_IM | General_Plant | WP 4369 INTERLOCK MET | None | PLC_DISCREAD | B3/446 | WP 4369 INTERLOCK MET
WP4369_PBS | General_Plant | WP 4369 PC START | None | PLC_DISCWRITE | B100/460 | WP 4369 PC START
WP4369_PBT | General_Plant | WP 4369 PC STOP | None | PLC_DISCWRITE | B100/459 | WP 4369 PC STOP
WP4369FTS_ALM | General_Plant | WP 369 FAILED TO START! | On | PLC_ALARM | B101/165 | WP 369 FAILED TO START!
WP4369MS_X | General_Plant | WP 4369 AUX FDBK | Off | PLC_DISCREAD | I:027/11 | WP 369 STOPPED
:TagID | Group | Comment
AS715_HZ | Hydrator | AS 715 Hertz | Hz | 120 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_AS0715_ST2.SPT
AS715_IM | Hydrator | AS 715 INTERLOCKS MET | None | USCNEL051 | AS715_IM | AS 715 INTERLOCKS MET
AS715_IT | Hydrator | AS 715 AMPS | A | 75 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_AS0715_IT.IND | AS 715 AMPS
AS715_PBS | Hydrator | AS 715 PC START | None | USCNEL051 | NEL_HD1_AS0715.PBE_HMI | AS 715 PC START
AS715_PBT | Hydrator | AS 715 PC STOP | None | USCNEL051 | NEL_HD1_AS0715.PBS_HMI | AS 715 PC STOP
AS715_VFDSP | Hydrator | AS 715 VFD SPEED SP | % | 120 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_AS0715_ST.SPT
AS715FTS_ALM | Hydrator | AS 715 FAILED TO START!! | On | USCNEL051 | NEL_HD1_AS0715.FTS_ALM | AS 715 FAILED TO START!!
AS715HIIT_SP | Hydrator | AS 715 HI AMP ALARM SETPOINT | A | 50 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_AS0715_IT.AH_SPT
AS715IT_ALM | Hydrator | AS 715 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_AS0715_IT.AH | AS 715 HIGH AMPS!!
AS715VFD_AUTO | Hydrator | AS 715 VFD IN AUTO | None | USCNEL051 | NEL_HD1_AS0715_VFD_SSA_LCS
AS715VFD_STOP | Hydrator | AS 715 VFD STOPPING | None | USCNEL051 | AS715VFD_STOP
AS715VFDFAULT_ALM | Hydrator | AS 715 VFD FAULTED!! | On | USCNEL051 | NEL_HD1_AS0715_VFD_FLT | AS 715 VFD FAULTED!!
AS715VFDMS_X | Hydrator | AS 715 VFD FDBK | Off | USCNEL051 | NEL_HD1_AS0715.AUX | AS 715 VFD STOPPED!!
BE713_AUTO | Hydrator | BE 713 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_BE0713.SSA_LCS | BE 713 IN AUTO POSITION
BE713_BYP | Hydrator | BE 713 MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_BE0713.SS_BYP_PB | BE 713 MOTION SWITCH BYPASS
BE713_IM | Hydrator | BE 713 INTERLOCKS MET | None | USCNEL051 | BE713_IM | BE 713 INTERLOCKS MET
BE713_IT | Hydrator | BE 713 AMPS | A | 30 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_IT.IND | BE 713 AMPS
BE713_JOGIN | Hydrator | BE 713 JOG PLUG INSERTED | On | USCNEL051 | NEL_HD1_BE0713_JOG_PLUG | BE 713 JOG PLUG INSERTED
BE713_PBS | Hydrator | BE 713 PC START | None | USCNEL051 | NEL_HD1_BE0713.PBE_HMI | BE 713 PC START
BE713_PBT | Hydrator | BE 713 PC STOP | None | USCNEL051 | NEL_HD1_BE0713.PBS_HMI | BE 713 PC STOP
BE713FTS_ALM | Hydrator | BE 713 FAILED TO START!! | On | USCNEL051 | NEL_HD1_BE0713.FTS_ALM | BE 713 FAILED TO START!!
BE713HIIT_SP | Hydrator | BE 713 HI AMP ALARM SETPOINT | A | 20 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_IT.AH_SPT
BE713IT_ALM | Hydrator | BE 713 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_BE0713_IT.AH | BE 713 HIGH AMPS!!
BE713MS_X | Hydrator | BE 713 AUX FDBK | Off | USCNEL051 | NEL_HD1_BE0713.AUX | BE 713 STOPPED!!
BE713MSF_ALM | Hydrator | BE 713 MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_BE0713.SS_ALM | BE 713 MOTION SWITCH FAILURE!!
BE719_AUTO | Hydrator | BE 719 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_BE0719.SSA_LCS | BE 719 IN AUTO POSITION
BE719_BYP | Hydrator | BE 719 MOTION SWITCH BYPASSED!! | On | USCNEL051 | NEL_HD1_BE0719.SS_BYP_PB | BE 719 MOTION SWITCH BYPASSED!!
BE719_IM | Hydrator | BE 719 INTERLOCKS MET | None | USCNEL051 | BE719_IM | BE 719 INTERLOCKS MET
BE719_IT | Hydrator | BE 719 AMPS | A | 30 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_BE0719_IT.IND | BE 719 AMPS
BE719_JOGIN | Hydrator | BE 713 JOG PLUG INSERTED | On | USCNEL051 | NEL_HD1_BE0719_JOG_PLUG | BE 713 JOG PLUG INSERTED
BE719_PBS | Hydrator | BE 719 PC START | None | USCNEL051 | NEL_HD1_BE0719.PBE_HMI | BE 719 PC START
BE719_PBT | Hydrator | BE 719 PC STOP | None | USCNEL051 | NEL_HD1_BE0719.PBS_HMI | BE 719 PC STOP
BE719FTS_ALM | Hydrator | BE 719 FAILED TO START!! | On | USCNEL051 | NEL_HD1_BE0719.FTS_ALM | BE 719 FAILED TO START!!
BE719HIIT_SP | Hydrator | BE 719 HI AMP ALARM SETPOINT | A | 20 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_BE0719_IT.AH_SPT
BE719IT_ALM | Hydrator | BE 719 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_BE0719_IT.AH | BE 719 HIGH AMPS!!
BE719MS_X | Hydrator | BE 719 AUX FDBK | Off | USCNEL051 | NEL_HD1_BE0719.AUX | BE 719 STOPPED!!
BE719MSF_ALM | Hydrator | BE 719 MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_BE0719.SS_ALM | BE 719 MOTION SWITCH FAILURE!!
BN703HL_ALM | Hydrator | BN 703 HIGH LEVEL! | None | USCNEL051 | NEL_HD1_BN0703_LSH.ALM | BN 703 HIGH LEVEL!
BN703LL_ALM | Hydrator | BN 703 LOW LEVEL! | None | USCNEL051 | NEL_HD1_BN0703_LSL.ALM | BN 703 LOW LEVEL!
BN703NOHL_ALM | Hydrator | BN 703 NO HIGH LEVEL FOR 5 MIN | On | USCNEL051 | NEL_HD1_BN0703_FTF.ALM | BN 703 NO HIGH LEVEL FOR 5 MIN
CV711_%OPEN | Hydrator | CV 711 VALVE POSITION | % OPEN | 100 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_ZT.IND
CV711_ACT | Hydrator | CV 711 WATER FLOW RATE | GPM | 75 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_FT.IND
CV711DAY_WATERTOT | Hydrator | CV 711 Water Totalizer - Current Day | GAL | 110000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_FT.TPT
CV711HIFLOW_ALM | Hydrator | CV 711 HIGH WATER FLOW ALARM!! | On | USCNEL051 | NEL_HD1_CV0711_FT.AH | CV 711 HIGH WATER FLOW ALARM!!
CV711HIFLOW_SP | Hydrator | CV 711 HIGH FLOW ALARM SETPOINT | GPM | 65 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_FT.AH_SPT
CV711LOFLOW_SP | Hydrator | CV 711 LOW FLOW ALARM SETPOINT | A | 65 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_FT.AL_SPT
CV711LOWFLOW_ALM | Hydrator | CV 711 LOW WATER FLOW ALARM!! | On | USCNEL051 | NEL_HD1_CV0711_FT.AL | CV 711 LOW WATER FLOW ALARM!!
CV711PCMAN_SP | Hydrator | CV711 % VALVE OPEN PC SETPOINT | % OPEN | 100 | 0.25 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_ZT.SPT
CV711PCPID_SP | Hydrator | CV 711 PC SETPOINT GPM | GPM | 75 | 0.25 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_FT.SPT
CV711PID_AM | Hydrator | CV 711 AUTO/MANUAL IND 0=MAN 1=AUTO | None | USCNEL051 | NEL_HD1_CV0711_FT.PID_SSA_HMI
CV711YEST_WATERTOT | Hydrator | CV 711 Water Totalizer- Yesterdays | GAL | 110000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_CV0711_FT.TPY
DC414_DIFF_PRESSURE | Hydrator | DC 414 DIFF PRESSURE BACK LIME HANDLING | "WC | 10 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_DC4414_PT.IND | DC 414 DIFF PRESSURE
DC414_DIFF_PRESSURE_INH | Hydrator | DC 414 DIFF PRESSURE BACK LIME HANDLING INHIBITOR | None | 0
DF711_AUTO | Hydrator | DF 711 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_DF0711.SSA_LCS | DF 711 IN AUTO POSITION
DF711_IM | Hydrator | DF 711 INTERLOCKS MET | None | USCNEL051 | DF711_IM | DF 711 INTERLOCKS MET
DF711_IT | Hydrator | DF 711 AMPS | A | 75 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_DF0711_IT.IND | DF 711 AMPS
DF711_PBS | Hydrator | DF 711 PC START | None | USCNEL051 | NEL_HD1_DF0711.PBE_HMI | DF 711 PC START
DF711_PBT | Hydrator | DF 711 PC STOP | None | USCNEL051 | NEL_HD1_DF0711.PBS_HMI | DF 711 PC STOP
DF711FTS_ALM | Hydrator | DF 711 FAILED TO START!! | On | USCNEL051 | NEL_HD1_DF0711.FTS_ALM | DF 711 FAILED TO START!!
DF711HIIT_SP | Hydrator | DF 711 HI AMP ALARM SETPOINT | A | 60 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_DF0711_IT.AH_SPT
DF711IT_ALM | Hydrator | DF 711 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_DF0711_IT.AH | DF 711 HIGH AMPS!!
DF711MS_X | Hydrator | DF 711 AUX FDBK | Off | USCNEL051 | NEL_HD1_DF0711.AUX | DF 711 STOPPED!!
FN714_AUTO | Hydrator | FN 714 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_FN0714.SSA_LCS | FN 714 IN AUTO POSITION
FN714_IM | Hydrator | FN 714 INTERLOCKS MET | None | USCNEL051 | FN714_IM | FN 714 INTERLOCKS MET
FN714_IT | Hydrator | FN 714 AMPS | A | 15 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0714_IT.IND | FN 714 AMPS
FN714_PBS | Hydrator | FN 714 PC START | None | USCNEL051 | NEL_HD1_FN0714.PBE_HMI | FN 714 PC START
FN714_PBT | Hydrator | FN 714 PC STOP | None | USCNEL051 | NEL_HD1_FN0714.PBS_HMI | FN 714 PC STOP
FN714FTS_ALM | Hydrator | FN 714 FAILED TO START!! | On | USCNEL051 | NEL_HD1_FN0714.FTS_ALM | FN 714 FAILED TO START!!
FN714MS_X | Hydrator | FN 714 AUX FDBK | Off | USCNEL051 | NEL_HD1_FN0714.AUX | FN 714 STOPPED!!
FN721_AUTO | Hydrator | FN 721 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_FN0721.SSA_LCS | FN 721 IN AUTO POSITION
FN721_IM | Hydrator | FN 721 INTERLOCKS MET | None | USCNEL051 | FN721_IM | FN 721 INTERLOCKS MET
FN721_IT | Hydrator | FN 721 AMPS | A | 50 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0721_IT.IND | FN 721 AMPS
FN721_PBS | Hydrator | FN 721 PC START | None | USCNEL051 | NEL_HD1_FN0721.PBE_HMI | FN 721 PC START
FN721_PBT | Hydrator | FN 721 PC STOP | None | USCNEL051 | NEL_HD1_FN0721.PBS_HMI | FN 721 PC STOP
FN721FTS_ALM | Hydrator | FN 721 FAILED TO START | On | USCNEL051 | NEL_HD1_FN0721.FTS_ALM | FN 721 FAILED TO START
FN721HIIT_SP | Hydrator | FN 721 HI AMP ALARM SETPOINT | A | 40 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0721_IT.AH_SPT
FN721IT_ALM | Hydrator | FN 721 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_FN0721_IT.AH | FN 721 HIGH AMPS!!
FN721LOIT_SP | Hydrator | PM 721 LOW AMP ALARM SETPOINT | A | 40 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0721_IT.AL_SPT
FN721LOWIT_ALM | Hydrator | FN 721 LOW AMP ALARM!! | On | USCNEL051 | NEL_HD1_FN0721_IT.AL | FN 721 LOW AMP ALARM!!
FN721MS_X | Hydrator | FN 721 AUX FDBK | Off | USCNEL051 | NEL_HD1_FN0721.AUX | FN 721 STOPPED!!
FN725_AUTO | Hydrator | FN 725 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_FN0725.SSA_LCS | FN 725 IN AUTO POSITION
FN725_IM | Hydrator | FN 725 INTERLOCKS MET | None | USCNEL051 | FN725_IM | FN 725 INTERLOCKS MET
FN725_IT | Hydrator | FN 725 AMPS | A | 30 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0725_IT.IND | FN 725 AMPS
FN725_PBS | Hydrator | FN 725 PC START | None | USCNEL051 | NEL_HD1_FN0725.PBE_HMI | FN 725 PC START
FN725_PBT | Hydrator | FN 725 PC STOP | None | USCNEL051 | NEL_HD1_FN0725.PBS_HMI | FN 725 PC STOP
FN725FTS_ALM | Hydrator | FN 725 FAILED TO START!! | On | USCNEL051 | NEL_HD1_FN0725.FTS_ALM | FN 725 FAILED TO START!!
FN725HIIT_SP | Hydrator | FN 725 HI AMP ALARM SETPOINT | A | 30 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0725_IT.AH_SPT
FN725IT_ALM | Hydrator | FN 725 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_FN0725_IT.AH | FN 725 HIGH AMPS!!
FN725LOIT_SP | Hydrator | FN 725 LOW AMP ALARM SETPOINT | A | 30 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_FN0725_IT.AL_SPT
FN725LOWIT_ALM | Hydrator | FN 725 LOW AMP ALARM!! | On | USCNEL051 | NEL_HD1_FN0725_IT.AL | FN 725 LOW AMP ALARM!!
FN725MS_X | Hydrator | FN 725 AUX FDBK | Off | USCNEL051 | NEL_HD1_FN0725.AUX | FN 725 STOPPED!!
HM717_AUTO | Hydrator | HM 717 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_HM0717.SSA_LCS | HM 717 IN AUTO POSITION
HM717_IM | Hydrator | HM 717 INTERLOCKS MET | None | USCNEL051 | HM717_IM | HM 717 INTERLOCKS MET
HM717_IT | Hydrator | HM 717 AMPS | A | 150 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_HM0717_IT.IND | HM 717 AMPS
HM717_PBS | Hydrator | HM 717 PC START | None | USCNEL051 | NEL_HD1_HM0717.PBE_HMI | HM 717 PC START
HM717_PBT | Hydrator | HM 717 PC STOP | None | USCNEL051 | NEL_HD1_HM0717.PBS_HMI | HM 717 PC STOP
HM717FTS_ALM | Hydrator | HM 717 FAIL TO START!! | On | USCNEL051 | NEL_HD1_HM0717.FTS_ALM | HM 717 FAIL TO START!!
HM717HIIT_SP | Hydrator | HM 717 HI AMP ALARM SETPOINT | A | 120 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_HM0717_IT.AH_SPT
HM717IT_ALM | Hydrator | HM 717 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_HM0717_IT.AH | HM 717 HIGH AMPS!!
HM717LOIT_SP | Hydrator | HM 717 LOW AMP ALARM SETPOINT | A | 120 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_HM0717_IT.AL_SPT
HM717LOWIT_ALM | Hydrator | HM 717 LOW AMP ALARM!! | On | USCNEL051 | NEL_HD1_HM0717_IT.AL | HM 717 LOW AMP ALARM!!
HM717MS_X | Hydrator | HM 717 AUX FDBK | Off | USCNEL051 | NEL_HD1_HM0717.AUX | HM 717 STOPPED!!K
HYDMOIST%_10AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1000.IND
HYDMOIST%_10AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1000.TPY
HYDMOIST%_10PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2200.IND
HYDMOIST%_10PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2200.TPY
HYDMOIST%_11AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 11 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1100.IND
HYDMOIST%_11AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1100.TPY
HYDMOIST%_11PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 11 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2300.IND
HYDMOIST%_11PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2300.TPY
HYDMOIST%_12AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 12 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0000.IND
HYDMOIST%_12AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0000.TPY
HYDMOIST%_12PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 12 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1200.IND
HYDMOIST%_12PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1200.TPY
HYDMOIST%_1AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 1 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0100.IND
HYDMOIST%_1AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0100.TPY
HYDMOIST%_1PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 1 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1300.IND
HYDMOIST%_1PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1300.TPY
HYDMOIST%_2AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 2 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0200.IND
HYDMOIST%_2AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0200.TPY
HYDMOIST%_2PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 2 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1400.IND
HYDMOIST%_2PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1400.TPY
HYDMOIST%_3AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 3 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0300.IND
HYDMOIST%_3AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0300.TPY
HYDMOIST%_3PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 3 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1500.IND
HYDMOIST%_3PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1500.TPY
HYDMOIST%_4AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 4 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0400.IND
HYDMOIST%_4AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0400.TPY
HYDMOIST%_4PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 4 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1600.IND
HYDMOIST%_4PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1600.TPY
HYDMOIST%_5AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 5 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0500.IND
HYDMOIST%_5AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0500.TPY
HYDMOIST%_5PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 5 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1700.IND
HYDMOIST%_5PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1700.TPY
HYDMOIST%_6AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 6 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0600.IND
HYDMOIST%_6AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0600.TPY
HYDMOIST%_6PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 6 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1800.IND
HYDMOIST%_6PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1800.TPY
HYDMOIST%_7AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 7 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0700.IND
HYDMOIST%_7AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0700.TPY
HYDMOIST%_7PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 7 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1900.IND
HYDMOIST%_7PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_1900.TPY
HYDMOIST%_8AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 8 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0800.IND
HYDMOIST%_8AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0800.TPY
HYDMOIST%_8PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 8 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2000.IND
HYDMOIST%_8PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2000.TPY
HYDMOIST%_9AM | Hydrator | FINISHED HYDRATE % MOISTURE AT 8 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0900.IND
HYDMOIST%_9AM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_0900.TPY
HYDMOIST%_9PM | Hydrator | FINISHED HYDRATE % MOISTURE AT 9 PM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2100.IND
HYDMOIST%_9PM_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AT 10 AM | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_2100.TPY
HYDMOIST%_DAVG | Hydrator | FINISHED HYDRATE % MOISTURE DAY SHIFT AVERAGE | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_DS.AVG
HYDMOIST%_DAVG_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE DAY SHIFT AVERAGE | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_DS.TPY
HYDMOIST%_GAVG | Hydrator | FINISHED HYDRATE % MOISTURE GRAVE SHIFT AVERAGE | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_NS.AVG
HYDMOIST%_GAVG_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE GRAVE SHIFT AVERAGE | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2_NS.TPY
HYDMOIST%_LAST | Hydrator | FINISHED HYDRATE % MOISTURE AT LAST READING | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | HYDMOIST_LAST
HYDMOIST%_TAVG | Hydrator | FINISHED HYDRATE % MOISTURE AVERAGE | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2.AVG
HYDMOIST%_TAVG_PrevDay | Hydrator | FINISHED HYDRATE % MOISTURE AVERAGE | % MOISTURE | 5 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT2.TPY
HYDRES200_11AM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 11 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1100.IND
HYDRES200_11AM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 11 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1100.TPY
HYDRES200_11PM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 11 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_2300.IND
HYDRES200_11PM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 11 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_2300.TPY
HYDRES200_1AM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 1 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0100.IND
HYDRES200_1AM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 11 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0100.TPY
HYDRES200_1PM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 1 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1300.IND
HYDRES200_1PM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 1 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1300.TPY
HYDRES200_3AM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 3 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0300.IND
HYDRES200_3AM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 3 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0300.TPY
HYDRES200_3PM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 3 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1500.IND
HYDRES200_3PM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 1 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1500.TPY
HYDRES200_5AM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 5 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0500.IND
HYDRES200_5AM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 5 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0500.TPY
HYDRES200_5PM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 5 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1700.IND
HYDRES200_5PM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 5 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1700.TPY
HYDRES200_7AM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 7 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0700.IND
HYDRES200_7AM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 7 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0700.TPY
HYDRES200_7PM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 7 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1900.IND
HYDRES200_7PM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 7 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_1900.TPY
HYDRES200_9AM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 9 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0900.IND
HYDRES200_9AM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 9 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_0900.TPY
HYDRES200_9PM | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 9 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_2100.IND
HYDRES200_9PM_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT 9 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_2100.TPY
HYDRES200_DAVG | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE DAY SHIFT AVERAG | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_DS.AVG
HYDRES200_DAVG_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE DAY SHIFT AVERAG | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_DS.TPY
HYDRES200_GAVG | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE GRAVE SHIFT AVER | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_NS.AVG
HYDRES200_GAVG_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE GRAVE SHIFT AVER | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2_NS.TPY
HYDRES200_LAST | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AT LAST READING | % | 50 | 0.001 | 0 | 0 | USCNEL051 | HYDRES200_LAST
HYDRES200_TAVG | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AVERAGE | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2.AVG
HYDRES2001_TAVG_PrevDay | Hydrator | FINISHED HYDRATE 200 MESH RESIDUE AVERAGE | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR2.TPY
HYDRES30_11AM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 11 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1100.IND
HYDRES30_11AM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 11 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1100.TPY
HYDRES30_11PM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 11 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_2300.IND
HYDRES30_11PM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 11 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_2300.TPY
HYDRES30_1AM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 1 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0100.IND
HYDRES30_1AM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 1 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0100.TPY
HYDRES30_1PM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 1 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1300.IND
HYDRES30_1PM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 11 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1300.TPY
HYDRES30_3AM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 3 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0300.IND
HYDRES30_3AM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 3 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0300.TPY
HYDRES30_3PM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 3 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1500.IND
HYDRES30_3PM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 3 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1500.TPY
HYDRES30_5AM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 5 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0500.IND
HYDRES30_5AM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 3 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0500.TPY
HYDRES30_5PM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 5 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1700.IND
HYDRES30_5PM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 5 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1700.TPY
HYDRES30_7AM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 7 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0700.IND
HYDRES30_7AM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 7 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0700.TPY
HYDRES30_7PM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 7 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1900.IND
HYDRES30_7PM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 7 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_1900.TPY
HYDRES30_9AM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 9 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0900.IND
HYDRES30_9AM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 9 AM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_0900.TPY
HYDRES30_9PM | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 9 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_2100.IND
HYDRES30_9PM_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT 9 PM | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_2100.TPY
HYDRES30_DAVG | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE DAY SHIFT AVERAGE | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_DS.AVG
HYDRES30_DAVG_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE DAY SHIFT AVERAGE | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_DS.TPY
HYDRES30_GAVG | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE GRAVE SHIFT AVERA | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_NS.AVG
HYDRES30_GAVG_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE GRAVE SHIFT AVERA | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1_NS.TPY
HYDRES30_LAST | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AT LAST READING | % | 50 | 0.001 | 0 | 0 | USCNEL051 | HYDRES30_LAST
HYDRES30_TAVG | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AVERAGE | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1.AVG
HYDRES30_TAVG_PrevDay | Hydrator | FINISHED HYDRATE 30 MESH RESIDUE AVERAGE | % | 50 | 0.001 | 0 | 0 | USCNEL051 | NEL_HD1_BE0713_FR1.TPY
MCR7_MCC | Hydrator | MCR 7 MCC HIGHLIGHT BUCKET # | # | 500 | 0 | 0 |  | 0 | 0 | 0
MOIST%_HYD | Hydrator | SS 710 HYDRATE MOISTURE READING | % MOISTURE | 5 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT.IND | SS 710 HYDRATE MOISTURE READING
MOIST%AVG_HYD | Hydrator | SS 710 HYDRATE AVERAGE MOISTURE READING | % MOISTURE | 5 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_MT.STATS.AVE | SS 710 HYDRATE AVERAGE MOISTURE READING
PLANT_AMBIENT_AIR | Hydrator | Plant Ambient Air Temp | °F | 500 | 0 | 0 | 0 | USCNEL051 | NEL_HD1_AMBIENT_TT.IND
PM708_AUTO | Hydrator | PM 708 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_PM0708.SSA_LCS | PM 708 IN AUTO POSITION
PM708_IM | Hydrator | PM 708 INTERLOCKS MET | None | USCNEL051 | PM708_IM | PM 708 INTERLOCKS MET
PM708_IT | Hydrator | PM 708 AMPS | A | 15 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_PM0708_IT.IND | PM 708 AMPS
PM708_PBS | Hydrator | PM 708 PC START | None | USCNEL051 | NEL_HD1_PM0708.PBE_HMI | PM 708 PC START
PM708_PBT | Hydrator | PM 708 PC STOP | None | USCNEL051 | NEL_HD1_PM0708.PBS_HMI | PM 708 PC STOP
PM708FTS_ALM | Hydrator | PM 708 FAILED TO START!! | On | USCNEL051 | NEL_HD1_PM0708.FTS_ALM | PM 708 FAILED TO START!!
PM708HIIT_SP | Hydrator | PM 708 HI AMP ALARM SETPOINT | A | 15 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_PM0708_IT.AH_SPT
PM708IT_ALM | Hydrator | PM 708 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_PM0708_IT.AH | PM 708 HIGH AMPS!!
PM708MS_X | Hydrator | PM 708 AUX FDBK | Off | USCNEL051 | NEL_HD1_PM0708.AUX | PM 708 STOPPED!!
PT711_ACT | Hydrator | PT 711 Ducon Differential Pressure 0-15" | "WC | 15 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_DF0711_PT.IND
RA714A_AUTO | Hydrator | RA 714-A IN AUTO POSITION | None | USCNEL051 | NEL_HD1_RV0714A.SSA_LCS | RA 714-A IN AUTO POSITION
RA714A_BYP | Hydrator | RA 714-A MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_RV0714A.SS_BYP_PB | RA 714-A MOTION SWITCH BYPASS
RA714A_IM | Hydrator | RA 714-A INTERLOCKS MET | None | USCNEL051 | RV714A_IM | RA 714-A INTERLOCKS MET
RA714A_PBS | Hydrator | RA 714-A PC START | None | USCNEL051 | NEL_HD1_RV0714A.PBE_HMI | RA 714-A PC START
RA714A_PBT | Hydrator | RA 714-A PC STOP | None | USCNEL051 | NEL_HD1_RV0714A.PBS_HMI | RA 714-A PC STOP
RA714AFTS_ALM | Hydrator | RA 714-A FAILED TO START!! | On | USCNEL051 | NEL_HD1_RV0714A.FTS_ALM | RA 714-A FAILED TO START!!
RA714AMS_X | Hydrator | RA 714-A AUX FDBK | Off | USCNEL051 | NEL_HD1_RV0714A.AUX | RA 714-A STOPPED!!
RA714AMSF_ALM | Hydrator | RA 714-A MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_RV0714A.SS_ALM | RA 714-A MOTION SWITCH FAILURE!!
RA716_AUTO | Hydrator | RA 716 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_RA0716.SSA_LCS | RA 716 IN AUTO POSITION
RA716_BYP | Hydrator | RA 716 MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_RA0716.SS_BYP_PB | RA 716 MOTION SWITCH BYPASS
RA716_IM | Hydrator | RA 716 INTERLOCKS MET | None | USCNEL051 | RA716_IM | RA 716 INTERLOCKS MET
RA716_PBS | Hydrator | RA 716 PC START | None | USCNEL051 | NEL_HD1_RA0716.PBE_HMI | RA 716 PC START
RA716_PBT | Hydrator | RA 716 PC STOP | None | USCNEL051 | NEL_HD1_RA0716.PBS_HMI | RA 716 PC STOP
RA716FTS_ALM | Hydrator | RA 716 FAILED TO START!! | On | USCNEL051 | NEL_HD1_RA0716.FTS_ALM | RA 716 FAILED TO START!!
RA716MS_X | Hydrator | RA 716 AUX FDBK | Off | USCNEL051 | NEL_HD1_RA0716.AUX | RA 716 STOPPED!!
RA716MSF_ALM | Hydrator | RA 716 MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_RA0716.SS_ALM | RA 716 MOTION SWITCH FAILURE!!
RA723_AUTO | Hydrator | RA 723 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_RA0723.SSA_LCS | RA 723 IN AUTO POSITION
RA723_BYP | Hydrator | RA 723 MOTION SWITCH BYPASSED | On | USCNEL051 | NEL_HD1_RA0723.SS_BYP_PB | RA 723 MOTION SWITCH BYPASSED
RA723_IM | Hydrator | RA 723 INTERLOCKS MET | None | USCNEL051 | RA723_IM | RA 723 INTERLOCKS MET
RA723_PBS | Hydrator | RA 723 PC START | None | USCNEL051 | NEL_HD1_RA0723.PBE_HMI | RA 723 PC START
RA723_PBT | Hydrator | RA 723 PC STOP | None | USCNEL051 | NEL_HD1_RA0723.PBS_HMI | RA 723 PC STOP
RA723FTS_ALM | Hydrator | RA 723 FAILED TO START!! | On | USCNEL051 | NEL_HD1_RA0723.FTS_ALM | RA 723 FAILED TO START!!
RA723MS_X | Hydrator | RA 723 AUX FDBK | Off | USCNEL051 | NEL_HD1_RA0723.AUX | RA 723 STOPPED!!
RA723MSF_ALM | Hydrator | RA 723 MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_RA0723.SS_ALM | RA 723 MOTION SWITCH FAILURE!!
SC701_AUTO | Hydrator | SC 701 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_SC0701.SSA_LCS | SC 701 IN AUTO POSITION
SC701_AUTOFILL | Hydrator | SC 701 AUTO FILL | None | USCNEL051 | SC701_AUTOFILL | SC 701 AUTO FILL
SC701_BYP | Hydrator | SC 701 MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_SC0701.SS_BYP_PB | SC 701 MOTION SWITCH BYPASS
SC701_IM | Hydrator | SC 701 INTERLOCKS MET | None | USCNEL051 | SC701_IM | SC 701 INTERLOCKS MET
SC701_PBS | Hydrator | SC 701 PC START | None | USCNEL051 | NEL_HD1_SC0701.PBE_HMI | SC 701 PC START
SC701_PBT | Hydrator | SC 701 PC STOP | None | USCNEL051 | NEL_HD1_SC0701.PBS_HMI | SC 701 PC STOP
SC701FTS_ALM | Hydrator | SC 701 FAILED TO START | On | USCNEL051 | NEL_HD1_SC0701.FTS_ALM | SC 701 FAILED TO START
SC701MS_X | Hydrator | SC 701 AUX FDBK | None | USCNEL051 | NEL_HD1_SC0701.AUX | SC 701 STOPPED!
SC701MSF_ALM | Hydrator | SC 701 MOTION SWITCH FAILURE | On | USCNEL051 | NEL_HD1_SC0701.SS_ALM | SC 701 MOTION SWITCH FAILURE
SC702_AUTO | Hydrator | SC 702 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_SC0702.SSA_LCS | SC 702 IN AUTO POSITION
SC702_AUTOFILL | Hydrator | SC 702 AUTO FILL BN 703 | None | USCNEL051 | SC702_AUTOFILL | SC 702 AUTO FILL BN 703
SC702_BYP | Hydrator | SC 702 MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_SC0702.SS_BYP_PB | SC 702 MOTION SWITCH BYPASS
SC702_IM | Hydrator | SC 702 INTERLOCKS MET | None | USCNEL051 | SC702_IM | SC 702 INTERLOCKS MET
SC702_PBS | Hydrator | SC 702 PC START | None | USCNEL051 | NEL_HD1_SC0702.PBE_HMI | SC 702 PC START
SC702_PBT | Hydrator | SC 702 PC STOP | None | USCNEL051 | NEL_HD1_SC0702.PBS_HMI | SC 702 PC STOP
SC702A_MS_X | Hydrator | SC 702A AUX FDBK | None | USCNEL051 | NEL_HD1_SC702A.AUX | SC 702A STOPPED!
SC702AMS_X | Hydrator |  | None | USCNEL051 | NEL_HD1_SC702A.AUX | SC 702A STOPPED!
SC702AMSF_ALM | Hydrator |  | On | USCNEL051 | NEL_HD1_SC702A.SS_ALM | SC 702A Motion Switch not detected
SC702FTS_ALM | Hydrator | SC 702 FAILED TO START | On | USCNEL051 | NEL_HD1_SC0702.FTS_ALM | SC 702 FAILED TO START
SC702MS_X | Hydrator |  | None | USCNEL051 | NEL_HD1_SC0702.AUX | SC 702 STOPPED!
SC702MSF_ALM | Hydrator | SC 702 MOTION SWITCH FAILURE | On | USCNEL051 | NEL_HD1_SC0702.SS_ALM | SC 702 MOTION SWITCH FAILURE
SC707_AUTO | Hydrator | SC 707 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_SC0707.SSA_LCS | SC 707 IN AUTO POSITION
SC707_BYP | Hydrator | SC 707 MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_SC0707.SS_BYP_PB | SC 707 MOTION SWITCH BYPASS
SC707_IM | Hydrator | SC 707 INTERLOCKS MET | None | USCNEL051 | SC707_IM | SC 707 INTERLOCKS MET
SC707_PBS | Hydrator | SC 707 PC START | None | USCNEL051 | NEL_HD1_SC0707.PBE_HMI | SC 707 PC START
SC707_PBT | Hydrator | SC 707 PC STOP | None | USCNEL051 | NEL_HD1_SC0707.PBS_HMI | SC 707 PC STOP
SC707FTS_ALM | Hydrator | SC 707 FAILED TO START!! | On | USCNEL051 | NEL_HD1_SC0707.FTS_ALM | SC 707 FAILED TO START!!
SC707MS_X | Hydrator | SC 707 AUX FDBK | Off | USCNEL051 | NEL_HD1_SC0707.AUX | SC 707 STOPPED!!
SC707MSF_ALM | Hydrator | SC 707 MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_SC0707.SS_ALM | SC 707 MOTION SWITCH FAILURE!!
SC712_AUTO | Hydrator | SC 712 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_SC0712.SSA_LCS | SC 712 IN AUTO POSITION
SC712_BYP | Hydrator | SC 712 MOTION SWITCH BYPASS | On | USCNEL051 | NEL_HD1_SC0712.SS_BYP_PB | SC 712 MOTION SWITCH BYPASS
SC712_IM | Hydrator | SC 712 INTERLOCKS MET | None | USCNEL051 | SC712_IM | SC 712 INTERLOCKS MET
SC712_IT | Hydrator | SC 712 AMPS | A | 20 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_SC0712_IT.IND | SC 712 AMPS
SC712_PBS | Hydrator | SC 712 PC START | None | USCNEL051 | NEL_HD1_SC0712.PBE_HMI | SC 712 PC START
SC712_PBT | Hydrator | SC 712 PC STOP | None | USCNEL051 | NEL_HD1_SC0712.PBS_HMI | SC 712 PC STOP
SC712FTS_ALM | Hydrator | SC 712 FAILED TO START! | On | USCNEL051 | NEL_HD1_SC0712.FTS_ALM | SC 712 FAILED TO START!
SC712HIIT_SP | Hydrator | SC 712 HI AMP ALARM SETPOINT | A | 20 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_SC0712_IT.AH_SPT
SC712IT_ALM | Hydrator | SC 712 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_SC0712_IT.AH | SC 712 HIGH AMPS!!
SC712MS_X | Hydrator | SC 712 AUX FDBK | Off | USCNEL051 | NEL_HD1_SC0712.AUX | SC 712 STOPPED!!
SC712MSF_ALM | Hydrator | SC 712 MOTION SWITCH FAILURE! | On | USCNEL051 | NEL_HD1_SC0712.SS_ALM | SC 712 MOTION SWITCH FAILURE!
SC718_AUTO | Hydrator | SC 718 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_SC0718.SSA_LCS | SC 718 IN AUTO POSITION
SC718_BYP | Hydrator | SC 718 MOTION SWITCH BYPASSED!! | On | USCNEL051 | NEL_HD1_SC0718.SS_BYP_PB | SC 718 MOTION SWITCH BYPASSED!!
SC718_IM | Hydrator | SC 718 INTERLOCKS MET | None | USCNEL051 | SC718_IM | SC 718 INTERLOCKS MET
SC718_IT | Hydrator | SC 718 AMPS | A | 15 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_SC0718_IT.IND | SC 718 AMPS
SC718_PBS | Hydrator | SC 718 PC START | None | USCNEL051 | NEL_HD1_SC0718.PBE_HMI | SC 718 PC START
SC718_PBT | Hydrator | SC 718 PC STOP | None | USCNEL051 | NEL_HD1_SC0718.PBS_HMI | SC 718 PC STOP
SC718FTS_ALM | Hydrator | SC 718 FAILED TO START!! | On | USCNEL051 | NEL_HD1_SC0718.FTS_ALM | SC 718 FAILED TO START!!
SC718HIIT_SP | Hydrator | SC 718 HI AMP ALARM SETPOINT | A | 15 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_SC0718_IT.AH_SPT
SC718IT_ALM | Hydrator | SC 718 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_SC0718_IT.AH | SC 718 HIGH AMPS!!
SC718MS_X | Hydrator | SC 718 AUX FDBK | None | USCNEL051 | NEL_HD1_SC0718.AUX | SC 718 STOPPED!!
SC718MSF_ALM | Hydrator | SC 718 MOTION SWITCH FAILURE!! | On | USCNEL051 | NEL_HD1_SC0718.SS_ALM | SC 718 MOTION SWITCH FAILURE!!
SILO64HRHI_ALM | Hydrator | SILO 6 HIGH LEVEL FOR 4 HOURS!! | On | USCNEL051 | NEL_HD1_SL0006_FTF.ALM | SILO 6 HIGH LEVEL FOR 4 HOURS!!
SILO6HL_ALM | Hydrator | SILO 6 HIGH LEVEL!! | On | USCNEL051 | NEL_HD1_SL0006_LSH.ALM | SILO 6 HIGH LEVEL!!
SS710_AUTO | Hydrator | SS 710 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_SS0710.SSA_LCS | SS 710 IN AUTO POSITION
SS710_IM | Hydrator | SS 710 INTERLOCKS MET | None | USCNEL051 | SS710_IM | SS 710 INTERLOCKS MET
SS710_IT | Hydrator | SS 710 AMPS | A | 50 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_IT.IND | SS 710 AMPS
SS710_PBS | Hydrator | SS 710 PC START | None | USCNEL051 | NEL_HD1_SS0710.PBE_HMI | SS 710 PC START
SS710_PBT | Hydrator | SS 710 PC STOP | None | USCNEL051 | NEL_HD1_SS0710.PBS_HMI | SS 710 PC STOP
SS710FTS_ALM | Hydrator | SS 710 FAILED TO START!! | On | USCNEL051 | NEL_HD1_SS0710.FTS_ALM | SS 710 FAILED TO START!!
SS710HIIT_SP | Hydrator | SS 710 HI AMP ALARM SETPOINT | A | 50 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_SS0710_IT.AH_SPT
SS710IT_ALM | Hydrator | SS 710 HIGH AMPS!! | On | USCNEL051 | NEL_HD1_SS0710_IT.AH | SS 710 HIGH AMPS!!
SS710MS_X | Hydrator | SS 710 AUX FDBK | Off | USCNEL051 | NEL_HD1_SS0710.AUX | SS 710 STOPPED!!
TE700_ACT | Hydrator | TE 700 TEMPERATURE | F | 1000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_TE0700_TT.IND | TE 700 TEMPERATURE
TE700HITEMP_ALM | Hydrator | SS 710 HI TEMP ALARM!! | On | USCNEL051 | NEL_HD1_TE0700_TT.AH | SS 710 HI TEMP ALARM!!
TE700HITEMP_SP | Hydrator | TE 700 HIGH TEMP ALARM SP | deg F | 220 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_TE0700_TT.AH_SPT
WF704_%VFD | Hydrator | WF 704 % VFD | % VFD | 100 | 0.25 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_ST.SPT | WF 704 % VFD
WF704_ACT | Hydrator | WF 704 ACTUAL TON/HR LIME FEED | TON/HR | 15 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.IND | WF 704 ACTUAL TON/HR LIME FEED
WF704_AUTO | Hydrator | WF 704 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_WF0704.SSA_LCS | WF 704 IN AUTO POSITION
WF704_IM | Hydrator | WF 704 INTERLOCKS MET | None | USCNEL051 | WF704_IM | WF 704 INTERLOCKS MET
WF704_PBS | Hydrator | WF 704 PC START | None | USCNEL051 | NEL_HD1_WF0704.PBE_HMI | WF 704 PC START
WF704_PBT | Hydrator | WF 704 PC STOP | None | USCNEL051 | NEL_HD1_WF0704.PBS_HMI | WF 704 PC STOP
WF704_PC_AM | Hydrator | WF 704 PC AUTO/MANUAL TOGGLE 1=MANUAL 0=AUTO | None | USCNEL051 | NEL_HD1_WF0704.SSA_HMI | WF 704 PC AUTO/MANUAL TOGGLE 0=MANUAL 1=AUTO
WF704DAY_HOURTOT | Hydrator | WF 704 RUN TIME TOTALIZER - CURRENT DAY | HOURS | 24 | 0.01 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_RT_TPT_HRS | WF 704 RUN TIME TOTALIZER - CURRENT DAY
WF704DAY_HYDTOT | Hydrator | WF 704 CURRENT DAY HYDRATE TOTALIZER | TON HYDRATE | 500 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT2.TPT | WF 704 CURRENT DAY HYDRATE TOTALIZER
WF704DAY_LIMETOT | Hydrator | WF 704 CURRENT DAILY TOTALIZER | TON LIME | 400 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.TPT | WF 704 CURRENT DAILY TOTALIZER
WF704FTS_ALM | Hydrator | WF 704 FAILED TO START!! | On | USCNEL051 | NEL_HD1_WF0704.FTS_ALM | WF 704 FAILED TO START!!
WF704HYDPROD_SP | Hydrator | Hydrator Production Based on WF 704 Feedrate SP | TON/HR | 20 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT2.SPT
WF704MS_X | Hydrator | WF 704 AUX FDBK | Off | USCNEL051 | NEL_HD1_WF0704.AUX | WF 704 STOPPED!!
WF704PCMAN_SP | Hydrator | WF 704 PC MANUAL SETPOINT | % VFD | 100 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_ST.SPT | WF 704 PC MANUAL SETPOINT
WF704PCPID_SP | Hydrator | WF 704 PC SETPOINT TO PID LOOP IN TON/HR LIME FEED | TON/HR | 15 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.SPT | WF 704 PC SETPOINT TO PID LOOP IN TON/HR LIME FEED
WF704PID_AM | Hydrator | WF 704 PID A/M INDICATOR 0=MANUAL 1=AUTO | None | USCNEL051 | NEL_HD1_WF0704_QT.PID_SSA_HMI | WF 704 PID A/M INDICATOR 0=MANUAL 0=AUTO
WF704PID_CV | Hydrator | WF 704 PID CONTROL VARIABLE (VFD SPEED) |  | 4095 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_ST.SPT | WF 704 PID CONTROL VARIABLE (VFD SPEED)
WF704PID_DB | Hydrator | WF 704 PID DEADBAND |  | 4095 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.PID.DB | WF 704 PID DEADBAND
WF704PID_DR | Hydrator | WF 704 DERIVATIVE RATE | 0.01 MIN | 5000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.PID_KD | WF 704 DERIVATIVE RATE
WF704PID_ER | Hydrator | WF 704 PID ERROR (SP-PV) |  | 4095 | 1 | 0 | -4095 | USCNEL051 | NEL_HD1_WF0704_QT.PID.ERR | WF 704 PID ERROR (SP-PV)
WF704PID_PG | Hydrator | WF 704 PID PROPORTIONAL GAIN | 0.01 | 5000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.PID_KP | WF 704 PID PROPORTIONAL GAIN
WF704PID_PV | Hydrator | WF 704 PROCESS VARIABLE (LIME TPH) |  | 4095 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.IND | WF 704 PROCESS VARIABLE (LIME TPH)
WF704PID_RT | Hydrator | WF 704 PID RES TIME | 0.01 MIN/REPEAT | 5000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.PID_KI | WF 704 PID RES TIME
WF704PID_SP | Hydrator | WF 704 PID SETPOINT (LIME TPH) |  | 4095 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.SPT | WF 704 PID SETPOINT (LIME TPH)
WF704PID_TB | Hydrator | WF 704 PID TIEBACK (VFD SPEED) |  | 4095 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.PID.TIE | WF 704 PID TIEBACK (VFD SPEED)
WF704PID_UT | Hydrator | WF 704 PID UPDATE TIME | 0.01 SEC | 1000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.PID_TMR.PRE | WF 704 PID UPDATE TIME
WF704YEST_HOURTOT | Hydrator | WF 704 RUN TIME TOTALIZER - YESTERDAY | HOURS | 24 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_RT_TPY_HRS | WF 704 RUN TIME TOTALIZER - YESTERDAY
WF704YEST_HYDTOT | Hydrator | WF 704 PREVIOUS DAY'S TOTAL HYDRATE PRODUCTION | TON HYDRATE | 500 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT2.TPY | WF 704 PREVIOUS DAY'S TOTAL HYDRATE PRODUCTION
WF704YEST_LIMETOT | Hydrator | WF 704 PREVIOUS DAYS LIME TOTALIZER | TON HYDRATE | 400 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_WF0704_QT.TPY | WF 704 PREVIOUS DAYS LIME TOTALIZER
WP709_AUTO | Hydrator | WP 709 IN AUTO POSITION | None | USCNEL051 | NEL_HD1_WP0709.SSA_LCS | WP 709 IN AUTO POSITION
WP709_IM | Hydrator | WP 709 INTERLOCKS MET | None | USCNEL051 | WP709_IM | WP 709 INTERLOCKS MET
WP709_PBS | Hydrator | WP 709 PC START | None | USCNEL051 | NEL_HD1_WP0709.PBE_HMI | WP 709 PC START
WP709_PBT | Hydrator | WP 709 PC STOP | None | USCNEL051 | NEL_HD1_WP0709.PBS_HMI | WP 709 PC STOP
WP709FTS_ALM | Hydrator | WP 709 FAILED TO START!! | On | USCNEL051 | NEL_HD1_WP0709.FTS_ALM | WP 709 FAILED TO START!!
WP709MS_X | Hydrator | WP 709 AUX FDBK | Off | USCNEL051 | NEL_HD1_WP0709.AUX | WP 709 STOPPED!!
WT709AHL_ALM | Hydrator | WT 709 HIGH LEVEL! | On | USCNEL051 | NEL_HD1_WT0709A_LSH.ALM | Canyon Well Hydrator Tank High Level!
WT709BLL_ALM | Hydrator | WT 709 LOW LEVEL! | Off | USCNEL051 | NEL_HD1_WT0709B_LSL.ALM | Canyon Well Hydrator Tank Low Level!
WV709A_%OPEN | Hydrator | WV 709-A VALVE POSITION | % OPEN | 100 | 0.1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_ZT.IND | WV 709-A VALVE POSITION
WV709A_ACT | Hydrator | WV 709-A WATER FLOW RATE | GPM | 75 | 0.05 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.IND | WV 709-A WATER FLOW RATE
WV709A_PC_AM | Hydrator | WV 709-A PC AUTO/MANUAL TOGGLE 0=MANUAL 1=AUTO | None | USCNEL051 | NEL_HD1_WV0709A_FT.PID_SSA_HMI | WV 709-A PC AUTO/MANUAL TOGGLE 0=MANUAL 1=AUTO
WV709ADAY_WATERTOT | Hydrator | WV 709-A WATER TOTALIZER - CURRENT DAY | GAL | 110000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.TPT | WV 709-A WATER TOTALIZER - CURRENT DAY
WV709AHIFLOW_ALM | Hydrator | WV 709-A HIGH WATER FLOW ALARM!! | On | USCNEL051 | NEL_HD1_WV0709A_FT.AH | WV 709-A HIGH WATER FLOW ALARM!!
WV709AHIFLOW_SP | Hydrator | WV 709-A HIGH FLOW ALARM SETPOINT | A | 65 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.AH_SPT
WV709ALOFLOW_SP | Hydrator | WV 709-A LOW FLOW ALARM SETPOINT | A | 65 | 0.5 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.AL_SPT
WV709ALOWFLOW_ALM | Hydrator | WV 709-A LOW WATER FLOW ALARM!! | On | USCNEL051 | NEL_HD1_WV0709A_FT.AL | WV 709-A LOW WATER FLOW ALARM!!
WV709APCMAN_SP | Hydrator | WV 709-A % VALVE OPEN PC SETPOINT | % OPEN | 100 | 0.25 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_ZT.SPT | WV 709-A % VALVE OPEN PC SETPOINT
WV709APCPID_SP | Hydrator | WV 709-A PC SETPOINT GPM | GPM | 75 | 0.25 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.SPT | WV 709-A PC SETPOINT GPM
WV709APID_AM | Hydrator | WV 709-A AUTO/MANUAL IND 0=MAN 1=AUTO | None | USCNEL051 | NEL_HD1_WV0709A_FT.PID_SSA_HMI | WV 709-A AUTO/MANUAL IND 0=MAN 1=AUTO
WV709APID_CV | Hydrator | WV 709-A PID CONTROL VARIABLE (VALVE POSITION) |  | 4095 | 5 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_ZT.SPT | WV 709-A PID CONTROL VARIABLE (VALVE POSITION)
WV709APID_DB | Hydrator | WV 709-A PID DEADBAND |  | 4095 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID.DB | WV 709-A PID DEADBAND
WV709APID_DR | Hydrator | WV 709-A DERIVATIVE RATE | 0.01 MIN | 5000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID_KD | WV 709-A DERIVATIVE RATE
WV709APID_ER | Hydrator | WV 709-A PID ERROR (SP-PV) |  | 4095 | 5 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID.ERR | WV 709-A PID ERROR (SP-PV)
WV709APID_PG | Hydrator | WV 709-A PID PROPORTIONAL GAIN | 0.01 | 5000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID_KP | WV 709-A PID PROPORTIONAL GAIN
WV709APID_PV | Hydrator | WV 709-A PROCESS VARIABLE (WATER GPM) |  | 4095 | 0 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.IND | WV 709-A PROCESS VARIABLE (WATER GPM)
WV709APID_RT | Hydrator | WV 709-A PID RES TIME | 0.01 MIN/REPEAT | 5000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID_KI | WV 709-A PID RES TIME
WV709APID_SP | Hydrator | WV 709-A PID SETPOINT (WATER GPM) |  | 4095 | 5 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.SPT | WV 709-A PID SETPOINT (WATER GPM)
WV709APID_TB | Hydrator | WV 709-A PID TIEBACK (VALVE POSITION) |  | 4095 | 5 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID.TIE | WV 709-A PID TIEBACK (VALVE POSITION)
WV709APID_UT | Hydrator | WV 709-A PID UPDATE TIME | 0.01 MIN | 1000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.PID_TMR.PRE | WV 709-A PID UPDATE TIME
WV709AYEST_WATERTOT | Hydrator | WV 709-A WATER TOTALIZER - YESTERDAYS | GAL | 110000 | 1 | 0 | 0 | USCNEL051 | NEL_HD1_WV0709A_FT.TPY | WV 709-A WATER TOTALIZER - YESTERDAYS
WV711A_IM | Hydrator | WV 711-A INTERLOCKS MET | None | USCNEL051 | WV711A_IM | WV 711-A INTERLOCKS MET
WV711A_TOG | Hydrator | WV 711-A TOGGLE OPEN/CLOSED | None | USCNEL051 | WV711A_TOG | WV 711-A TOGGLE OPEN/CLOSED
WV711B_Close | Hydrator | WV 711-B PC Close Valve | None | USCNEL051 | NEL_HD1_WV0711B.PBC_HMI
WV711B_Open | Hydrator | WV 711-B PC Open Valve | None | USCNEL051 | NEL_HD1_WV0711B.PBO_HMI
WV711B_Opened | Hydrator | WV 711-B Valve Open | None | USCNEL051 | NEL_HD1_WV0711B.COIL
WV711C_Close | Hydrator | WV 711-C PC Close Valve | None | USCNEL051 | NEL_HD1_WV0711C.PBC_HMI
WV711C_Open | Hydrator | WV 711-C PC Open Valve | None | USCNEL051 | NEL_HD1_WV0711C.PBO_HMI
WV711C_Opened | Hydrator | WV 711-C Valve Open | None | USCNEL051 | NEL_HD1_WV0711C.COIL
ADEQ_K1FUELTOT_HOUR | Kiln1 | KILN 1 TOTAL TONS FUEL PER HOUR | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:151 | KILN 1 TONS LIMESTONE PER HOUR
ADEQ_K1LIMETOT_HOUR | Kiln1 | KILN 1 TOTAL TONS LIME PER HOUR | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:149 | KILN 1 TONS LIMESTONE PER HOUR
ADEQ_K1STR | Kiln1 | KILN 1 STROKES/HR | STROKES/HR | 250 | 1 | 0 | 0 | PLC_FLTREAD | F9:200 | KILN 1 STROKES/HR
ADEQ_K1STR_HOUR | Kiln1 | KILN 1 STROKES/HR HOURLY READING | STROKES/HR | 250 | 1 | 0 | 0 | PLC_FLTREAD | F9:216 | KILN 1 STROKES/HR HOURLY READING
ADEQ_K1TONFUELLSPHR | Kiln1 | KILN 1 TONS COAL/COKE AND LIMESTONE PER HOUR | TONS/HR | 150 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:205 | KILN 1 TONS COAL/COKE AND LIMESTONE PER HOUR
ADEQ_K1TONFUELLSPHR_HOUR | Kiln1 | KILN 1 TONS FUEL AND LIMESTONE PER HOUR - HOURLY | TONS/HR | 150 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:221 | KILN 1 TONS FUEL AND LIMESTONE PER HOUR - HOURLY
ADEQ_K1TONFUELPHR | Kiln1 | KILN 1 TONS COAL/COKE PER HOUR | TON/HR | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:204 | KILN 1 TONS COAL/COKE PER HOUR
ADEQ_K1TONFUELPHR_HOUR | Kiln1 | KILN 1 TONS COAL/COKE PER HOUR - HOURLY READING | TON/HR | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:220 | KILN 1 TONS COAL/COKE PER HOUR - HOURLY READING
ADEQ_K1TONLSPHR | Kiln1 | KILN 1 TONS LIMESTONE PER HOUR | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:203 | KILN 1 TONS LIMESTONE PER HOUR
ADEQ_K1TONLSPHR_HOUR | Kiln1 | KILN 1 TONS LIMESTONE PER HOUR - HOURLY READING | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:219 | KILN 1 TONS LIMESTONE PER HOUR - HOURLY READING
ADEQ_K1TONLSPSTR | Kiln1 | KILN 1 TONS LIMESTONE PER STROKE | TON/STROKE | 1 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:202 | KILN 1 TONS LIMESTONE PER STROKE
ADEQ_K1TONLSPSTR_HOUR | Kiln1 | KILN 1 TONS LIMESTONE PER STROKE - HOURLY READING | TON/STROKE | 1 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:218 | KILN 1 TONS LIMESTONE PER STROKE - HOURLY READING
ADEQ_K1TOTSTR | Kiln1 | KILN 1 TOTAL STROKES | TOT | 10000 | 10 | 0 | 0 | PLC_FLTREAD | F9:201 | KILN 1 TOTAL STROKES
ADEQ_K1TOTSTR_DAY | Kiln1 | KILN 1 TOTAL STROKES - DAILY | STROKES | 9999 | 1 | 0 | 0 | PLC_FLTREAD | F9:120 | KILN 1 TOTAL STROKES - DAILY
ADEQ_K1TOTSTR_HOUR | Kiln1 | KILN 1 TOTAL STROKES - HOURLY READING | STROKES | 10000 | 1 | 0 | 0 | PLC_FLTREAD | F9:217 | KILN 1 TOTAL STROKES - HOURLY READING
ADEQ_K1TOTTONLS | Kiln1 | KILN 1 TOTAL TONS LIMESTONE | TONS | 2500 | 1 | 0 | 0 | PLC_FLTREAD | F9:206 | KILN 1 TOTAL TONS LIMESTONE
ADEQ_K1TOTTONLS_DAY | Kiln1 | KILN 1 TOTAL TON LIMESTONE - DAILY | STROKES | 2000 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:121 | KILN 1 TOTAL TON LIMESTONE - DAILY
ADEQ_K1TOTTONLS_HOUR | Kiln1 | KILN 1 TOTAL TONS LIMESTONE - HOURLY READING | TONS | 2500 | 1 | 0 | 0 | PLC_FLTREAD | F9:222 | KILN 1 TOTAL TONS LIMESTONE - HOURLY READING
BDP_K1LIME | Kiln1 | KILN 1 LIME Best Demonstrated Performance | TON | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:76 | KILN 1 LIME TOTALIZER
BE1317_IM | Kiln1 | BE 1-317 INTERLOCKS MET | None | PLC_DISCREAD | B3/272 | BE 1-317 INTERLOCKS MET
BE1317_JOGIN | Kiln1 | BE 1-317 JOG PLUG INSERTED | None | PLC_DISCREAD | I:24/06
BE1317_PBS | Kiln1 | BE 1-317 PC START | None | PLC_DISCWRITE | B100/314 | BE 1-317 PC START
BE1317_PBT | Kiln1 | BE 1-317 PC STOP | None | PLC_DISCWRITE | B100/280 | BE 1-317 PC STOP
BE1317FTS_ALM | Kiln1 | BE 1-317 FAILED TO START | On | PLC_ALARM | B101/239 | BE 1-317 FAILED TO START
BE1317MS_BYP | Kiln1 | BE 1-317 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/74 | BE 1-317 MOTION SWITCH BYPASSED
BE1317MS_X | Kiln1 | BE 1-317 AUX FDBK | Off | PLC_DISCREAD | I:24/02 | BE 1-317 STOPPED
BE1317MSF_ALM | Kiln1 | BE 1-317 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/240 | BE 1-317 MOTION SWITCH FAILURE
BM1602_IM | Kiln1 | BM 1602 INTERLOCKS MET | None | PLC_DISCREAD | B3/257 | BM 1602 INTERLOCKS MET
BM1602_IT | Kiln1 | BM 1-602 AMPS | Amps | 110 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:176 | BM 1-602 AMPS
BM1602_LT | Kiln1 | BM 1-602 LEVEL | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:173 | BM 1-602 LEVEL
BM1602_PBS | Kiln1 | BM 1-602 PC START | None | PLC_DISCWRITE | B100/458 | BM 1-602 PC START
BM1602_PBT | Kiln1 | BM 1-602 PC STOP | None | PLC_DISCWRITE | B100/448 | BM 1-602 PC STOP
BM1602_PDT | Kiln1 | BM 1-602 DIFFERENTIAL PRESSURE | "WC | 5 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:164 | BM 1-602 DIFFERENTIAL PRESSURE
BM1602_SSA_HMI | Kiln1 | BM 1-602 Kiln 1 Ball mill 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1345 | BM 1-602 Kiln 1 Ball mill 0=Auto 1=Man
BM1602FTS_ALM | Kiln1 | BM 1-602 FAILED TO START | On | PLC_ALARM | B101/257 | BM 1-602 FAILED TO START
BM1602HIAMP_ALM | Kiln1 | BM 1-602 HIGH AMP ALARM | On | PLC_ALARM | B101/469 | BM 1-602 HIGH AMP ALARM
BM1602HIOUTTEMP_ALM | Kiln1 | BM 1-602 OUTLET TEMP > 180 | On | PLC_ALARM | B101/470 | BM 1-602 OUTLET TEMP > 180
BM1602HITEMP_ALM | Kiln1 | BM 1-602 INLET TEMP > 540 | On | PLC_ALARM | B101/471 | BM 1-602 INLET TEMP > 540
BM1602LUBEFAIL_ALM | Kiln1 | BM 1602 LUBE FAILURE! | On | PLC_ALARM | B101:36/13 | BM 1602 LUBE FAILURE!
BM1602MS_X | Kiln1 | BM 1602 FDBK | Off | PLC_DISCREAD | I:106/06 | BM 1-602 STOPPED!!
BM1602TT_1 | Kiln1 | BM 1-602 INLET TEMPERATURE | °F | 1000 | 3 | 0 | 0 | PLC_INTREAD | N39:16 | BM 1-602 INLET TEMPERATURE
BM1602TT_2 | Kiln1 | BM 1-602 OUTLET TEMPERATURE | °F | 1000 | 2 | 0 | 0 | PLC_INTREAD | N39:17 | BM 1-602 OUTLET TEMPERATURE
BM1602TT1_PIDSP | Kiln1 | BM INLET TEMP PID SP FOR FV 1-607-B | F | 540 | 1 | 0 | 500 | PLC_INTWRITE | N102:58 | BM INLET TEMP PID SP FOR FV 1-607-B
BM1602TT2_PIDSP | Kiln1 | BM OUTLET TEMP PID SP FOR FV 1-607-B | F | 185 | 1 | 0 | 160 | PLC_INTWRITE | N102:57 | BM OUTLET TEMP PID SP FOR FV 1-607-B
BV4518_EN | Kiln1 | BV 1-518 ENABLED TO RUN | None | PLC_DISCREAD | B3/357 | BV 1-518 ENABLED TO RUN
BV4518_IM | Kiln1 | BV 1-518 INTERLOCKS MET | None | PLC_DISCREAD | B3/283 | BV 1-518 INTERLOCKS MET
BV4518_PAUSE | Kiln1 | BV 1-518 PAUSE TIMER SETPOINT | SEC | 120 | 1 | 0 | 0 | PLC_INTWRITE | T4:147.PRE | BV 1-518 PAUSE TIMER SETPOINT
BV4518_PBS | Kiln1 | BV 1-518 PC START | None | PLC_DISCWRITE | B100/456 | BV 1-518 PC START
BV4518_PBT | Kiln1 | BV 1-518 PC STOP | None | PLC_DISCWRITE | B100/446 | BV 1-518 PC STOP
BV4518_RUN | Kiln1 | BV 4518 RUN TIMER SETPOINT | SEC | 120 | 1 | 0 | 0 | PLC_INTWRITE | T4:146.PRE | BV 4518 RUN TIMER SETPOINT
BV4518_SSA_HMI | Kiln1 | BV 1-518 Auto Man switch 0=Auto 1=Man | None | PLC_DISCWRITE | B3/1602 | BV 1-518 Auto Man switch 0=Auto 1=Man
BV4518FTS_ALM | Kiln1 | BV 1-518 FAILED TO START | On | PLC_ALARM | B101/255 | BV 1-518 FAILED TO START
BV4518MS_X | Kiln1 | BV 4518 AUX FDBK | None | PLC_DISCREAD | I:106/04 | BV 4518 AUX FDBK
C1310_HILVL | Kiln1 | KILN 1 COOLER HIGH LEVEL | None | PLC_DISCREAD | N102:171/1 | KILN 1 COOLER HIGH LEVEL
C1310_LOLVL | Kiln1 | KILN 1 COOLER LOW LEVEL | None | PLC_DISCREAD | N102:170/1 | KILN 1 COOLER LOW LEVEL
C1310HI_ALM | Kiln1 | C 1-310 HIGH LEVEL TOO LONG | On | PLC_ALARM | T70:0.DN | C 1-310 HIGH LEVEL TOO LONG
C1310HIGH_ALMSP | Kiln1 | C 1-310 HIGH LEVEL TOO LONG |  | 3600 | 0 | 0 | 0 | PLC_INTWRITE | T70:00.PRE | C 1-310 HIGH LEVEL TOO LONG
C1310LO_ALM | Kiln1 | C 1-310 LOW LEVEL TOO LONG | On | PLC_ALARM | T70:1.DN | C 1-310 LOW LEVEL TOO LONG
C1310LOW_ALMSP | Kiln1 | C 1-310 LOW LEVEL TOO LONG |  | 7200 | 0 | 0 | 0 | PLC_INTWRITE | T70:01.PRE | C 1-310 LOW LEVEL TOO LONG
CM1602LT_TREND | Kiln1 | Kiln #1 coal mill level trending |  | 100 | 1 | 0 | Kiln #1 coal mill level trending | 0 | 0 | 0
CM1602PDT_TREND | Kiln1 | KILN #1 COAL MILL DIFF PRESSURE TRENDING |  | 5 | 0.1 | 0 | KILN #1 COAL MILL DIFF PRESSURE TRENDING | 0 | 0 | 0
CM1602TT_1_TREND | Kiln1 | KILN 1 COAL MILL INLET TEMPERATURE |  | 800 | 2 | 0 | KILN 1 COAL MILL INLET TEMPERATURE | 0 | 0 | 0
CM1602TT_2_TREND | Kiln1 | KILN 1 COAL MILL OUTLET TEMPERATURE |  | 400 | 2 | 0 | KILN 1 COAL MILL OUTLET TEMPERATURE | 0 | 0 | 0
CO1310TT_1_STREND | Kiln1 | KILN #1 SECONDARY AIR TEMPERTURE |  | 1000 | 5 | 0 | KILN #1 SECONDARY AIR TEMPERTURE | 0 | 0 | 0
CO1310TT_1_TREND | Kiln1 | KILN 1 SECONDARY AIR TEMPERATURE |  | 1800 | 5 | 0 | KILN 1 SECONDARY AIR TEMPERATURE | 0 | 0 | 0
CO1310TT_2_TREND | Kiln1 | KILN 1 COOLER PRODUCT TEMPERATURE |  | 1000 | 5 | 0 | KILN 1 COOLER PRODUCT TEMPERATURE | 0 | 0 | 0
DC1_319_OULETTEMP | Kiln1 | PRIMARY OUTLET KILN1 DC1-319 | DEG F | 1000 | 2 | 0 | 0 | PLC_INTREAD | N60:01 | DC1_319_OULETTEMP
DC1313PT_1 | Kiln1 | KILN 1 FILTER BED INLET PRESSURE | " WC | 2.5 | 0.02 | 0 | -2.5 | PLC_FLTREAD | F9:170 | KILN 1 FILTER BED INLET PRESSURE
DC1313PT_2 | Kiln1 | KILN 1 FILTER BED OUTLET PRESSURE | " WC | 15 | 0.02 | 0 | 0 | PLC_FLTREAD | F9:169 | KILN 1 FILTER BED OUTLET PRESSURE
DC1319_PDT | Kiln1 | KILN 1 DUST COLLECTOR 319 DIFF. PRESS | " WC | 50 | 0.02 | 0 | 0 | PLC_FLTREAD | F9:87 | KILN 1 DUST COLLECTOR 319 DIFF. PRESS
DG1342_POS1 | Kiln1 | KILN 1 DIVERTER GATE TO PC 401 | None | PLC_DISCWRITE | B100/511 | KILN 1 DIVERTER GATE TO PC 401
DG1342_POS2 | Kiln1 | KILN 1 DIVERTER GATE TO PC 420 | None | PLC_DISCWRITE | B100/512 | KILN 1 DIVERTER GATE TO PC 420
DG1342_POS3 | Kiln1 | KILN 1 DIVERTER GATE TO BC 401 AND PC 420 | None | PLC_DISCWRITE | B100/513 | KILN 1 DIVERTER GATE TO BC 401 AND PC 420
ESTTOT_K1LIME | Kiln1 | ESTIMATED KILN 1 LIME TOTALIZER AT STROKE RATE | TON | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:7 | KILN 1 LIME TOTALIZER
FH1309_DOOR | Kiln1 | FH 1-309 INDICATE HOOD DOOR OPEN/CLOSED FOR PID | None | PLC_DISCWRITE | B100/70 | FH 1-309 INDICATE HOOD DOOR OPEN/CLOSED FOR PID
FH1309_PT | Kiln1 | KILN 1 FIRING HOOD DRAFT | "WC | 1 | 0.005 | 0 | -1 | PLC_FLTREAD | F9:167 | KILN 1 FIRING HOOD DRAFT
FH1309DOOR_VIS | Kiln1 | FH 1-309 OPEN/CLOSE DOOR BUTTON VISIBILITY CONTROL | None | PLC_DISCREAD | B3/315 | FH 1-309 OPEN/CLOSE DOOR BUTTON VISIBILITY CONTROL
FN1307A_AUTO | Kiln1 | FN 1-307-A Field switch in Auto | None | PLC_DISCREAD | I:25/12 | FN 1-307-A Field switch in Auto
FN1307A_IM | Kiln1 | FN 1-307-A INTERLOCKS MET | None | PLC_DISCREAD | B3/970 | FN 1-307-A INTERLOCKS MET
FN1307A_PBS | Kiln1 | FN 1-307-A PC START | None | PLC_DISCWRITE | B100/749 | FN 1-307-A PC START
FN1307A_PBT | Kiln1 | FN 1-307-A PC STOP | None | PLC_DISCWRITE | B100/748 | FN 1-307-A PC STOP
FN1307A_SSA_HMI | Kiln1 | FN 1-307-A 0=Auto 1=Man | None | PLC_ALARM | b3/1262 | FN 1-307-A FAILED TO START!
FN1307AFTS_ALM | Kiln1 | FN 1-307-A FAILED TO START! | On | PLC_ALARM | B101/140 | FN 1-307-A FAILED TO START!
FN1307AMS_X | Kiln1 | FN 1-307-A AUX FDBK | Off | PLC_DISCREAD | I:25/14 | FN 1-307-A STOPPED!
FN1312_IM | Kiln1 | FN 1-312 INTERLOCKS MET | None | PLC_DISCREAD | B3/267 | FN 1-312 INTERLOCKS MET
FN1312_IT | Kiln1 | FN 1-312 AMPS | Amps | 999 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:161 | FN 1-312 AMPS
FN1312_PBS | Kiln1 | FN 1-312 PC START | None | PLC_DISCWRITE | B100/431 | FN 1-312 PC START
FN1312_PBT | Kiln1 | FN 1-312 PC STOP | None | PLC_DISCWRITE | B100/410 | FN 1-312 PC STOP
FN1312_PDT | Kiln1 | FN 1-312 D/P | " H2O | 5 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:168 | FN 1-312 D/P
FN1312_SSA_HMI | Kiln1 | FN 1-312 cooler fan 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1279 | FN 1-312 cooler fan 0=Auto 1=Man
FN1312_ST_IND | Kiln1 | FV 1-312 COOLER FAN DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | FN1312_ST_IND | FV 1-312 COOLER FAN DAMPER POSITION
FN1312FTS_ALM | Kiln1 | FN 1-312 FAILED TO START | On | PLC_ALARM | B101/200 | FN 1-312 FAILED TO START
FN1312HIAMP_ALM | Kiln1 | FN 1-312 HIGH AMP ALARM | On | PLC_ALARM | B101/415 | FN 1-312 HIGH AMP ALARM
FN1312MS_X | Kiln1 | FN 1-312 AUX FDBK | Off | PLC_DISCREAD | N32:0/1 | FN 1-312 STOPPED
FN1313C1_AUTO | Kiln1 | FN 1-313-C1 IN AUTO POSITION | None | PLC_DISCREAD | I:73/0 | FN 1-313-C1 IN AUTO POSITION
FN1313C1_DISC | Kiln1 | FN 1-313-C1 DISCONNECT | None | PLC_DISCREAD | I:73/1 | FN 1-313-C1 DISCONNECT
FN1313C1_IM | Kiln1 | FN 1-313-C1 INTERLOCKS MET | None | PLC_DISCREAD | B3/282 | FN 1-313-C1 INTERLOCKS MET
FN1313C1_IT | Kiln1 | FN 1-313-C1 AMPS | AMPS | 60 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:304 | FN 1-313-C1 AMPS
FN1313C1_PBS | Kiln1 | FN 1-313-C1 PC START | None | PLC_DISCWRITE | B100/405 | FN 1-313-C1 PC START
FN1313C1_PBT | Kiln1 | FN 1-313-C1 PC STOP | None | PLC_DISCWRITE | B100/404 | FN 1-313-C1 PC STOP
FN1313C1_PT | Kiln1 | FN 1-313-C1 PRESSURE | " WC | 30 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:318 | FN 1-313-C1 PRESSURE
FN1313C1FTS_ALM | Kiln1 | FN 1-313-C1 FAILED TO START | On | PLC_ALARM | B101/221 | FN 1-313-C1 FAILED TO START
FN1313C1MS_X | Kiln1 | FN 1-313-C1 AUX FDBK | Off | PLC_DISCREAD | I:73/2 | FN 1-313-C1 STOPPED
FN1313C2_AUTO | Kiln1 | FN 1-313-C2 IN AUTO POSITION | None | PLC_DISCREAD | I:73/3 | FN 1-313-C2 IN AUTO POSITION
FN1313C2_DISC | Kiln1 | FN 1-313-C2 DISCONNECT | None | PLC_DISCREAD | I:73/4 | FN 1-313-C2 DISCONNECT
FN1313C2_IM | Kiln1 | FN 1-313-C2 INTERLOCKS MET | None | PLC_DISCREAD | B3/543 | FN 1-313-C2 INTERLOCKS MET
FN1313C2_IT | Kiln1 | FN 1-313-C2 AMPS | AMPS | 60 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:305 | FN 1-313-C2 AMPS
FN1313C2_PBS | Kiln1 | FN 1-313-C2 PC START | None | PLC_DISCWRITE | B100/472 | FN 1-313-C2 PC START
FN1313C2_PBT | Kiln1 | FN 1-313-C2 PC STOP | None | PLC_DISCWRITE | B100/471 | FN 1-313-C2 PC STOP
FN1313C2_PT | Kiln1 | FN 1-313-C2 PRESSURE | " WC | 30 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:319 | FN 1-313-C2 PRESSURE
FN1313C2FTS_ALM | Kiln1 | FN 1-313-C2 FAILED TO START | On | PLC_ALARM | B101/222 | FN 1-313-C2 FAILED TO START
FN1313C2MS_X | Kiln1 | FN 1-313-C2 AUX FDBK | Off | PLC_DISCREAD | I:73/5 | FN 1-313-C2 STOPPED
FN1314_0SP | Kiln1 | FN 1-314 SPEED SET TO ZERO | None | PLC_DISCREAD | I:25/01 | FN 1-314 SPEED SET TO ZERO
FN1314_IM | Kiln1 | FN 1-314 INTERLOCKS MET | None | PLC_DISCREAD | B3/270 | FN 1-314 INTERLOCKS MET
FN1314_IT | Kiln1 | FN 1-314 AMPS | A | 200 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:52 | FN 1-314 AMPS
FN1314_PBS | Kiln1 | FN 1-314 PC START | None | PLC_DISCWRITE | B100/385 | FN 1-314 PC START
FN1314_PBT | Kiln1 | FN 1-314 PC STOP | None | PLC_DISCWRITE | B100/364 | FN 1-314 PC STOP
FN1314_SP | Kiln1 | FN 1-314 SPEED PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:42 | FN 1-314 SPEED PC SETPOINT
FN1314_SPD | Kiln1 | FN 1-314 ID FAN SPEED | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:50 | FN 1-314 ID FAN SPEED
FN1314_ST | Kiln1 | FN 1314 SPEED | RPM | 1250 | 1 | 0 | 0 | PLC_FLTREAD | F9:63 | FN 1314 SPEED
FN1314CLOSED_ALM | Kiln1 | FN 1-314 CLOSED | On | PLC_ALARM | I:25/01 | FN 1-314 CLOSED
FN1314FTS_ALM | Kiln1 | FN 1-314 FAILED TO START! | On | PLC_ALARM | B101/233 | FN 1-314 FAILED TO START!
FN1314HIAMP_ALM | Kiln1 | FN 1-314 HIGH AMP ALARM | On | PLC_ALARM | B101/466 | FN 1-314 HIGH AMP ALARM
FN1314HIPID_SP | Kiln1 | FN 1-314 HI SPEED PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:52 | FN 1-314 HI SPEED PID SP
FN1314HIPRESS_ALM | Kiln1 | FN 1-314 AMERICAN STANDARD OIL PUMP PRESSURE HIGH | On | PLC_ALARM | I:26/17 | FN 1-314 AMERICAN STANDARD OIL PUMP PRESSURE HIGH
FN1314LOWPID_SP | Kiln1 | FN 1-314 LOW PID SPEED SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:51 | FN 1-314 LOW PID SPEED SP
FN1314LOWPRESS_ALM | Kiln1 | FN 1-314 LOW OIL PRESSURE | On | PLC_ALARM | I:26/16 | FN 1-314 LOW OIL PRESSURE
FN1314LOWPRESS10MIN_ALM | Kiln1 | FN 1-314 LOW OIL PRESSURE FOR 10 MIN SHUTDOWN FAN | On | PLC_ALARM | B101/262 | FN 1-314 LOW OIL PRESSURE FOR 10 MIN SHUTDOWN FAN
FN1314MOTWIND1_TT | Kiln1 | FN 1-314 MOTOR WINDING #1 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:381 | FN 1-314 MOTOR WINDING #1 TEMP
FN1314MOTWIND1TT_ALM | Kiln1 | FN 1-314 MOTOR WINDING 1 TEMP HIGH | On | PLC_ALARM | B101/420 | FN 1-314 MOTOR WINDING 1 TEMP HIGH
FN1314MOTWIND1TTHH_ALM | Kiln1 | FN 1-314 MOT WINDING #1 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/430 | FN 1-314 MOT WINDING #1 TEMP HIHI - SHUTDOWN 3 MIN
FN1314MOTWIND1TTSD_ALM | Kiln1 | FN 1-314 MOTOR WINDING #1 SHUTDOWN FAN | On | PLC_ALARM | B101/440 | FN 1-314 MOTOR WINDING #1 SHUTDOWN FAN
FN1314MOTWIND2_TT | Kiln1 | FN 1-314 MOTOR WINDING #2 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:382 | FN 1-314 MOTOR WINDING #2 TEMP
FN1314MOTWIND2TT_ALM | Kiln1 | FN 1-314 MOTOR WINDING 2 TEMP HIGH | On | PLC_ALARM | B101/421 | FN 1-314 MOTOR WINDING 2 TEMP HIGH
FN1314MOTWIND2TTHH_ALM | Kiln1 | FN 1-314 MOT WINDING #2 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/431 | FN 1-314 MOT WINDING #2 TEMP HIHI - SHUTDOWN 3 MIN
FN1314MOTWIND2TTSD_ALM | Kiln1 | FN 1-314 MOTOR WINDING #2 SHUTDOWN FAN | On | PLC_ALARM | B101/441 | FN 1-314 MOTOR WINDING #2 SHUTDOWN FAN
FN1314MOTWIND3_TT | Kiln1 | FN 1-314 MOTOR WINDING #3 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:383 | FN 1-314 MOTOR WINDING #3 TEMP
FN1314MOTWIND3TT_ALM | Kiln1 | FN 1-314 MOTOR WINDING 3 TEMP HIGH | On | PLC_ALARM | B101/422 | FN 1-314 MOTOR WINDING 3 TEMP HIGH
FN1314MOTWIND3TTHH_ALM | Kiln1 | FN 1-314 MOT WINDING #3 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/432 | FN 1-314 MOT WINDING #3 TEMP HIHI - SHUTDOWN 3 MIN
FN1314MOTWIND3TTSD_ALM | Kiln1 | FN 1-314 MOTOR WINDING #3 SHUTDOWN FAN | On | PLC_ALARM | B101/442 | FN 1-314 MOTOR WINDING #3 SHUTDOWN FAN
FN1314MOTWIND4_TT | Kiln1 | FN 1-314 MOTOR WINDING #4 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:384 | FN 1-314 MOTOR WINDING #4 TEMP
FN1314MOTWIND4TT_ALM | Kiln1 | FN 1-314 MOTOR WINDING 4 TEMP HIGH | On | PLC_ALARM | B101/423 | FN 1-314 MOTOR WINDING 4 TEMP HIGH
FN1314MOTWIND4TTHH_ALM | Kiln1 | FN 1-314 MOT WINDING #4 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/433 | FN 1-314 MOT WINDING #4 TEMP HIHI - SHUTDOWN 3 MIN
FN1314MOTWIND4TTSD_ALM | Kiln1 | FN 1-314 MOTOR WINDING #4 SHUTDOWN FAN | On | PLC_ALARM | B101/443 | FN 1-314 MOTOR WINDING #4 SHUTDOWN FAN
FN1314MOTWIND5_TT | Kiln1 | FN 1-314 MOTOR WINDING #5 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:385 | FN 1-314 MOTOR WINDING #5 TEMP
FN1314MOTWIND5TT_ALM | Kiln1 | FN 1-314 MOTOR WINDING 5 TEMP HIGH | On | PLC_ALARM | B101/424 | FN 1-314 MOTOR WINDING 5 TEMP HIGH
FN1314MOTWIND5TTHH_ALM | Kiln1 | FN 1-314 MOT WINDING #5 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/434 | FN 1-314 MOT WINDING #5 TEMP HIHI - SHUTDOWN 3 MIN
FN1314MOTWIND5TTSD_ALM | Kiln1 | FN 1-314 MOTOR WINDING #5 SHUTDOWN FAN | On | PLC_ALARM | B101/444 | FN 1-314 MOTOR WINDING #5 SHUTDOWN FAN
FN1314MOTWIND6_TT | Kiln1 | FN 1-314 MOTOR WINDING #6 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:386 | FN 1-314 MOTOR WINDING #6 TEMP
FN1314MOTWIND6TT_ALM | Kiln1 | FN 1-314 MOTOR WINDING 6 TEMP HIGH | On | PLC_ALARM | B101/425 | FN 1-314 MOTOR WINDING 6 TEMP HIGH
FN1314MOTWIND6TTHH_ALM | Kiln1 | FN 1-314 MOT WINDING #6 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/435 | FN 1-314 MOT WINDING #6 TEMP HIHI - SHUTDOWN 3 MIN
FN1314MOTWIND6TTSD_ALM | Kiln1 | FN 1-314 MOTOR WINDING #6 SHUTDOWN FAN | On | PLC_ALARM | B101/445 | FN 1-314 MOTOR WINDING #6 SHUTDOWN FAN
FN1314MS_X | Kiln1 | FN 1-314 AUX FDBK | Off | PLC_DISCREAD | I:25/16 | FN 1-314 STOPPED
FN1314NFANBEAR_TT | Kiln1 | FN 1-314 NORTH FAN BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:377 | FN 1-314 NORTH FAN BEARING TEMP
FN1314NFANBEARTT_ALM | Kiln1 | FN 1-314 NORTH FAN BEARING TEMP HIGH | On | PLC_ALARM | B101/416 | FN 1-314 NORTH FAN BEARING TEMP HIGH
FN1314NFANBEARTTHH_ALM | Kiln1 | FN 1-314 N. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/426 | FN 1-314 N. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN1314NFANBEARTTSD_ALM | Kiln1 | FN 1-314 NORTH FAN BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/436 | FN 1-314 NORTH FAN BEARING SHUTDOWN FAN
FN1314NMOTBEAR_TT | Kiln1 | FN 1-314 NORTH MOTOR BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:379 | FN 1-314 NORTH MOTOR BEARING TEMP
FN1314NMOTBEARTT_ALM | Kiln1 | FN 1-314 NORTH MOTOR BEARING TEMP HIGH | On | PLC_ALARM | B101/418 | FN 1-314 NORTH MOTOR BEARING TEMP HIGH
FN1314NMOTBEARTTHH_ALM | Kiln1 | FN 1-314 N. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/428 | FN 1-314 N. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN1314NMOTBEARTTSD_ALM | Kiln1 | FN 1-314 NORTH MOTOR BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/438 | FN 1-314 NORTH MOTOR BEARING SHUTDOWN FAN
FN1314PID_%RUN | Kiln1 | KILN 1 OXYGEN PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:289 | KILN 1 OXYGEN PID % RUNTIME - TODAY
FN1314PID_%RUN_YEST | Kiln1 | KILN 1 OXYGEN PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:339 | KILN 1 OXYGEN PID % RUNTIME - PAST
FN1314PID_AVAIL | Kiln1 | KILN 1 OXYGEN PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:288 | KILN 1 OXYGEN PID AVAIL RUN HOURS - TODAY
FN1314PID_AVAIL_YEST | Kiln1 | KILN 1 OXYGEN PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:338 | KILN 1 OXYGEN PID AVAIL RUN HOURS - PAST
FN1314SFANBEAR_TT | Kiln1 | FN 1-314 SOUTH FAN BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:378 | FN 1-314 SOUTH FAN BEARING TEMP
FN1314SFANBEARTT_ALM | Kiln1 | FN 1-314 SOUTH FAN BEARING TEMP HIGH | On | PLC_ALARM | B101/417 | FN 1-314 SOUTH FAN BEARING TEMP HIGH
FN1314SFANBEARTTHH_ALM | Kiln1 | FN 1-314 S. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/427 | FN 1-314 S. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN1314SFANBEARTTSD_ALM | Kiln1 | FN 1-314 SOUTH FAN BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/437 | FN 1-314 SOUTH FAN BEARING SHUTDOWN FAN
FN1314SMOTBEAR_TT | Kiln1 | FN 1-314 SOUTH MOTOR BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:380 | FN 1-314 SOUTH MOTOR BEARING TEMP
FN1314SMOTBEARTT_ALM | Kiln1 | FN 1-314 SOUTH MOTOR BEARING TEMP HIGH | On | PLC_ALARM | B101/419 | FN 1-314 SOUTH MOTOR BEARING TEMP HIGH
FN1314SMOTBEARTTHH_ALM | Kiln1 | FN 1-314 S. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/429 | FN 1-314 S. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN1314SMOTBEARTTSD_ALM | Kiln1 | FN 1-314 SOUTH MOTOR BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/439 | FN 1-314 SOUTH MOTOR BEARING SHUTDOWN FAN
FN1314TT_ALM | Kiln1 | FN 1-314 INLET TEMPERATURE > 550 | On | PLC_ALARM | B101/467 | FN 1-314 INLET TEMPERATURE > 550
FN1314TT_TREND | Kiln1 | KILN 1 ID FAN 314 INLET TEMPERATURE | DEG F | 600 | 2 | 0 | KILN 1 ID FAN 314 INLET TEMPERATURE | 0 | 0 | 0
FN1321_BYP | Kiln1 | FN 1-321 BYPASSED | On | PLC_DISCWRITE | B100/406 | FN 1-321 BYPASSED
FN1321_IM | Kiln1 | FN 1-321 INTERLOCKS MET | None | PLC_DISCREAD | B3/271 | FN 1-321 INTERLOCKS MET
FN1321_PBS | Kiln1 | FN 1-321 PC START | None | PLC_DISCWRITE | B100/199 | FN 1-321 PC START
FN1321_PBT | Kiln1 | FN 1-321 PC STOP | None | PLC_DISCWRITE | B100/183 | FN 1-321 PC STOP
FN1321FTS_ALM | Kiln1 | FN 1-321 FAILED TO START | On | PLC_ALARM | B101/243 | FN 1-321 FAILED TO START
FN1321MS_X | Kiln1 | FN 1-321 AUX FDBK | Off | PLC_DISCREAD | I:24/5 | FN 1-321 STOPPED
FN1326_IM | Kiln1 | FN 1-326 INTERLOCKS MET | None | PLC_DISCREAD | B3/263 | FN 1-326 INTERLOCKS MET
FN1326_PBS | Kiln1 | FN 1-326 PC START | None | PLC_DISCWRITE | B100/376 | FN 1-326 PC START
FN1326_PBT | Kiln1 | FN 1-326 PC STOP | None | PLC_DISCWRITE | B100/355 | FN 1-326 PC STOP
FN1326_SSA_HMI | Kiln1 | FN 1-326 water cooler fan 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1320 | FN 1-326 water cooler fan 0=Auto 1=Man
FN1326FTS_ALM | Kiln1 | FN 1-326 FAILED TO START | On | PLC_ALARM | B101/244 | FN 1-326 FAILED TO START
FN1326MS_X | Kiln1 | FN 1-326 AUX FDBK | Off | PLC_DISCREAD | I:25/05 | FN 1-326 STOPPED
FN1331_IM | Kiln1 | FN 1331 INTERLOCKS MET | None | PLC_DISCREAD | B3/268 | FN 1331 INTERLOCKS MET
FN1331_IT | Kiln1 | FN 1-331 AMPS | " WC | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:53 | FN 1-331 AMPS
FN1331_PBS | Kiln1 | FN 1-331 PC START | None | PLC_DISCWRITE | B100/384 | FN 1-331 PC START
FN1331_PBT | Kiln1 | FN 1-331 PC STOP | None | PLC_DISCWRITE | B100/363 | FN 1-331 PC STOP
FN1331_TT | Kiln1 | FN 1-331 INLET TEMP | DEG F | 1000 | 1 | 0 | 0 | PLC_INTREAD | N58:01 | FN 1-331 INLET TEMP
FN1331CLOSED_ALM | Kiln1 | FN 1-331 DAMPER CLOSED | None | PLC_ALARM | I:25/00 | FN 1-331 DAMPER CLOSED
FN1331FTS_ALM | Kiln1 | FN 1331 FAILED TO START | On | PLC_ALARM | B101/248 | FN 1331 FAILED TO START
FN1331HIAMP_ALM | Kiln1 | FN 1-331 HIGH AMP ALARM | On | PLC_ALARM | B101/468 | FN 1-331 HIGH AMP ALARM
FN1331MS_X | Kiln1 | FN 1-331 AUX FDBK | Off | PLC_DISCREAD | I:25/15 | FN 1-331 STOPPED
FN1335_IM | Kiln1 | FN 1-335 INTERLOCKS MET | None | PLC_DISCREAD | B3/260 | FN 1-335 INTERLOCKS MET
FN1335_PBS | Kiln1 | FN 1-335 PC START | None | PLC_DISCWRITE | B100/454 | FN 1-335 PC START
FN1335_PBT | Kiln1 | FN 1-335 PC STOP | None | PLC_DISCWRITE | B100/444 | FN 1-335 PC STOP
FN1335_SSA_HMI | Kiln1 | FN 1-335 nose ring fan 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1274 | FN 1-335 nose ring fan 0=Auto 1=Man
FN1335FTS_ALM | Kiln1 | FN 1335 FAILED TO START | On | PLC_ALARM | B101/249 | FN 1335 FAILED TO START
FN1335MS_X | Kiln1 | FN 1-335 AUX FDBK | Off | PLC_DISCREAD | I:106/02 | FN 1-335 STOPPED
FN1341_IM | Kiln1 | FN 1-341 INTERLOCKS MET | None | PLC_DISCREAD | B3/256 | FN 1-341 INTERLOCKS MET
FN1341_IT | Kiln1 | FN 1341 AMPS | Amps | 45 | 0.5 | 0 | 0 | PLC_FLTREAD | F27:17 | FN 1341 AMPS
FN1341_PBS | Kiln1 | FN 1-341 PC START | None | PLC_DISCWRITE | B100/509 | FN 1-341 PC START
FN1341_PBT | Kiln1 | FN 1341 PC STOP | None | PLC_DISCWRITE | B100/510 | FN 1341 PC STOP
FN1341_SSA_HMI | Kiln1 | FN 1-341 cooler fan 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1285 | FN 1-312 cooler fan 0=Auto 1=Man
FN1341FTS_ALM | Kiln1 | FN 1-341 FAILED TO START | On | PLC_ALARM | B101/254 | FN 1-341 FAILED TO START
FN1341MS_X | Kiln1 | FN 1-341 AUX FDBK | Off | PLC_DISCREAD | I:106/10 | FN 1-341 STOPPED
FN1605_AUTO | Kiln1 | FN 1-605 IN AUTO | None | PLC_DISCREAD | I:106/7 | FN 1-605 IN AUTO
FN1605_HZ | Kiln1 | FN 1-605 VFD HERTZ | Hz | 60 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:436 | FN 1-605 VFD HERTZ
FN1605_IM | Kiln1 | FN 1-605 INTERLOCKS MET | None | PLC_DISCREAD | B3/258 | FN 1-605 INTERLOCKS MET
FN1605_IT | Kiln1 | FN 1-605 AMPS | AMPS | 150 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:174 | FN 1-605 AMPS
FN1605_PBS | Kiln1 | FN 1-605 PC START | None | PLC_DISCWRITE | B100/452 | FN 1-605 PC START
FN1605_PBT | Kiln1 | FN 1-605 PC STOP | None | PLC_DISCWRITE | B100/442 | FN 1-605 PC STOP
FN1605_PCVFD% | Kiln1 | FN 1-605 PC VFD % SP | % | 100 | 0.05 | 0 | 0 | PLC_FLTWRITE | F71:12 | FN 1-605 PC VFD % SP
FN1605_SSA_HMI | Kiln1 | FN 1-605 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1295 | FN 1-605 0=Auto 1=Man
FN1605_TT | Kiln1 | FN 1-605 INLET TEMPERATURE | °F | 250 | 2 | 0 | 0 | PLC_INTREAD | N39:19 | FN 1-605 INLET TEMPERATURE
FN1605_VFDATSPD | Kiln1 | FN 1-605 VFD AT SPEED | None | PLC_DISCREAD | B3:46/10 | FN 1-605 VFD AT SPEED
FN1605_VFDCTRL | Kiln1 | FN 1-605 CONTROL VFD=1 A/F=0 | None | PLC_DISCWRITE | B3/748 | FN 1-605 CONTROL VFD=1 A/F=0
FN1605_VFDFLT | Kiln1 | FN 1-605 VFD FAULTED | On | PLC_ALARM | B101/146 | FN 1-605 VFD FAULTED
FN1605_VFDIM | Kiln1 | FN 1-605 VFD ENABLED | None | PLC_DISCREAD | O:116/4 | FN 1-605 VFD ENABLED
FN1605_VFDPBT | Kiln1 | FN 1-605 PC STOP VFD | None | PLC_DISCWRITE | B100:5/13 | FN 1-605 PC STOP VFD
FN1605_VFDRES | Kiln1 | FN 1-605 RESET VFD FAULT | None | PLC_DISCWRITE | B100/94 | FN 1-605 RESET VFD FAULT
FN1605FTS_ALM | Kiln1 | FN 1-605 FAILED TO START | On | PLC_ALARM | B101/259 | FN 1-605 FAILED TO START
FN1605HIAMP_ALM | Kiln1 | FN 1-605 HIGH AMP ALARM | On | PLC_ALARM | B101/472 | FN 1-605 HIGH AMP ALARM
FN1605MS_X | Kiln1 | FN 1-605 AUX FDBK | Off | PLC_DISCREAD | I:106/00 | FN 1-605 STOPPED
FN1605STATOR_ALM | Kiln1 | FN 1-605 HIGH MOTOR STATOR TEMP!! | Off | PLC_ALARM | I:105/10 | FN 1-605 HIGH MOTOR STATOR TEMP!!
FN1605VFD_COOLEN | Kiln1 | FN 1-605 PC Enable Cooldown | None | PLC_DISCWRITE | B100/531
FN1605VFD_COOLPER | Kiln1 | FN 1-605 Allow Cooldown Cycle Permissive | None | PLC_DISCREAD | B3/1200
FN1605VFD_PBS | Kiln1 | FN 1-605 PC VFD START | None | PLC_DISCWRITE | B100/92 | FN 1-605 PC VFD START
FN1605VFDMS_X | Kiln1 | FN 1-605 VFD RUNNING | Off | PLC_DISCREAD | O:116/5 | FN 1-605 VFD STOPPED!!
FN1614_IM | Kiln1 | FN 1-614 INTERLOCKS MET | None | USCNEL101 | NEL_KN1_FN1614.PLOCK | FN 1-614 INTERLOCKS MET
FN1614_PBE | Kiln1 | FN 1614 PC START | None | USCNEL101 | NEL_KN1_FN1614.PBE_HMI | FN 1614 PC START
FN1614_PBS | Kiln1 | FN 1614 PC STOP | None | USCNEL101 | NEL_KN1_FN1614.PBS_HMI | FN 1614 PC STOP
FN1614_SSA_HMI | Kiln1 | FN 1-614 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1290 | FN 1-614 0=Auto 1=Man
FN1614FTS_ALM | Kiln1 | FN 1-614 FAILED TO START | On | USCNEL101 | NEL_KN1_FN1314.FTS_ALM | FN 1-614 FAILED TO START
FN1614MS_X | Kiln1 | FN 1614 AUX FDBK | Off | USCNEL101 | NEL_KN1_FN1314.AUX | FN 1-614 STOPPED
FV1312_SP | Kiln1 | FV 1-312 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:10 | FV 1-312 PC SETPOINT
FV1312_ZT | Kiln1 | FV 1-312 COOLER FAN DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:148 | FV 1-312 COOLER FAN DAMPER POSITION
FV1312HIPID_SP | Kiln1 | FV 1-312 HI DAMPER PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N80:11 | FV 1-312 HI DAMPER PID SP
FV1312LOWPID_SP | Kiln1 | FV 1-312 LOW PID DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N80:12 | FV 1-312 LOW PID DAMPER SP
FV1312PID_%RUN | Kiln1 | KILN 1 HOOD DRAFT PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:283 | KILN 1 HOOD DRAFT PID % RUNTIME - TODAY
FV1312PID_%RUN_YEST | Kiln1 | KILN 1 HOOD DRAFT PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:333 | KILN 1 HOOD DRAFT PID % RUNTIME - PAST
FV1312PID_AVAIL | Kiln1 | KILN 1 HOOD DRAFT PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:282 | KILN 1 HOOD DRAFT PID AVAIL RUN HOURS - TODAY
FV1312PID_AVAIL_YEST | Kiln1 | KILN 1 HOOD DRAFT PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:332 | KILN 1 HOOD DRAFT PID AVAIL RUN HOURS - PAST
FV1331_AM | Kiln1 | FV 1-331 CONTROL AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100:4/11 | FV 1-331 CONTROL AUTO MANUAL 1=AUTO 0=MANUAL
FV1331_SP | Kiln1 | FV 1-331 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:21 | FV 1-331 PC SETPOINT
FV1331_SP2 | Kiln1 | FV 1-331 REAL # SETPOINT | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:242 | FV 1-331 REAL # SETPOINT
FV1331_ZT | Kiln1 | FV 1-331 VENT FAN DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:51 | FV 1-331 VENT FAN DAMPER POSITION
FV1331HIPID_SP | Kiln1 | FV 1-331 HI DAMPER PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:54 | FV 1-331 HI DAMPER PID SP
FV1331LOWPID_SP | Kiln1 | FV 1-331 LOW PID DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:53 | FV 1-331 LOW PID DAMPER SP
FV1331PID_%RUN | Kiln1 | KILN 1 VENT FAN CTRL % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:295 | KILN 1 VENT FAN CTRL % RUNTIME - TODAY
FV1331PID_%RUN_YEST | Kiln1 | KILN 1 VENT FAN CTRL % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:343 | KILN 1 VENT FAN CTRL % RUNTIME - PAST
FV1331PID_4HRALM | Kiln1 | K1 AUTO VENT FAN DAMPER HAS NOT RUN IN 4 HRS | On | PLC_ALARM | B101/139 | K1 AUTO VENT FAN DAMPER HAS NOT RUN IN 4 HRS
FV1331PID_4HRRES | Kiln1 | FV 1-331 CONTROL 4 HR W/ NO RUN RESET | None | PLC_DISCWRITE | B100/89 | FV 1-331 CONTROL 4 HR W/ NO RUN RESET
FV1331PID_AVAIL | Kiln1 | KILN 1 VENT FAN CTRL AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:294 | KILN 1 VENT FAN CTRL AVAIL RUN HOURS - TODAY
FV1331PID_AVAIL_YEST | Kiln1 | KILN 1 VENT FAN CTRL AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:342 | KILN 1 VENT FAN CTRL AVAIL RUN HOURS - PAST
FV1607A_OPEN95 | Kiln1 | FV 1-607-A OPEN 95% | None | PLC_DISCREAD | B3:46/2 | FV 1-607-A OPEN 95%
FV1607A_PBS | Kiln1 | FV 1-607-A OPEN | None | PLC_DISCWRITE | B100:6/0 | FV 1-607-A OPEN
FV1607A_PBT | Kiln1 | FV 1-607-A CLOSE | None | PLC_DISCWRITE | B100:6/1 | FV 1-607-A CLOSE
FV1607A_SP | Kiln1 | FV 1-607-A PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:9 | FV 1-607-A PC SETPOINT
FV1607A_ZT | Kiln1 | FV 1-607-A AIR/FUEL DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:149 | FV 1-607-A AIR/FUEL DAMPER POSITION
FV1607AOPEN95_ALM | Kiln1 | FV 1-607-A OPEN LESS THAN 95% | Off | PLC_ALARM | B3:46/2 | FV 1-607-A OPEN LESS THAN 95%
FV1607B_AM | Kiln1 | FV 1-607-B PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100/81 | FV 1-607-B PID AUTO MANUAL 1=AUTO 0=MANUAL
FV1607B_CV | Kiln1 | FV 1-607-B CONTROL VARIABLE = FV1607-B_SP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N86:24 | FV 1-607-B CONTROL VARIABLE = FV1607-B_SP
FV1607B_ER | Kiln1 | FV 1-607-B PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N86:15 | FV 1-607-B PID ERROR
FV1607B_MANSP | Kiln1 | FV 1-607-B PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:8 | FV 1-607-B PC SETPOINT
FV1607B_PIDSP | Kiln1 | FV 1-607-B PID SP - SP = BM OUTLET/INLET TEMP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N86:2 | FV 1-607-B PID SP - SP = BM OUTLET/INLET TEMP
FV1607B_PV | Kiln1 | FV 1-607-B PROCESS VARIABLE =TEMPERATURE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N86:23 | FV 1-607-B PROCESS VARIABLE =TEMPERATURE
FV1607B_SP | Kiln1 | FV 1-607-B ACTUAL SETPOINT AUTO OR MANUAL | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:253 | FV 1-607-B ACTUAL SETPOINT AUTO OR MANUAL
FV1607B_TB | Kiln1 | FV 1-607-B TIEBACK VARIABLE = FV1607-B_ZT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N86:25 | FV 1-607-B TIEBACK VARIABLE = FV1607-B_ZT
FV1607B_ZT | Kiln1 | FV 1-607-B BALL MILL TEMPERING DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:150 | FV 1-607-B BALL MILL TEMPERING DAMPER POSITION
FV1607BHIPID_SP | Kiln1 | FV 1-607-B HI DAMPER PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:56 | FV 1-607-B HI DAMPER PID SP
FV1607BLOWPID_SP | Kiln1 | FV 1-607-B LOW PID DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:55 | FV 1-607-B LOW PID DAMPER SP
FV1607BPID_DB | Kiln1 | FV 1-607-B PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N86:9 | FV 1-607-B PID DEADBAND
FV1607BPID_DR | Kiln1 | FV 1-607-B PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N86:5 | FV 1-607-B PID DR
FV1607BPID_PG | Kiln1 | FV 1-607-B PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N86:3 | FV 1-607-B PID PG
FV1607BPID_RT | Kiln1 | FV 1-607-B PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N86:4 | FV 1-607-B PID RT
FV1607BPID_UT | Kiln1 | FV 1-607-B PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | T4:288.PRE | FV 1-607-B PID UPDATE TIME
FV1607PID_%RUN | Kiln1 | KILN 1 BM TEMPERING TEE PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:293 | KILN 1 BM TEMPERING TEE PID % RUNTIME - TODAY
FV1607PID_%RUN_YEST | Kiln1 | KILN 1 BM TEMPERING TEE PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:341 | KILN 1 BM TEMPERING TEE PID % RUNTIME - PAST
FV1607PID_AVAIL | Kiln1 | KILN 1 BM TEMPERING TEE PID AVAIL RUN HOURS- TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:292 | KILN 1 BM TEMPERING TEE PID AVAIL RUN HOURS- TODAY
FV1607PID_AVAIL_YEST | Kiln1 | KILN 1 BM TEMPERING TEE PID AVAIL RUN HOURS- YEST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:340 | KILN 1 BM TEMPERING TEE PID AVAIL RUN HOURS- YEST
GB1313_ADVTM | Kiln1 | GB 1-313 MAN ADVANCE TIMER ENABLED | None | PLC_DISCREAD | T4:581.EN | GB 1-313 MAN ADVANCE TIMER ENABLED
GB1313_BWFTM | Kiln1 | GB 1-313 BACKWASH FINAL TIMER B4 OPENING GATE | 0.01 sec | 2000 | 1 | 0 | 0 | PLC_INTREAD | N102:89 | GB 1-313 BACKWASH FINAL TIMER B4 OPENING GATE
GB1313_BWPTM | Kiln1 | GB 1-313 BACKWASH PAUSE TIMER TO CLOSE GATE | sec | 20 | 1 | 0 | 0 | PLC_INTREAD | N102:87 | GB 1-313 BACKWASH PAUSE TIMER TO CLOSE GATE
GB1313_BWTM | Kiln1 | GB 1-313 TOTAL BACKWASH CYCLE TIME | sec | 1800 | 1 | 0 | 0 | PLC_INTREAD | N102:86 | GB 1-313 TOTAL BACKWASH CYCLE TIME
GB1313_MANADVANCE | Kiln1 | KILN 1 GRAVEL BED ADVANCE 1 MODULE | None | PLC_DISCWRITE | B100/475 | KILN 1 GRAVEL BED ADVANCE 1 MODULE
GB1313_RKTM | Kiln1 | GB 1-313 RAKE TOTAL RUN TIMER | sec | 600 | 1 | 0 | 0 | PLC_INTREAD | N102:88 | GB 1-313 RAKE TOTAL RUN TIMER
GB1313ADV_TM | Kiln1 | GB 1-313 TIME B4 MAN ADVANCE OCCURS | sec | 60 | 1 | 0 | 0 | PLC_INTREAD | T4:581.PRE | GB 1-313 TIME B4 MAN ADVANCE OCCURS
IV1211&1215_PBS | Kiln1 | IV 1-211 & 1-215 PC OPEN | None | PLC_DISCWRITE | B100/424 | IV 1-211 & 1-215 PC OPEN
IV1211&1215_PBT | Kiln1 | IV 1-211 & 1-215 PC CLOSE | None | PLC_DISCWRITE | B100/403 | IV 1-211 & 1-215 PC CLOSE
IV1211_CLOSED | Kiln1 | IV 1-211 CLOSED | None | PLC_DISCREAD | I:37/05 | IV 1-211 CLOSED
IV1211_OPEN | Kiln1 | IV 1-211 OPEN | Off | PLC_DISCREAD | I:37/11 | IV 1-211 CLOSED!
IV1215_CLOSED | Kiln1 | IV 1-215 CLOSED | None | PLC_DISCREAD | I:37/04 | IV 1-215 CLOSED
IV1215_OPEN | Kiln1 | IV 1-215 OPEN | Off | PLC_DISCREAD | I:37/10 | IV 1-215 CLOSED!
IV13131_CLOSED | Kiln1 | IV 1-313-1 CLOSED | None | PLC_DISCREAD | O:77/6 | IV 1-313-1 CLOSED
IV131310_CLOSED | Kiln1 | IV 1-313-10 CLOSED | None | PLC_DISCREAD | O:77/17 | IV 1-313-10 CLOSED
IV131310MAN_BF | Kiln1 | GB 1-313 MOD #10 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/514 | GB 1-313 MOD #10 MANUAL BACKFLUSH ACTIVE
IV13131MAN_BF | Kiln1 | GB 1-313 MOD #1 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/500 | GB 1-313 MOD #1 MANUAL BACKFLUSH ACTIVE
IV13132_CLOSED | Kiln1 | IV 1-313-2 CLOSED | None | PLC_DISCREAD | O:77/7 | IV 1-313-2 CLOSED
IV13132MAN_BF | Kiln1 | GB 1-313 MOD #2 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/501 | GB 1-313 MOD #2 MANUAL BACKFLUSH ACTIVE
IV13133_CLOSED | Kiln1 | IV 1-313-3 CLOSED | None | PLC_DISCREAD | O:77/10 | IV 1-313-3 CLOSED
IV13133MAN_BF | Kiln1 | GB 1-313 MOD #3 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/502 | GB 1-313 MOD #3 MANUAL BACKFLUSH ACTIVE
IV13134_CLOSED | Kiln1 | IV 1-313-4 CLOSED | None | PLC_DISCREAD | O:77/11 | IV 1-313-4 CLOSED
IV13134MAN_BF | Kiln1 | GB 1-313 MOD #4 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/503 | GB 1-313 MOD #4 MANUAL BACKFLUSH ACTIVE
IV13135_CLOSED | Kiln1 | IV 1-313-5 CLOSED | None | PLC_DISCREAD | O:77/12 | IV 1-313-5 CLOSED
IV13135MAN_BF | Kiln1 | GB 1-313 MOD #5 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/504 | GB 1-313 MOD #5 MANUAL BACKFLUSH ACTIVE
IV13136_CLOSED | Kiln1 | IV 1-313-6 CLOSED | None | PLC_DISCREAD | O:77/13 | IV 1-313-6 CLOSED
IV13136MAN_BF | Kiln1 | GB 1-313 MOD #6 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/505 | GB 1-313 MOD #6 MANUAL BACKFLUSH ACTIVE
IV13137_CLOSED | Kiln1 | IV 1-313-7 CLOSED | None | PLC_DISCREAD | O:77/14 | IV 1-313-7 CLOSED
IV13137MAN_BF | Kiln1 | GB 1-313 MOD #7 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/506 | GB 1-313 MOD #7 MANUAL BACKFLUSH ACTIVE
IV13138_CLOSED | Kiln1 | IV 1-313-8 CLOSED | None | PLC_DISCREAD | O:77/15 | IV 1-313-8 CLOSED
IV13138MAN_BF | Kiln1 | GB 1-313 MOD #8 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/507 | GB 1-313 MOD #8 MANUAL BACKFLUSH ACTIVE
IV13139_CLOSED | Kiln1 | IV 1-313-9 CLOSED | None | PLC_DISCREAD | O:77/16 | IV 1-313-9 CLOSED
IV13139MAN_BF | Kiln1 | GB 1-313 MOD #9 MANUAL BACKFLUSH ACTIVE | On | PLC_DISCWRITE | B100/508 | GB 1-313 MOD #9 MANUAL BACKFLUSH ACTIVE
IV1313MANBF_ACTIVE | Kiln1 | GB 1-313 MOD MANUAL BACKFLUSH ACTIVE | None | PLC_DISCREAD | B3/718 | GB 1-313 MOD MANUAL BACKFLUSH ACTIVE
K1_BLASTER_LOW_PRESSURE | Kiln1 | K1 Air Blaster Low Air Pressure Alarm | On | PLC_ALARM | B101/587 | K1 BLASTERS LOW AIR PRESSURE
K1_CANNON_FIRE_DELAY | Kiln1 | Kiln 1 Cannon Fire Delay Timer Preset | secs | 100 | 1 | 0 | 0 | PLC_INTREAD | N99:13 | PH 1-305 ACTIVE RAM #
K1_LIMECO2 | Kiln1 | KILN 1 LIME CO2 RUNNING VALUE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F69:0 | KILN 1 LIME CO2 RUNNING VALUE
K1_LIMECO2_1 | Kiln1 | KILN 1 LIME CO2 6 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:2 | KILN 1 LIME CO2 6 AM
K1_LIMECO2_1_YEST | Kiln1 | KILN 1 LIME CO2 6 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:702 | KILN 1 LIME CO2 6 AM
K1_LIMECO2_10 | Kiln1 | KILN 1 LIME CO2 10:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:11 | KILN 1 LIME CO2 10:30 AM
K1_LIMECO2_10_YEST | Kiln1 | KILN 1 LIME CO2 10:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:711 | KILN 1 LIME CO2 10:30 AM
K1_LIMECO2_11 | Kiln1 | KILN 1 LIME CO2 11:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:12 | KILN 1 LIME CO2 11:00 AM
K1_LIMECO2_11_YEST | Kiln1 | KILN 1 LIME CO2 11:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:712 | KILN 1 LIME CO2 11:00 AM
K1_LIMECO2_12 | Kiln1 | KILN 1 LIME CO2 11:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:13 | KILN 1 LIME CO2 11:30 AM
K1_LIMECO2_12_YEST | Kiln1 | KILN 1 LIME CO2 11:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:713 | KILN 1 LIME CO2 11:30 AM
K1_LIMECO2_13 | Kiln1 | KILN 1 LIME CO2 12:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:14 | KILN 1 LIME CO2 12:00 PM
K1_LIMECO2_13_YEST | Kiln1 | KILN 1 LIME CO2 12:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:714 | KILN 1 LIME CO2 12:00 PM
K1_LIMECO2_14 | Kiln1 | KILN 1 LIME CO2 12:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:15 | KILN 1 LIME CO2 12:30 PM
K1_LIMECO2_14_YEST | Kiln1 | KILN 1 LIME CO2 12:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:715 | KILN 1 LIME CO2 12:30 PM
K1_LIMECO2_15 | Kiln1 | KILN 1 LIME CO2 1:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:16 | KILN 1 LIME CO2 1:00 PM
K1_LIMECO2_15_YEST | Kiln1 | KILN 1 LIME CO2 1:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:716 | KILN 1 LIME CO2 1:00 PM
K1_LIMECO2_16 | Kiln1 | KILN 1 LIME CO2 1:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:17 | KILN 1 LIME CO2 1:30 PM
K1_LIMECO2_16_YEST | Kiln1 | KILN 1 LIME CO2 1:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:717 | KILN 1 LIME CO2 1:30 PM
K1_LIMECO2_17 | Kiln1 | KILN 1 LIME CO2 2:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:18 | KILN 1 LIME CO2 2:00 PM
K1_LIMECO2_17_YEST | Kiln1 | KILN 1 LIME CO2 2:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:718 | KILN 1 LIME CO2 2:00 PM
K1_LIMECO2_18 | Kiln1 | KILN 1 LIME CO2 2:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:19 | KILN 1 LIME CO2 2:30 PM
K1_LIMECO2_18_YEST | Kiln1 | KILN 1 LIME CO2 2:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:719 | KILN 1 LIME CO2 2:30 PM
K1_LIMECO2_19 | Kiln1 | KILN 1 LIME CO2 3:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:20 | KILN 1 LIME CO2 3:00 PM
K1_LIMECO2_19_YEST | Kiln1 | KILN 1 LIME CO2 3:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:720 | KILN 1 LIME CO2 3:00 PM
K1_LIMECO2_2 | Kiln1 | KILN 1 LIME CO2 6:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:3 | KILN 1 LIME CO2 6:30 AM
K1_LIMECO2_2_YEST | Kiln1 | KILN 1 LIME CO2 6:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:703 | KILN 1 LIME CO2 6:30 AM
K1_LIMECO2_20 | Kiln1 | KILN 1 LIME CO2 3:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:21 | KILN 1 LIME CO2 3:30 PM
K1_LIMECO2_20_YEST | Kiln1 | KILN 1 LIME CO2 3:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:721 | KILN 1 LIME CO2 3:30 PM
K1_LIMECO2_21 | Kiln1 | KILN 1 LIME CO2 4:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:22 | KILN 1 LIME CO2 4:00 PM
K1_LIMECO2_21_YEST | Kiln1 | KILN 1 LIME CO2 4:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:722 | KILN 1 LIME CO2 4:00 PM
K1_LIMECO2_22 | Kiln1 | KILN 1 LIME CO2 4:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:23 | KILN 1 LIME CO2 4:30 PM
K1_LIMECO2_22_YEST | Kiln1 | KILN 1 LIME CO2 4:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:723 | KILN 1 LIME CO2 4:30 PM
K1_LIMECO2_23 | Kiln1 | KILN 1 LIME CO2 5:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:24 | KILN 1 LIME CO2 5:00 PM
K1_LIMECO2_23_YEST | Kiln1 | KILN 1 LIME CO2 5:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:724 | KILN 1 LIME CO2 5:00 PM
K1_LIMECO2_24 | Kiln1 | KILN 1 LIME CO2 5:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:25 | KILN 1 LIME CO2 5:30 PM
K1_LIMECO2_24_YEST | Kiln1 | KILN 1 LIME CO2 5:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:725 | KILN 1 LIME CO2 5:30 PM
K1_LIMECO2_25 | Kiln1 | KILN 1 LIME CO2 6:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:26 | KILN 1 LIME CO2 6:00 PM
K1_LIMECO2_25_YEST | Kiln1 | KILN 1 LIME CO2 6:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:726 | KILN 1 LIME CO2 6:00 PM
K1_LIMECO2_26 | Kiln1 | KILN 1 LIME CO2 6:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:27 | KILN 1 LIME CO2 6:30 PM
K1_LIMECO2_26_YEST | Kiln1 | KILN 1 LIME CO2 6:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:727 | KILN 1 LIME CO2 6:30 PM
K1_LIMECO2_27 | Kiln1 | KILN 1 LIME CO2 7:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:28 | KILN 1 LIME CO2 7:00 PM
K1_LIMECO2_27_YEST | Kiln1 | KILN 1 LIME CO2 7:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:728 | KILN 1 LIME CO2 7:00 PM
K1_LIMECO2_28 | Kiln1 | KILN 1 LIME CO2 7:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:29 | KILN 1 LIME CO2 7:30 PM
K1_LIMECO2_28_YEST | Kiln1 | KILN 1 LIME CO2 7:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:729 | KILN 1 LIME CO2 7:30 PM
K1_LIMECO2_29 | Kiln1 | KILN 1 LIME CO2 8:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:30 | KILN 1 LIME CO2 8:00 PM
K1_LIMECO2_29_YEST | Kiln1 | KILN 1 LIME CO2 8:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:730 | KILN 1 LIME CO2 8:00 PM
K1_LIMECO2_3 | Kiln1 | KILN 1 LIME CO2 7:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:4 | KILN 1 LIME CO2 7:00 AM
K1_LIMECO2_3_YEST | Kiln1 | KILN 1 LIME CO2 7:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:704 | KILN 1 LIME CO2 7:00 AM
K1_LIMECO2_30 | Kiln1 | KILN 1 LIME CO2 8:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:31 | KILN 1 LIME CO2 8:30 PM
K1_LIMECO2_30_YEST | Kiln1 | KILN 1 LIME CO2 8:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:731 | KILN 1 LIME CO2 8:30 PM
K1_LIMECO2_31 | Kiln1 | KILN 1 LIME CO2 9:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:32 | KILN 1 LIME CO2 9:00 PM
K1_LIMECO2_31_YEST | Kiln1 | KILN 1 LIME CO2 9:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:732 | KILN 1 LIME CO2 9:00 PM
K1_LIMECO2_32 | Kiln1 | KILN 1 LIME CO2 9:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:33 | KILN 1 LIME CO2 9:30 PM
K1_LIMECO2_32_YEST | Kiln1 | KILN 1 LIME CO2 9:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:733 | KILN 1 LIME CO2 9:30 PM
K1_LIMECO2_33 | Kiln1 | KILN 1 LIME CO2 10:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:34 | KILN 1 LIME CO2 10:00 PM
K1_LIMECO2_33_YEST | Kiln1 | KILN 1 LIME CO2 10:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9;734 | KILN 1 LIME CO2 10:00 PM
K1_LIMECO2_34 | Kiln1 | KILN 1 LIME CO2 10:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:35 | KILN 1 LIME CO2 10:30 PM
K1_LIMECO2_34_YEST | Kiln1 | KILN 1 LIME CO2 10:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:735 | KILN 1 LIME CO2 10:30 PM
K1_LIMECO2_35 | Kiln1 | KILN 1 LIME CO2 11:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:36 | KILN 1 LIME CO2 11:00 PM
K1_LIMECO2_35_YEST | Kiln1 | KILN 1 LIME CO2 11:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:736 | KILN 1 LIME CO2 11:00 PM
K1_LIMECO2_36 | Kiln1 | KILN 1 LIME CO2 11:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:37 | KILN 1 LIME CO2 11:30 PM
K1_LIMECO2_36_YEST | Kiln1 | KILN 1 LIME CO2 11:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:737 | KILN 1 LIME CO2 11:30 PM
K1_LIMECO2_37 | Kiln1 | KILN 1 LIME CO2 12:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:38 | KILN 1 LIME CO2 12:00 AM
K1_LIMECO2_37_YEST | Kiln1 | KILN 1 LIME CO2 12:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:738 | KILN 1 LIME CO2 12:00 AM
K1_LIMECO2_38 | Kiln1 | KILN 1 LIME CO2 12:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:39 | KILN 1 LIME CO2 12:30 AM
K1_LIMECO2_38_YEST | Kiln1 | KILN 1 LIME CO2 12:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:739 | KILN 1 LIME CO2 12:30 AM
K1_LIMECO2_39 | Kiln1 | KILN 1 LIME CO2 1:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:40 | KILN 1 LIME CO2 1:00 AM
K1_LIMECO2_39_YEST | Kiln1 | KILN 1 LIME CO2 1:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:740 | KILN 1 LIME CO2 1:00 AM
K1_LIMECO2_4 | Kiln1 | KILN 1 LIME CO2 7:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:5 | KILN 1 LIME CO2 7:30 AM
K1_LIMECO2_4_YEST | Kiln1 | KILN 1 LIME CO2 7:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:705 | KILN 1 LIME CO2 7:30 AM
K1_LIMECO2_40 | Kiln1 | KILN 1 LIME CO2 1:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:41 | KILN 1 LIME CO2 1:30 AM
K1_LIMECO2_40_YEST | Kiln1 | KILN 1 LIME CO2 1:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:741 | KILN 1 LIME CO2 1:30 AM
K1_LIMECO2_41 | Kiln1 | KILN 1 LIME CO2 2:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:42 | KILN 1 LIME CO2 2:00 AM
K1_LIMECO2_41_YEST | Kiln1 | KILN 1 LIME CO2 2:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:742 | KILN 1 LIME CO2 2:00 AM
K1_LIMECO2_42 | Kiln1 | KILN 1 LIME CO2 2:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:43 | KILN 1 LIME CO2 2:30 AM
K1_LIMECO2_42_YEST | Kiln1 | KILN 1 LIME CO2 2:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:743 | KILN 1 LIME CO2 2:30 AM
K1_LIMECO2_43 | Kiln1 | KILN 1 LIME CO2 3:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:44 | KILN 1 LIME CO2 3:00 AM
K1_LIMECO2_43_YEST | Kiln1 | KILN 1 LIME CO2 3:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:744 | KILN 1 LIME CO2 3:00 AM
K1_LIMECO2_44 | Kiln1 | KILN 1 LIME CO2 3:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:45 | KILN 1 LIME CO2 3:30 AM
K1_LIMECO2_44_YEST | Kiln1 | KILN 1 LIME CO2 3:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:745 | KILN 1 LIME CO2 3:30 AM
K1_LIMECO2_45 | Kiln1 | KILN 1 LIME CO2 4:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:46 | KILN 1 LIME CO2 4:00 AM
K1_LIMECO2_45_YEST | Kiln1 | KILN 1 LIME CO2 4:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:746 | KILN 1 LIME CO2 4:00 AM
K1_LIMECO2_46 | Kiln1 | KILN 1 LIME CO2 4:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:47 | KILN 1 LIME CO2 4:30 AM
K1_LIMECO2_46_YEST | Kiln1 | KILN 1 LIME CO2 4:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:747 | KILN 1 LIME CO2 4:30 AM
K1_LIMECO2_47 | Kiln1 | KILN 1 LIME CO2 5:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:48 | KILN 1 LIME CO2 5:00 AM
K1_LIMECO2_47_YEST | Kiln1 | KILN 1 LIME CO2 5:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:748 | KILN 1 LIME CO2 5:00 AM
K1_LIMECO2_48 | Kiln1 | KILN 1 LIME CO2 5:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:49 | KILN 1 LIME CO2 5:30 AM
K1_LIMECO2_48_YEST | Kiln1 | KILN 1 LIME CO2 5:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:749 | KILN 1 LIME CO2 5:30 AM
K1_LIMECO2_5 | Kiln1 | KILN 1 LIME CO2 8:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:6 | KILN 1 LIME CO2 8:00 AM
K1_LIMECO2_5_YEST | Kiln1 | KILN 1 LIME CO2 8:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:706 | KILN 1 LIME CO2 8:00 AM
K1_LIMECO2_6 | Kiln1 | KILN 1 LIME CO2 8:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:7 | KILN 1 LIME CO2 8:30 AM
K1_LIMECO2_6_YEST | Kiln1 | KILN 1 LIME CO2 8:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:707 | KILN 1 LIME CO2 8:30 AM
K1_LIMECO2_7 | Kiln1 | KILN 1 LIME CO2 9:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:8 | KILN 1 LIME CO2 9:00 AM
K1_LIMECO2_7_YEST | Kiln1 | KILN 1 LIME CO2 9:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:708 | KILN 1 LIME CO2 9:00 AM
K1_LIMECO2_8 | Kiln1 | KILN 1 LIME CO2 9:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:9 | KILN 1 LIME CO2 9:30 AM
K1_LIMECO2_8_YEST | Kiln1 | KILN 1 LIME CO2 9:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:709 | KILN 1 LIME CO2 9:30 AM
K1_LIMECO2_9 | Kiln1 | KILN 1 LIME CO2 10:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:10 | KILN 1 LIME CO2 10:00 AM
K1_LIMECO2_9_YEST | Kiln1 | KILN 1 LIME CO2 10:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:710 | KILN 1 LIME CO2 10:00 AM
K1_LIMECO2_DAVG | Kiln1 | KILN 1 LIME CO2 DAY SHIFT AVERAGE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:421 | KILN 1 LIME CO2 DAY SHIFT AVERAGE
K1_LIMECO2_DAVG_YEST | Kiln1 | KILN 1 LIME CO2 DAY SHIFT AVERAGE YESTERDAY | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:840
K1_LIMECO2_GAVG | Kiln1 | KILN 1 LIME CO2 GRAVE SHIFT AVERAGE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:422 | KILN 1 LIME CO2 GRAVE SHIFT AVERAGE
K1_LIMECO2_GAVG_YEST | Kiln1 | KILN 1 LIME CO2 GRAVE SHIFT AVERAGE YESTERDAY | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:841
K1_LIMECO2_LIMIT | Kiln1 | KILN 1 LIME CO2 0.5 HR SAMPLE LIMIT | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F69:1 | KILN 1 LIME CO2 0.5 HR SAMPLE LIMIT
K1_LIMECO2_TAVG | Kiln1 | KILN 1 LIME CO2 AVERAGE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:423 | KILN 1 LIME CO2 AVERAGE
K1_LIMECO2_TAVG_YEST | Kiln1 | KILN 1 LIME CO2 AVERAGE YESTERDAY | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:842
K1_LIMECO2_YEST | Kiln1 | KILN 1 LIME CO2 RUNNING VALUE YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:700 | KILN 1 LIME CO2 RUNNING VALUE
K1_LIMERES | Kiln1 | KILN 1 LIME RESIDUE - RUNNING VALUE | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:501 | KILN 1 LIME RESIDUE - RUNNING VALUE
K1_LIMERES_1 | Kiln1 | KILN 1 LIME RESIDUE - 6AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:502 | KILN 1 LIME RESIDUE - 6AM
K1_LIMERES_1_YEST | Kiln1 | KILN 1 LIME RESIDUE - 6AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:602 | KILN 1 LIME RESIDUE - 6AM
K1_LIMERES_10 | Kiln1 | KILN 1 LIME RESIDUE - 10.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:511 | KILN 1 LIME RESIDUE - 10.5AM
K1_LIMERES_10_YEST | Kiln1 | KILN 1 LIME RESIDUE - 10.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:611 | KILN 1 LIME RESIDUE - 10.5AM
K1_LIMERES_11 | Kiln1 | KILN 1 LIME RESIDUE - 11AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:512 | KILN 1 LIME RESIDUE - 11AM
K1_LIMERES_11_YEST | Kiln1 | KILN 1 LIME RESIDUE - 11AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:612 | KILN 1 LIME RESIDUE - 11AM
K1_LIMERES_12 | Kiln1 | KILN 1 LIME RESIDUE - 11.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:513 | KILN 1 LIME RESIDUE - 11.5AM
K1_LIMERES_12_YEST | Kiln1 | KILN 1 LIME RESIDUE - 11.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:613 | KILN 1 LIME RESIDUE - 11.5AM
K1_LIMERES_13 | Kiln1 | KILN 1 LIME RESIDUE - 12PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:514 | KILN 1 LIME RESIDUE - 12PM
K1_LIMERES_13_YEST | Kiln1 | KILN 1 LIME RESIDUE - 12PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:614 | KILN 1 LIME RESIDUE - 12PM
K1_LIMERES_14 | Kiln1 | KILN 1 LIME RESIDUE - 12.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:515 | KILN 1 LIME RESIDUE - 12.5PM
K1_LIMERES_14_YEST | Kiln1 | KILN 1 LIME RESIDUE - 12.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:615 | KILN 1 LIME RESIDUE - 12.5PM
K1_LIMERES_15 | Kiln1 | KILN 1 LIME RESIDUE - 1PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:516 | KILN 1 LIME RESIDUE - 1PM
K1_LIMERES_15_YEST | Kiln1 | KILN 1 LIME RESIDUE - 1PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:616 | KILN 1 LIME RESIDUE - 1PM
K1_LIMERES_16 | Kiln1 | KILN 1 LIME RESIDUE - 1.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:517 | KILN 1 LIME RESIDUE - 1.5PM
K1_LIMERES_16_YEST | Kiln1 | KILN 1 LIME RESIDUE - 1.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:617 | KILN 1 LIME RESIDUE - 1.5PM
K1_LIMERES_17 | Kiln1 | KILN 1 LIME RESIDUE - 2PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:518 | KILN 1 LIME RESIDUE - 2PM
K1_LIMERES_17_YEST | Kiln1 | KILN 1 LIME RESIDUE - 2PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:618 | KILN 1 LIME RESIDUE - 2PM
K1_LIMERES_18 | Kiln1 | KILN 1 LIME RESIDUE - 2.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:519 | KILN 1 LIME RESIDUE - 2.5PM
K1_LIMERES_18_YEST | Kiln1 | KILN 1 LIME RESIDUE - 2.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:619 | KILN 1 LIME RESIDUE - 2.5PM
K1_LIMERES_19 | Kiln1 | KILN 1 LIME RESIDUE - 3PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:520 | KILN 1 LIME RESIDUE - 3PM
K1_LIMERES_19_YEST | Kiln1 | KILN 1 LIME RESIDUE - 3PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:620 | KILN 1 LIME RESIDUE - 3PM
K1_LIMERES_2 | Kiln1 | KILN 1 LIME RESIDUE - 6.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:503 | KILN 1 LIME RESIDUE - 6.5AM
K1_LIMERES_2_YEST | Kiln1 | KILN 1 LIME RESIDUE - 6.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:603 | KILN 1 LIME RESIDUE - 6.5AM
K1_LIMERES_20 | Kiln1 | KILN 1 LIME RESIDUE - 3.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:521 | KILN 1 LIME RESIDUE - 3.5PM
K1_LIMERES_20_YEST | Kiln1 | KILN 1 LIME RESIDUE - 3.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:621 | KILN 1 LIME RESIDUE - 3.5PM
K1_LIMERES_21 | Kiln1 | KILN 1 LIME RESIDUE - 4PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:522 | KILN 1 LIME RESIDUE - 4PM
K1_LIMERES_21_YEST | Kiln1 | KILN 1 LIME RESIDUE - 4PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:622 | KILN 1 LIME RESIDUE - 4PM
K1_LIMERES_22 | Kiln1 | KILN 1 LIME RESIDUE - 4.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:523 | KILN 1 LIME RESIDUE - 4.5PM
K1_LIMERES_22_YEST | Kiln1 | KILN 1 LIME RESIDUE - 4.5PM YEST | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:623 | KILN 1 LIME RESIDUE - 4.5PM
K1_LIMERES_23 | Kiln1 | KILN 1 LIME RESIDUE - 5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:524 | KILN 1 LIME RESIDUE - 5PM
K1_LIMERES_23_YEST | Kiln1 | KILN 1 LIME RESIDUE - 5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:624 | KILN 1 LIME RESIDUE - 5PM
K1_LIMERES_24 | Kiln1 | KILN 1 LIME RESIDUE - 5.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:525 | KILN 1 LIME RESIDUE - 5.5PM
K1_LIMERES_24_YEST | Kiln1 | KILN 1 LIME RESIDUE - 5.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:625 | KILN 1 LIME RESIDUE - 5.5PM
K1_LIMERES_25 | Kiln1 | KILN 1 LIME RESIDUE - 6PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:526 | KILN 1 LIME RESIDUE - 6PM
K1_LIMERES_25_YEST | Kiln1 | KILN 1 LIME RESIDUE - 6PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:626 | KILN 1 LIME RESIDUE - 6PM
K1_LIMERES_26 | Kiln1 | KILN 1 LIME RESIDUE - 6.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:527 | KILN 1 LIME RESIDUE - 6.5PM
K1_LIMERES_26_YEST | Kiln1 | KILN 1 LIME RESIDUE - 6.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:627 | KILN 1 LIME RESIDUE - 6.5PM
K1_LIMERES_27 | Kiln1 | KILN 1 LIME RESIDUE - 7PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:528 | KILN 1 LIME RESIDUE - 7PM
K1_LIMERES_27_YEST | Kiln1 | KILN 1 LIME RESIDUE - 7PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:628 | KILN 1 LIME RESIDUE - 7PM
K1_LIMERES_28 | Kiln1 | KILN 1 LIME RESIDUE - 7.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:529 | KILN 1 LIME RESIDUE - 7.5PM
K1_LIMERES_28_YEST | Kiln1 | KILN 1 LIME RESIDUE - 7.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:629 | KILN 1 LIME RESIDUE - 7.5PM
K1_LIMERES_29 | Kiln1 | KILN 1 LIME RESIDUE - 8PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:530 | KILN 1 LIME RESIDUE - 8PM
K1_LIMERES_29_YEST | Kiln1 | KILN 1 LIME RESIDUE - 8PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:630 | KILN 1 LIME RESIDUE - 8PM
K1_LIMERES_3 | Kiln1 | KILN 1 LIME RESIDUE - 7AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:504 | KILN 1 LIME RESIDUE - 7AM
K1_LIMERES_3_YEST | Kiln1 | KILN 1 LIME RESIDUE - 7AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:604 | KILN 1 LIME RESIDUE - 7AM
K1_LIMERES_30 | Kiln1 | KILN 1 LIME RESIDUE - 8.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:531 | KILN 1 LIME RESIDUE - 8.5PM
K1_LIMERES_30_YEST | Kiln1 | KILN 1 LIME RESIDUE - 8.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:631 | KILN 1 LIME RESIDUE - 8.5PM
K1_LIMERES_31 | Kiln1 | KILN 1 LIME RESIDUE - 9PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:532 | KILN 1 LIME RESIDUE - 9PM
K1_LIMERES_31_YEST | Kiln1 | KILN 1 LIME RESIDUE - 9PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:632 | KILN 1 LIME RESIDUE - 9PM
K1_LIMERES_32 | Kiln1 | KILN 1 LIME RESIDUE - 9.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:533 | KILN 1 LIME RESIDUE - 9.5PM
K1_LIMERES_32_YEST | Kiln1 | KILN 1 LIME RESIDUE - 9.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:633 | KILN 1 LIME RESIDUE - 9.5PM
K1_LIMERES_33 | Kiln1 | KILN 1 LIME RESIDUE - 10PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:534 | KILN 1 LIME RESIDUE - 10PM
K1_LIMERES_33_YEST | Kiln1 | KILN 1 LIME RESIDUE - 10PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:634 | KILN 1 LIME RESIDUE - 10PM
K1_LIMERES_34 | Kiln1 | KILN 1 LIME RESIDUE - 10.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:535 | KILN 1 LIME RESIDUE - 10.5PM
K1_LIMERES_34_YEST | Kiln1 | KILN 1 LIME RESIDUE - 10.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:635 | KILN 1 LIME RESIDUE - 10.5PM
K1_LIMERES_35 | Kiln1 | KILN 1 LIME RESIDUE - 11PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:536 | KILN 1 LIME RESIDUE - 11PM
K1_LIMERES_35_YEST | Kiln1 | KILN 1 LIME RESIDUE - 11PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:636 | KILN 1 LIME RESIDUE - 11PM
K1_LIMERES_36 | Kiln1 | KILN 1 LIME RESIDUE - 11.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:537 | KILN 1 LIME RESIDUE - 11.5PM
K1_LIMERES_36_YEST | Kiln1 | KILN 1 LIME RESIDUE - 11.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:637 | KILN 1 LIME RESIDUE - 11.5PM
K1_LIMERES_37 | Kiln1 | KILN 1 LIME RESIDUE - 12AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:538 | KILN 1 LIME RESIDUE - 12AM
K1_LIMERES_37_YEST | Kiln1 | KILN 1 LIME RESIDUE - 12AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:638 | KILN 1 LIME RESIDUE - 12AM
K1_LIMERES_38 | Kiln1 | KILN 1 LIME RESIDUE - 12.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:539 | KILN 1 LIME RESIDUE - 12.5AM
K1_LIMERES_38_YEST | Kiln1 | KILN 1 LIME RESIDUE - 12.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:639 | KILN 1 LIME RESIDUE - 12.5AM
K1_LIMERES_39 | Kiln1 | KILN 1 LIME RESIDUE - 1AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:540 | KILN 1 LIME RESIDUE - 1AM
K1_LIMERES_39_YEST | Kiln1 | KILN 1 LIME RESIDUE - 1AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:640 | KILN 1 LIME RESIDUE - 1AM
K1_LIMERES_4 | Kiln1 | KILN 1 LIME RESIDUE - 7.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:505 | KILN 1 LIME RESIDUE - 7.5AM
K1_LIMERES_4_YEST | Kiln1 | KILN 1 LIME RESIDUE - 7.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:605 | KILN 1 LIME RESIDUE - 7.5AM
K1_LIMERES_40 | Kiln1 | KILN 1 LIME RESIDUE - 1.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:541 | KILN 1 LIME RESIDUE - 1.5AM
K1_LIMERES_40_YEST | Kiln1 | KILN 1 LIME RESIDUE - 1.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:641 | KILN 1 LIME RESIDUE - 1.5AM
K1_LIMERES_41 | Kiln1 | KILN 1 LIME RESIDUE - 2AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:542 | KILN 1 LIME RESIDUE - 2AM
K1_LIMERES_41_YEST | Kiln1 | KILN 1 LIME RESIDUE - 2AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:642 | KILN 1 LIME RESIDUE - 2AM
K1_LIMERES_42 | Kiln1 | KILN 1 LIME RESIDUE - 2.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:543 | KILN 1 LIME RESIDUE - 2.5AM
K1_LIMERES_42_YEST | Kiln1 | KILN 1 LIME RESIDUE - 2.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:643 | KILN 1 LIME RESIDUE - 2.5AM
K1_LIMERES_43 | Kiln1 | KILN 1 LIME RESIDUE - 3AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:544 | KILN 1 LIME RESIDUE - 3AM
K1_LIMERES_43_YEST | Kiln1 | KILN 1 LIME RESIDUE - 3AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:644 | KILN 1 LIME RESIDUE - 3AM
K1_LIMERES_44 | Kiln1 | KILN 1 LIME RESIDUE - 3.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:545 | KILN 1 LIME RESIDUE - 3.5AM
K1_LIMERES_44_YEST | Kiln1 | KILN 1 LIME RESIDUE - 3.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:645 | KILN 1 LIME RESIDUE - 3.5AM
K1_LIMERES_45 | Kiln1 | KILN 1 LIME RESIDUE - 4AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:546 | KILN 1 LIME RESIDUE - 4AM
K1_LIMERES_45_YEST | Kiln1 | KILN 1 LIME RESIDUE - 4AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:646 | KILN 1 LIME RESIDUE - 4AM
K1_LIMERES_46 | Kiln1 | KILN 1 LIME RESIDUE - 4.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:547 | KILN 1 LIME RESIDUE - 4.5AM
K1_LIMERES_46_YEST | Kiln1 | KILN 1 LIME RESIDUE - 4.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:647 | KILN 1 LIME RESIDUE - 4.5AM
K1_LIMERES_47 | Kiln1 | KILN 1 LIME RESIDUE - 5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:548 | KILN 1 LIME RESIDUE - 5AM
K1_LIMERES_47_YEST | Kiln1 | KILN 1 LIME RESIDUE - 5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:648 | KILN 1 LIME RESIDUE - 5AM
K1_LIMERES_48 | Kiln1 | KILN 1 LIME RESIDUE - 5.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:549 | KILN 1 LIME RESIDUE - 5.5AM
K1_LIMERES_48_YEST | Kiln1 | KILN 1 LIME RESIDUE - 5.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:649 | KILN 1 LIME RESIDUE - 5.5AM
K1_LIMERES_5 | Kiln1 | KILN 1 LIME RESIDUE - 8AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:506 | KILN 1 LIME RESIDUE - 8AM
K1_LIMERES_5_YEST | Kiln1 | KILN 1 LIME RESIDUE - 8AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:606 | KILN 1 LIME RESIDUE - 8AM
K1_LIMERES_6 | Kiln1 | KILN 1 LIME RESIDUE - 8.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:507 | KILN 1 LIME RESIDUE - 8.5AM
K1_LIMERES_6_YEST | Kiln1 | KILN 1 LIME RESIDUE - 8.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:607 | KILN 1 LIME RESIDUE - 8.5AM
K1_LIMERES_7 | Kiln1 | KILN 1 LIME RESIDUE - 9AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:508 | KILN 1 LIME RESIDUE - 9AM
K1_LIMERES_7_YEST | Kiln1 | KILN 1 LIME RESIDUE - 9AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:608 | KILN 1 LIME RESIDUE - 9AM
K1_LIMERES_8 | Kiln1 | KILN 1 LIME RESIDUE - 9.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:509 | KILN 1 LIME RESIDUE - 9.5AM
K1_LIMERES_8_YEST | Kiln1 | KILN 1 LIME RESIDUE - 9.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:609 | KILN 1 LIME RESIDUE - 9.5AM
K1_LIMERES_9 | Kiln1 | KILN 1 LIME RESIDUE - 10AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:510 | KILN 1 LIME RESIDUE - 10AM
K1_LIMERES_9_YEST | Kiln1 | KILN 1 LIME RESIDUE - 10AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:610 | KILN 1 LIME RESIDUE - 10AM
K1_LIMERES_YEST | Kiln1 | KILN 1 LIME RESIDUE - RUNNING VALUE YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:601 | KILN 1 LIME RESIDUE - RUNNING VALUE
K1_RES_LIMIT | Kiln1 | KILN 1 LIME RESIDUE 0.5 HR SAMPLE LIMIT | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:500 | KILN 1 LIME RESIDUE 0.5 HR SAMPLE LIMIT
K1_SPCCO2_ANS | Kiln1 | Answer Kiln 1 Leco CO2 SPC Alarm | None | 0
K1_SPCKE_ANS | Kiln1 | Answer Kiln1 Kiln Exit Temp SPC Alarm | None | 0
K1_SPCO2_ANS | Kiln1 | Answer Kiln O2 SPC Alarm | None | 0
K1_TEMP_DEV | Kiln1 | Kiln 1 Exit/Inlet Temperature Deviation Actual | deg F | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F71:25 | KILN 1 PERCENT CARBON MONOXIDE
K1_TEMP_DEV_SP | Kiln1 | Kiln 1 Exit/Inlet Temperature Deviation Setpoint | deg F | 2000 | 0 | 0 | 0 | PLC_FLTREAD | F71:24 | KILN 1 PERCENT CARBON MONOXIDE
K1BLAST_AM | Kiln1 | KILN 1 AIR BLASTERS AUTO MANUAL | None | PLC_DISCWRITE | B100/616
K1BLAST_INT | Kiln1 | K1 AIR CANNON SEQUENCE INTERVAL |  | 28800 | 0 | 0 | 1800 | PLC_INTWRITE | T4:751.PRE
K1BLAST_INTCTN | Kiln1 | K1 AIR CANNON SEQUENCE INTERVAL TIME |  | 32000 | 0 | 0 | 0 | PLC_INTREAD | n7:164
K1BLAST_NUM | Kiln1 | K1 AIR CANNON SEQUENCE NEXT CANNON |  | 100 | 0 | 0 | 0 | PLC_INTREAD | N7:163
K1BLAST_SEQCTN | Kiln1 | K1 AIR CANNON SEQUENCE TIME |  | 10000 | 0 | 0 | 0 | PLC_INTREAD | N73:1
K1BLAST1_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 1 PC BYPASS | None | PLC_DISCREAD | B100/721
K1BLAST1_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 1 PC START | None | PLC_DISCWRITE | B100/711
K1BLAST1_X | Kiln1 | KILN 1 AIR BLASTER CANNON 1 FDBK | None | PLC_DISCREAD | O:026/0
K1BLAST10_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 10 PC BYPASS | None | PLC_DISCREAD | B100/730
K1BLAST10_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 10 PC START | None | PLC_DISCWRITE | B100/720
K1BLAST10_X | Kiln1 | KILN 1 AIR BLASTER CANNON 10 FDBK | None | PLC_DISCREAD | O:026/11
K1BLAST2_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 2 PC BYPASS | None | PLC_DISCREAD | B100/722
K1BLAST2_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 2 PC START | None | PLC_DISCWRITE | B100/712
K1BLAST2_X | Kiln1 | KILN 1 AIR BLASTER CANNON 2 FDBK | None | PLC_DISCREAD | O:026/1
K1BLAST3_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 3 PC BYPASS | None | PLC_DISCREAD | B100/723
K1BLAST3_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 3 PC START | None | PLC_DISCWRITE | B100/713
K1BLAST3_X | Kiln1 | KILN 1 AIR BLASTER CANNON 3 FDBK | None | PLC_DISCREAD | O:026/2
K1BLAST4_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 4 PC BYPASS | None | PLC_DISCREAD | B100/724
K1BLAST4_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 4 PC START | None | PLC_DISCWRITE | B100/714
K1BLAST4_X | Kiln1 | KILN 1 AIR BLASTER CANNON 4 FDBK | None | PLC_DISCREAD | O:026/3
K1BLAST5_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 5 PC BYPASS | None | PLC_DISCREAD | B100/725
K1BLAST5_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 5 PC START | None | PLC_DISCWRITE | B100/715
K1BLAST5_X | Kiln1 | KILN 1 AIR BLASTER CANNON 5 FDBK | None | PLC_DISCREAD | O:026/4
K1BLAST6_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 6 PC BYPASS | None | PLC_DISCREAD | B100/726
K1BLAST6_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 6 PC START | None | PLC_DISCWRITE | B100/716
K1BLAST6_X | Kiln1 | KILN 1 AIR BLASTER CANNON 6 FDBK | None | PLC_DISCREAD | O:026/5
K1BLAST7_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 7 PC BYPASS | None | PLC_DISCREAD | B100/727
K1BLAST7_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 7 PC START | None | PLC_DISCWRITE | B100/717
K1BLAST7_X | Kiln1 | KILN 1 AIR BLASTER CANNON 7 FDBK | None | PLC_DISCREAD | O:026/6
K1BLAST8_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 8 PC BYPASS | None | PLC_DISCREAD | B100/728
K1BLAST8_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 8 PC START | None | PLC_DISCWRITE | B100/718
K1BLAST8_X | Kiln1 | KILN 1 AIR BLASTER CANNON 8 FDBK | None | PLC_DISCREAD | O:026/7
K1BLAST9_BYP | Kiln1 | KILN 1 AIR BLASTER CANNON 9 PC BYPASS | None | PLC_DISCREAD | B100/729
K1BLAST9_PCS | Kiln1 | KILN 1 AIR BLASTER CANNON 9 PC START | None | PLC_DISCWRITE | B100/719
K1BLAST9_X | Kiln1 | KILN 1 AIR BLASTER CANNON 9 FDBK | None | PLC_DISCREAD | O:026/10
K1BLASTXFERM_PCS | Kiln1 | KILN 1 AIR BLASTER XFER CHUTE MID PC START | None | PLC_DISCWRITE | B100/833
K1BLASTXFERM_X | Kiln1 | KILN 1 AIR BLASTER XFER CHUTE MID FDBK | None | PLC_DISCWRITE | O:026/13
K1BLASTXFERN_PCS | Kiln1 | KILN 1 AIR BLASTER XFER CHUTE NORTH PC START | None | PLC_DISCWRITE | B100/834
K1BLASTXFERN_X | Kiln1 | KILN 1 AIR BLASTER XFER CHUTE NORTH FDBK | None | PLC_DISCWRITE | O:026/14
K1BLASTXFERS_PCS | Kiln1 | KILN 1 AIR BLASTER XFER CHUTE SOUTH PC START | None | PLC_DISCWRITE | B100/832
K1BLASTXFERS_X | Kiln1 | KILN 1 AIR BLASTER XFER CHUTE SOUTH FDBK | None | PLC_DISCWRITE | O:026/12
K1CEMPID_CV | Kiln1 | KILN 1 CEM PID CV | ppm | 4095 | 5 | 0 | 0 | PLC_INTREAD | N85:24
K1CEMPID_DB | Kiln1 | KILN 1 CEM PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N85:9
K1CEMPID_DR | Kiln1 | KILN 1 CEM PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N85:5
K1CEMPID_ER | Kiln1 | KILN 1 CEM PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N85:15
K1CEMPID_PG | Kiln1 | KILN 1 CEM PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N85:3
K1CEMPID_PIDSP | Kiln1 | CEM PID SP - SP = K1CEM_PIDSP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N85:2
K1CEMPID_PV | Kiln1 | CEM PID PV 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N85:23
K1CEMPID_RT | Kiln1 | KILN 1 CEM PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N85:4
K1CEMPID_TB | Kiln1 | KILN 1 CEM PID TB 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N85:25
K1CEMPID_UT | Kiln1 | KILN 1 CEM PID UPDATE TIME | SEC | 10000 | 1 | 0 | 0 | PLC_INTREAD | T4:277.PRE
K1CO2CTRLSPC_ALM | Kiln1 | KILN 1 LECO CO2 SPC CONTROL VIOLATION | On | PLC_ALARM | B101/272 | KILN 1 LECO CO2 SPC CONTROL VIOLATION
K1CO2SPC_ACT | Kiln1 | KILN 1 ACTUAL LECO CO2 SPC VIOLATION | % LECO CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:403 | KILN 1 ACTUAL LECO CO2 SPC VIOLATION
K1CO2SPC_ACTION | Kiln1 | KILN 1 LECO CO2 SPC CORRECTIVE ACTION CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:102 | KILN 1 LECO CO2 SPC CORRECTIVE ACTION CODE
K1CO2SPC_REA | Kiln1 | KILN 1 LECO CO2 SPC REASON CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:101 | KILN 1 LECO CO2 SPC REASON CODE
K1CO2SPC_ULCL | Kiln1 | KILN 1 LECO CO2 SPC UCL/LCL VIOLATION | None | PLC_DISCREAD | B3/743 | KILN 1 LECO CO2 SPC UCL/LCL VIOLATION
K1CO2SPCDAY_ALM | Kiln1 | K1 LECO CO2 SPC VIOLATION DAY
K1CO2SPCHR_ALM | Kiln1 | K1 LECO CO2 SPC VIOLATION TIME
K1ETEMPCTRLSPC_ALM | Kiln1 | KILN 1 EXIT TEMP SPC CONTROL VIOLATION | On | PLC_ALARM | B101/242 | KILN 1 EXIT TEMP SPC CONTROL VIOLATION
K1ETEMPSPC_ACT | Kiln1 | KILN 1 ACTUAL EXIT TEMP SPC VIOLATION | F | 2516 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:402 | KILN 1 ACTUAL EXIT TEMP SPC VIOLATION
K1ETEMPSPC_ACTION | Kiln1 | KILN 1 EXIT TEMP SPC CORRECTIVE ACTION CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:100 | KILN 1 EXIT TEMP SPC CORRECTIVE ACTION CODE
K1ETEMPSPC_CL | Kiln1 | KILN 1 EXIT TEMP SPC CONTROL LIMIT | F | 2516 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:88
K1ETEMPSPC_REA | Kiln1 | KILN 1 EXIT TEMP SPC REASON CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:99 | KILN 1 EXIT TEMP SPC REASON CODE
K1ETEMPSPC_ULCL | Kiln1 | KILN 1 EXIT TEMP SPC UCL/LCL VIOLATION | None | PLC_DISCREAD | B3/741 | KILN 1 EXIT TEMP SPC UCL/LCL VIOLATION
K1ETEMPSPCDAY_ALM | Kiln1 | K1 EXIT TEMP SPC VIOLATION DAY
K1ETEMPSPCHR_ALM | Kiln1 | K1 EXIT TEMP SPC VIOLATION TIME
K1EXIT_AM | Kiln1 | KILN 1 EXIT TEMP PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100/476 | KILN 1 EXIT TEMP PID AUTO MANUAL 1=AUTO 0=MANUAL
K1EXIT_CV | Kiln1 | K1 EXIT TEMP PID CONTROL VARIABLE = WF1601_SP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N89:24 | K1 EXIT TEMP PID CONTROL VARIABLE = WF1601_SP
K1EXIT_ER | Kiln1 | KILN 1 EXIT TEMP PID PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | pd114:0.err | KILN 1 EXIT TEMP PID PID ERROR
K1EXIT_PCPIDSP | Kiln1 | K1 EXIT TEMP PID SP TO CONTROL WF 1-601 | °F | 2300 | 1 | 0 | 1700 | PLC_INTWRITE | N102:92 | K1 EXIT TEMP PID SP TO CONTROL WF 1-601
K1EXIT_PID_Valid | Kiln1 | Kiln 1 Exit Temp PID Validation Bit | None | PLC_DISCREAD | B100/477 | Kiln 1 Exit Temp PID Validation Bit0=MANUAL
K1EXIT_PIDACC | Kiln1 | KILN 1 EXIT TEMP PID UPDATE ACC |  | 32000 | 5 | 0 | 0 | PLC_FLTREAD | T4:585.ACC | KILN 1 EXIT TEMP PID PID ERROR
K1EXIT_PIDSP | Kiln1 | KILN 1 EXIT TEMP PID SP - SP = K1EXIT_PCPIDSP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N89:2 | KILN 1 EXIT TEMP PID SP - SP = K1EXIT_PCPIDSP
K1EXIT_PV | Kiln1 | K1 EXIT TEMP PID PROCESS VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N89:23 | K1 EXIT TEMP PID PROCESS VARIABLE
K1EXIT_TB | Kiln1 | K1 EXIT TEMP PID TIEBACK VARIABLE = WF1601_WT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N89:25 | K1 EXIT TEMP PID TIEBACK VARIABLE = WF1601_WT
K1EXITAUTO_SP | Kiln1 | KILN 1 EXIT TEMP PID SETPOINT AUTO SET | None | PLC_DISCWRITE | B100/550
K1EXITAUTOSP_NEW | Kiln1 | KILN 1 EXIT TEMP PID NEW SETPOINT RECOMMENDED | None | PLC_DISCWRITE | B100/551
K1EXITAUTOSP_OK | Kiln1 | KILN 1 EXIT TEMP PID NEW SETPOINT OK | None | PLC_DISCWRITE | B100/552
K1EXITHIPID_SP | Kiln1 | KILN 1 EXIT TEMP HI FEED RATE PID SP | TPH | 15 | 1 | 0 | 1 | PLC_INTWRITE | N102:91 | KILN 1 EXIT TEMP HI FEED RATE PID SP
K1EXITLOWPID_SP | Kiln1 | KILN 1 EXIT TEMP LOW FEED RATE PID SP | TPH | 14 | 1 | 0 | 0 | PLC_INTWRITE | N102:90 | KILN 1 EXIT TEMP LOW FEED RATE PID SP
K1EXITPID_%RUN | Kiln1 | KILN 1 EXIT TEMP PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:287 | KILN 1 EXIT TEMP PID % RUNTIME - TODAY
K1EXITPID_%RUN_YEST | Kiln1 | KILN 1 EXIT TEMP PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:337 | KILN 1 EXIT TEMP PID % RUNTIME - PAST
K1EXITPID_1HRRATE | Kiln1 | KILN 1 EXIT TEMP PID FUEL RATE CHANGE 1 HR |  | 10 | 0 | 0 | -10 | PLC_FLTREAD | f8:143
K1EXITPID_5MINRATE | Kiln1 | KILN 1 EXIT TEMP PID FUEL RATE CHANGE 5 MIN |  | 10 | 0 | 0 | -10 | PLC_FLTREAD | f8:142
K1EXITPID_AVAIL | Kiln1 | KILN 1 EXIT TEMP PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:286 | KILN 1 EXIT TEMP PID AVAIL RUN HOURS - TODAY
K1EXITPID_AVAIL_YEST | Kiln1 | KILN 1 EXIT TEMP PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:336 | KILN 1 EXIT TEMP PID AVAIL RUN HOURS - PAST
K1EXITPID_DB | Kiln1 | KILN 1 EXIT TEMP PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N89:9 | KILN 1 EXIT TEMP PID DEADBAND
K1EXITPID_DR | Kiln1 | KILN 1 EXIT TEMP PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N89:5 | KILN 1 EXIT TEMP PID DR
K1EXITPID_PG | Kiln1 | KILN 1 EXIT TEMP PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N89:3 | KILN 1 EXIT TEMP PID PG
K1EXITPID_RT | Kiln1 | KILN 1 EXIT TEMP PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N89:4 | KILN 1 EXIT TEMP PID RT
K1EXITPID_UT | Kiln1 | KILN 1 EXIT TEMP PID UPDATE TIME | .01 SEC | 32000 | 1 | 0 | 0 | PLC_INTREAD | T4:585.PRE | KILN 1 EXIT TEMP PID UPDATE TIME
K1EXITSP_RECOM | Kiln1 | KILN 1 RECOMMENDED EXIT TEMP PID SP | deg F | 2516 | 1 | 0 | 0 | PLC_FLTREAD | F9:458
K1FUELEFF_CUR | Kiln1 | KILN 1 FUEL EFFICIENCY | MMBTU/TON LIME | 50 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:244 | KILN 1 FUEL EFFICIENCY
K1FUELEFF_DAY | Kiln1 | KILN 1 FUEL EFFICIENCY DAILY FINAL | MMBTU/TON LIME | 50 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:247 | KILN 1 FUEL EFFICIENCY DAILY FINAL
K1HOODP_PIDSP | Kiln1 | K1 FIRE HOOD DRAFT PID SP TO CONTROL FN 1-314 | "WC | 0 | 0.01 | 0 | -0.3 | PLC_FLTWRITE | F71:4
K1HOODPPID_AM | Kiln1 | KILN 1 HOOD P PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100/67
K1HOODPPID_CV | Kiln1 | KILN 1 HOOD P PID CV (FN 1-314 %) |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N80:24
K1HOODPPID_DB | Kiln1 | KILN 1 HOOD P PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N80:9
K1HOODPPID_DR | Kiln1 | K1 HOOD P PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N80:5
K1HOODPPID_ER | Kiln1 | KILN 1 HOOD P PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N80:15
K1HOODPPID_PG | Kiln1 | KILN 1 HOOD P PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N77:3
K1HOODPPID_PIDSP | Kiln1 | FN 1-314 PID SP - SP = K1HOODP_PIDSP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N80:2
K1HOODPPID_PV | Kiln1 | KILN 1 HOOD P PID PV (HOOD DRAFT) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N80:23
K1HOODPPID_RT | Kiln1 | KILN 1 HOOD P PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N80:4
K1HOODPPID_TB | Kiln1 | KILN 1 HOOD P PID TB (FN 1-314 %) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N80:25
K1HOODPPID_UT | Kiln1 | KILN 1 HOOD P PID UPDATE TIME | SEC | 10000 | 1 | 0 | 0 | PLC_INTREAD | T4:269.PRE
K1O2_PIDSP | Kiln1 | K1 O2 PID SP | % | 2 | 0 | 0 | 0 | PLC_FLTWRITE | F71:32
K1O2CTRLSPC_ALM | Kiln1 | KILN 1 OXYGEN SPC CONTROL VIOLATION | On | PLC_ALARM | B101/236 | KILN 1 OXYGEN SPC CONTROL VIOLATION
K1O2PID_AM | Kiln1 | KILN 1 OXYGEN PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100:4/8
K1O2PROBEWATERFLOW_ALM | Kiln1 | KILN 1 O2 PROBE WATER FLOW SWITCH FAILED | On | PLC_ALARM | B101/31 | KILN 1 O2 PROBE WATER FLOW SWITCH FAILED
K1O2SPC_ACT | Kiln1 | KILN 1 ACTUAL OXYGEN SPC VIOLATION | % O2 | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:401 | KILN 1 ACTUAL OXYGEN SPC VIOLATION
K1O2SPC_ACTION | Kiln1 | KILN 1 OXYGEN SPC CORRECTIVE ACTION CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:98 | KILN 1 OXYGEN SPC CORRECTIVE ACTION CODE
K1O2SPC_REA | Kiln1 | KILN 1 OXYGEN SPC REASON CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:97 | KILN 1 OXYGEN SPC REASON CODE
K1O2SPC_ULCL | Kiln1 | KILN 1 OXYGEN SPC UCL/LCL VIOLATION | None | PLC_DISCREAD | B3/739 | KILN 1 OXYGEN SPC UCL/LCL VIOLATION
K1O2SPCDAY_ALM | Kiln1 | K1 O2 SPC VIOLATION DAY
K1O2SPCHR_ALM | Kiln1 | K1 O2 SPC VIOLATION TIME
K1RUNTIME_DAY | Kiln1 | KILN 1 RUNTIME DAILY FINAL | HOURS | 24 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:257 | KILN 1 RUNTIME DAILY FINAL
K1SPCCHART_PBS | Kiln1 | KILN 1 RESTART SPC CHARTS | On | PLC_DISCWRITE | B100/95 | KILN 1 SPC CHARTS RESTARTED, UPDATE IN 15 MIN!!
K1SPCUPDATE_ALM | Kiln1 | KILN 1 SPC CHART UPDATE IS OFF | On | PLC_ALARM | B101/138 | KILN 1 SPC CHART UPDATE TURNED OFF BY PLC!!
K1T30_0000 | Kiln1 | KILN 1 REACTIVITY T30 AT 0000 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:0
K1T30_0000_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0000 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:0
K1T30_0030 | Kiln1 | KILN 1 REACTIVITY T30 AT 0030 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:1
K1T30_0030_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0030 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:1
K1T30_0100 | Kiln1 | KILN 1 REACTIVITY T30 AT 0100 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:2
K1T30_0100_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0100 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:2
K1T30_0130 | Kiln1 | KILN 1 REACTIVITY T30 AT 0130 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:3
K1T30_0130_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0130 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:3
K1T30_0200 | Kiln1 | KILN 1 REACTIVITY T30 AT 0200 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:4
K1T30_0200_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0200 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:4
K1T30_0230 | Kiln1 | KILN 1 REACTIVITY T30 AT 0230 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:5
K1T30_0230_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0230 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:5
K1T30_0300 | Kiln1 | KILN 1 REACTIVITY T30 AT 0300 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:6
K1T30_0300_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0300 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:6
K1T30_0330 | Kiln1 | KILN 1 REACTIVITY T30 AT 0330 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:7
K1T30_0330_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0330 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:7
K1T30_0400 | Kiln1 | KILN 1 REACTIVITY T30 AT 0400 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:8
K1T30_0400_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0400 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:8
K1T30_0430 | Kiln1 | KILN 1 REACTIVITY T30 AT 0430 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:9
K1T30_0430_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0430 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:9
K1T30_0500 | Kiln1 | KILN 1 REACTIVITY T30 AT 0500 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:10
K1T30_0500_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0500 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:10
K1T30_0530 | Kiln1 | KILN 1 REACTIVITY T30 AT 0530 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:11
K1T30_0530_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0530 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:11
K1T30_0600 | Kiln1 | KILN 1 REACTIVITY T30 AT 0600 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:12
K1T30_0600_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0600 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:12
K1T30_0630 | Kiln1 | KILN 1 REACTIVITY T30 AT 0630 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:13
K1T30_0630_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0630 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:13
K1T30_0700 | Kiln1 | KILN 1 REACTIVITY T30 AT 0700 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:14
K1T30_0700_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0700 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:14
K1T30_0730 | Kiln1 | KILN 1 REACTIVITY T30 AT 0730 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:15
K1T30_0730_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0730 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:15
K1T30_0800 | Kiln1 | KILN 1 REACTIVITY T30 AT 0800 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:16
K1T30_0800_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0800 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:16
K1T30_0830 | Kiln1 | KILN 1 REACTIVITY T30 AT 0830 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:17
K1T30_0830_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0830 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:17
K1T30_0900 | Kiln1 | KILN 1 REACTIVITY T30 AT 0900 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:18
K1T30_0900_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0900 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:18
K1T30_0930 | Kiln1 | KILN 1 REACTIVITY T30 AT 0930 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:19
K1T30_0930_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 0930 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:19
K1T30_1000 | Kiln1 | KILN 1 REACTIVITY T30 AT 1000 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:20
K1T30_1000_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1000 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:20
K1T30_1030 | Kiln1 | KILN 1 REACTIVITY T30 AT 1030 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:21
K1T30_1030_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1030 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:21
K1T30_1100 | Kiln1 | KILN 1 REACTIVITY T30 AT 1100 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:22
K1T30_1100_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1100 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:22
K1T30_1130 | Kiln1 | KILN 1 REACTIVITY T30 AT 1130 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:23
K1T30_1130_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1130 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:23
K1T30_1200 | Kiln1 | KILN 1 REACTIVITY T30 AT 1200 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:24
K1T30_1200_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1200 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:24
K1T30_1230 | Kiln1 | KILN 1 REACTIVITY T30 AT 1230 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:25
K1T30_1230_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1230 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:25
K1T30_1300 | Kiln1 | KILN 1 REACTIVITY T30 AT 1300 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:26
K1T30_1300_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1300 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:26
K1T30_1330 | Kiln1 | KILN 1 REACTIVITY T30 AT 1330 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:27
K1T30_1330_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1330 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:27
K1T30_1400 | Kiln1 | KILN 1 REACTIVITY T30 AT 1400 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:28
K1T30_1400_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1400 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:28
K1T30_1430 | Kiln1 | KILN 1 REACTIVITY T30 AT 1430 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:29
K1T30_1430_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1430 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:29
K1T30_1500 | Kiln1 | KILN 1 REACTIVITY T30 AT 1500 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:30
K1T30_1500_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1500 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:30
K1T30_1530 | Kiln1 | KILN 1 REACTIVITY T30 AT 1530 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:31
K1T30_1530_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1530 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:31
K1T30_1600 | Kiln1 | KILN 1 REACTIVITY T30 AT 1600 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:32
K1T30_1600_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1600 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:32
K1T30_1630 | Kiln1 | KILN 1 REACTIVITY T30 AT 1630 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:33
K1T30_1630_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1630 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:33
K1T30_1700 | Kiln1 | KILN 1 REACTIVITY T30 AT 1700 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:34
K1T30_1700_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1700 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:34
K1T30_1730 | Kiln1 | KILN 1 REACTIVITY T30 AT 1730 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:35
K1T30_1730_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1730 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:35
K1T30_1800 | Kiln1 | KILN 1 REACTIVITY T30 AT 1800 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:36
K1T30_1800_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1800 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:36
K1T30_1830 | Kiln1 | KILN 1 REACTIVITY T30 AT 1830 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:37
K1T30_1830_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1830 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:37
K1T30_1900 | Kiln1 | KILN 1 REACTIVITY T30 AT 1900 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:38
K1T30_1900_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1900 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:38
K1T30_1930 | Kiln1 | KILN 1 REACTIVITY T30 AT 1930 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:39
K1T30_1930_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 1930 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:39
K1T30_2000 | Kiln1 | KILN 1 REACTIVITY T30 AT 2000 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:40
K1T30_2000_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2000 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:40
K1T30_2030 | Kiln1 | KILN 1 REACTIVITY T30 AT 2030 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:41
K1T30_2030_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2030 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:41
K1T30_2100 | Kiln1 | KILN 1 REACTIVITY T30 AT 2100 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:42
K1T30_2100_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2100 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:42
K1T30_2130 | Kiln1 | KILN 1 REACTIVITY T30 AT 2130 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:43
K1T30_2130_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2130 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:43
K1T30_2200 | Kiln1 | KILN 1 REACTIVITY T30 AT 2200 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:44
K1T30_2200_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2200 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:44
K1T30_2230 | Kiln1 | KILN 1 REACTIVITY T30 AT 2230 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:45
K1T30_2230_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2230 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:45
K1T30_2300 | Kiln1 | KILN 1 REACTIVITY T30 AT 2300 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:46
K1T30_2300_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2300 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:46
K1T30_2330 | Kiln1 | KILN 1 REACTIVITY T30 AT 2330 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:47
K1T30_2330_YEST | Kiln1 | KILN 1 REACTIVITY T30 AT 2330 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:47
K1T30_DAVG | Kiln1 | KILN 1 REACTIVITY T30 DAY SHIFT AVG | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N20:50
K1T30_DAVG_YEST | Kiln1 | KILN 1 REACTIVITY T30 DAY SHIFT AVG YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:50
K1T30_GAVG | Kiln1 | KILN 1 REACTIVITY T30 GRAVE SHIFT AVG | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N20:52
K1T30_GAVG_YEST | Kiln1 | KILN 1 REACTIVITY T30 GRAVE SHIFT AVG | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:52
K1T30_LAST | Kiln1 | KILN 1 REACTIVITY T30 LAST SAMPLE | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N20:48
K1T30_LAST_YEST | Kiln1 | KILN 1 REACTIVITY T30 LAST SAMPLE YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:48
K1T30_LOWLIMIT | Kiln1 | KILN 1 REACTIVITY T30 LOW LIMIT | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N20:54
K1T30_TAVG | Kiln1 | KILN 1 REACTIVITY T30 AVERAGE | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N20:53
K1T30_TAVG_YEST | Kiln1 | KILN 1 REACTIVITY T30 AVERAGE YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N23:53
K2_LIMECO2_DAVG_YEST | Kiln1 | KILN 2 LIME CO2 DAY SHIFT AVERAGE YESTERDAY | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:843
K2_LIMECO2_GAVG_YEST | Kiln1 | KILN 2 LIME CO2 GRAVE SHIFT AVERAGE YESTERDAY | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:844
K2_LIMECO2_TAVG_YEST | Kiln1 | KILN 2 LIME CO2 AVERAGE YESTERDAY | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:845
K2EXIT_PIDACC | Kiln1 | KILN 2 EXIT TEMP PID UPDATE ACC |  | 32000 | 5 | 0 | 0 | PLC_FLTREAD | T4:506.ACC | KILN 1 EXIT TEMP PID PID ERROR
KD1308_AMPS | Kiln1 | KILN 1 KILN DRIVE 1-308 AMPS | Amps | 291.4 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:466 | KD 1-308 AMPS
KD1308_ENABLE | Kiln1 | KILN 1 KILN DRIVE ENABLED | None | PLC_ALARM | B101/578
KD1308_FAULT | Kiln1 | KILN 1 KILN DRIVE 1-308 DRIVE FAULT | On | PLC_ALARM | B101/577 | KILN 1 KILN DRIVE FAULT
KD1308_IM | Kiln1 | KD 1-308 INTERLOCKS MET | None | PLC_DISCREAD | B3/269 | KD 1-308 INTERLOCKS MET
KD1308_IT_AH | Kiln1 | KD 1-308 Hi Current Alarm | On | PLC_ALARM | B3/1271 | Kiln 1 Kiln Drive HI CURRENT
KD1308_OFFSET | Kiln1 | KD 1308 STROKE OFFSET FOR KILN SPEED | % | 25 | 1 | 0 | -25 | PLC_INTWRITE | N99:10 | KD 1308 STROKE OFFSET FOR KILN SPEED
KD1308_PBS | Kiln1 | KD 1-308 START | None | PLC_DISCWRITE | B100/386 | KD 1-308 DRIVE RESET
KD1308_PBT | Kiln1 | KD 1308 PC STOP | None | PLC_DISCWRITE | B100/365 | KD 1308 PC STOP
KD1308_RESET | Kiln1 | KD 1-308 DRIVE RESET | None | PLC_DISCWRITE | B100/688 | KD 1-308 DRIVE RESET
KD1308_RPH | Kiln1 | KD 1-308 KILN RPH | RPH | 75 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:58 | KD 1-308 SPEED RPH
KD1308_RT_HRS | Kiln1 | KD 1-308 Kiln drive runtime hours | HRS | 100000 | 0.01 | 0 | 0 | PLC_FLTREAD | F28:0 | KD 1-308 Kiln drive runtime hours
KD1308_RT_RST | Kiln1 | KD 1-308 HMI runtime hours reset bit | None | PLC_DISCWRITE | B3/1270 | KD 1-308 HMI runtime hours reset bit
KD1308_SSA_HMI | Kiln1 | KD 1-308 HMI switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1267 | KD 1-308 HMI switch 0=Auto 1=Manual
KD1308_ST | Kiln1 | KD 1-308 SPEED FDBK | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:62 | KD 1-308 SPEED FDBK
KD1308FS_%RUN | Kiln1 | KILN 1 DRIVE FEED TO SPEED % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:285 | KILN 1 DRIVE FEED TO SPEED % RUNTIME - TODAY
KD1308FS_%RUN_YEST | Kiln1 | KILN 1 DRIVE FEED TO SPEED % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:335 | KILN 1 DRIVE FEED TO SPEED % RUNTIME - PAST
KD1308FS_AVAIL | Kiln1 | KILN 1 DRIVE FEED TO SPEED AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:284 | KILN 1 DRIVE FEED TO SPEED AVAIL RUN HOURS - TODAY
KD1308FS_AVAIL_YEST | Kiln1 | KILN 1 DRIVE FEED TO SPEED AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:334 | KILN 1 DRIVE FEED TO SPEED AVAIL RUN HOURS - PAST
KD1308FS_TOG | Kiln1 | KD 1-308 FEED TO SPEED PC TOGGLE ON/OFF | None | PLC_DISCWRITE | B100/66 | KD 1-308 FEED TO SPEED PC TOGGLE ON/OFF
KD1308FTS_ALM | Kiln1 | KD 1-308 FAILED TO START | On | PLC_ALARM | B101/199 | KD 1-308 FAILED TO START
KD1308IT | Kiln1 | KD 1-308 LOAD | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:54 | KD 1-308 LOAD
KD1308LUBE2_ALM | Kiln1 | KD 1-308 LUBE FAILURE | On | PLC_ALARM | I:57/12 | KD 1-308 LUBE FAILURE
KD1308MS_TIM | Kiln1 | KD 1-308 ROLLBACK TIMER TIMING | On | PLC_DISCREAD | T4:746.TT | KD 1-308 ROLLBACK TIMER TIMING
KD1308MS_X | Kiln1 | KD 1-308 KILN 1 KILN DRIVE AUX FDBK | Off | PLC_DISCREAD | B3:75/14 | KD 1-308 STOPPED
KD1308MSF_ALM | Kiln1 | KD 1-308 DRIVE FAULT | On | PLC_ALARM | I:25/10 | KD 1-308 DRIVE FAULT
KD1308ST_F | Kiln1 | KD 1308 DRIVE SPEED SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:44 | KD 1308 DRIVE SPEED SETPOINT
KILN1_CO_AVERAGE | Kiln1 | KILN 1 AVE CO PPM | PPM | 50000 | 25 | 0 | 0 | PLC_FLTREAD | F8:129 | KILN 1 PERCENT CARBON MONOXIDE
KILN1_COALBYWEIGHT | Kiln1 |  | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F71:22 | 2
KILN1_COKEBYBTU | Kiln1 | KILN #1 % COKE BY BTU | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:449
KILN1_COKEBYWEIGHT | Kiln1 | KILN 1 % COKE BY WEIGHT | % | 100 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:19
KILN1_DUSTSYS_PBS | Kiln1 | KILN 1 DUST SYSTEM PC START | None | PLC_DISCWRITE | B100/556
KILN1_OPAC_RES | Kiln1 | KILN 1 OPACITY RECALABRATED | None | PLC_DISCWRITE | B67/3 | KILN 1 OPACITY RECALABRATED
KILN1_SFUELAL2O3 | Kiln1 | KILN #1 SOLID FUEL % Al2O3 | % | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:455
KILN1_SFUELASH | Kiln1 | KILN #1 SOLID FUEL % ASH | % | 50 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:453
KILN1_SFUELBTUTON | Kiln1 | KILN #1 SOLID FUEL MMBTU/TON | MMBTU/ton | 40 | 0.1 | 0 | 5 | PLC_FLTREAD | F9:451
KILN1_TEMP_DEV_LOW | Kiln1 | Kiln1 Exit/Inlet Temperature Deviation Low | On | PLC_DISCREAD | B101:36/4 | Kiln 1 Exit/Inlet Temperature Deviation Low
KILN1DUSTBINHL_ALM | Kiln1 | KILN 1 DUST BIN HIGH LEVEL! | On | PLC_ALARM | I:23/01 | KILN 1 DUST BIN HIGH LEVEL!
KILN2_CO_AVERAGE | Kiln1 | KILN 2 AVE CO PPM | PPM | 50000 | 25 | 0 | 0 | PLC_FLTREAD | F8:128 | KILN 1 PERCENT CARBON MONOXIDE
KILN2_O2_AVERAGE | Kiln1 | KILN 2 AVE O2 % | % | 20.9 | 0 | 0 | 0 | PLC_FLTREAD | F27:71
KN1308_FTS_RATIO | Kiln1 | KD 1308 FTS Ratio | LST/RPH | 2 | 0 | 0 | 0 | PLC_FLTREAD | F9:483 | KILN 1 PERCENT OXYGEN
KN1308_NOX_IND | Kiln1 | KILN 1 NOx Value | PPM | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:467 | KILN 1 PERCENT OXYGEN
KN1308_NOX_SPT | Kiln1 | KILN 1 NOx SNCR Setpoint | PPM | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:480 | KILN 1 PERCENT OXYGEN
KN1308_UE_IND | Kiln1 | KILN 1 SNCR UREA FLOW RATE | GPM | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:469 | SNCR K1 UE GPM HIGH
KN1308AT_1 | Kiln1 | KILN 1 OPACITY 6 MINUTE AVERAGE |  | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:20 | KILN 1 OPACITY 6 MINUTE AVERAGE
KN1308AT_2 | Kiln1 | KILN 1 OPACITY INSTANTANEOUS |  | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:21 | KILN 1 OPACITY INSTANTANEOUS
KN1308AT_2ROLL | Kiln1 | KILN 1 OPACITY 3-HR ROLLING AVERAGE | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:407 | KILN 1 OPACITY 3-HR ROLLING AVERAGE
KN1308AT_3 | Kiln1 | KILN 1 PERCENT OXYGEN | % | 25 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:26 | KILN 1 PERCENT OXYGEN
KN1308AT_3_ALM | Kiln1 | KILN 1 EXTRACTION 02 > 5% FOR 5 MIN | On | PLC_ALARM | B101/149 | KILN 1 EXTRACTION 02 > 5% FOR 5 MIN
KN1308AT_4 | Kiln1 | KILN 1 PERCENT CARBON MONOXIDE | PPM | 50000 | 25 | 0 | 0 | PLC_FLTREAD | F9:27 | KILN 1 PERCENT CARBON MONOXIDE
KN1308AT1_ALM | Kiln1 | KILN 1 OPACITY 6 MINUTE AVERAGE > 15% | On | PLC_ALARM | B101/264 | KILN 1 OPACITY 6 MINUTE AVERAGE > 15%
KN1308AT2ROLL_ALM | Kiln1 | KILN 1 3-HR ROLLING AVERAGE OPACITY > 25% | On | PLC_ALARM | B101/533 | KILN 1 3-HR ROLLING AVERAGE OPACITY > 25%
KN1308AT2ROLL_HOURS | Kiln1 | KILN 1 3-HR ROLLING AVG HIGH FOR XX HOURS | Hours | 8760 | 0 | 0 | 0 | PLC_INTREAD | C5:9.ACC
KN1308AT2ROLL24_ALM | Kiln1 | KILN 1 3-HR ROLLING AVERAGE HIGH FOR OVER 24 HOURS | On | PLC_ALARM | B101/565 | KILN 1 3-HR ROLLING AVERAGE HIGH FOR OVER 24 HOURS!!
KN1308SHTDWN15_ALM | Kiln1 | TURN KILN 1/4 TURN | On | PLC_ALARM | B101:7/12 | TURN KILN 1/4 TURN
KN1308SHTDWN30_ALM | Kiln1 | TURN KILN 1/4 TURN | On | PLC_ALARM | B101:7/13 | TURN KILN 1/4 TURN
KN1308SHTDWNSTOP_ALM | Kiln1 | 4 HRS SINCE BM 1-605 OFF, STOP TURNING KILN | On | PLC_ALARM | B101:7/14 | 4 HRS SINCE BM 1-605 OFF, STOP TURNING KILN
KN1308TT_1 | Kiln1 | KILN 1 FIRING ZONE TEMP | °F | 3000 | 5 | 0 | 0 | PLC_FLTREAD | F9:34 | KILN 1 FIRING ZONE TEMP
KN1308TT_1_TREND | Kiln1 | KILN 1 FIRING ZONE TEMPERATURE |  | 2400 | 5 | 0 | KILN 1 FIRING ZONE TEMPERATURE | 0 | 0 | 0
KN1308TT_2 | Kiln1 | KILN 1 EXIT TEMP | °F | 3000 | 1 | 0 | 0 | PLC_INTREAD | N58:00 | KILN 1 EXIT TEMP
KN1308TT_2_STREND | Kiln1 | KILN 1 EXIT TEMPERATURE |  | 2200 | 5 | 0 | KILN 1 EXIT TEMPERATURE | 0 | 0 | 0
KN1308TT_2_TREND | Kiln1 | KILN 1 EXIT TEMPERATURE |  | 2400 | 5 | 0 | KILN 1 EXIT TEMPERATURE | 0 | 0 | 0
KN1308TT_4 | Kiln1 | KILN #1 SECONDARY AIR TEMP | °F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N39:18 | KILN #1 SECONDARY AIR TEMP
KN1308TT_4_TREND | Kiln1 | Kiln #1 secondary air temp trending |  | 2200 | 5 | 0 | Kiln #1 secondary air temp trending | 0 | 0 | 0
KN1308TT_DNE | Kiln1 | KILN 1 D.E. N.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:4 | KILN 1 D.E. N.E. TRUNION BRG TEMPERATURE
KN1308TT_DNW | Kiln1 | KILN 1 D.E. N.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:5 | KILN 1 D.E. N.W. TRUNION BRG TEMPERATURE
KN1308TT_DSE | Kiln1 | KILN 1 D.E. S.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:6 | KILN 1 D.E. S.E. TRUNION BRG TEMPERATURE
KN1308TT_DSW | Kiln1 | KILN 1 D.E. S.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:7 | KILN 1 D.E. S.W. TRUNION BRG TEMPERATURE
KN1308TT_FNE | Kiln1 | KILN 1 F.E. N.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:0 | KILN 1 F.E. N.E. TRUNION BRG TEMPERATURE
KN1308TT_FNW | Kiln1 | KILN 1 F.E. N.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:1 | KILN 1 F.E. N.W. TRUNION BRG TEMPERATURE
KN1308TT_FSE | Kiln1 | KILN 1 F.E. S.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:2 | KILN 1 F.E. S.E. TRUNION BRG TEMPERATURE
KN1308TT_FSW | Kiln1 | KILN 1 F.E. S.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N43:3 | KILN 1 F.E. S.W. TRUNION BRG TEMPERATURE
KN1308TTDNE_HA | Kiln1 | KILN 1 D.E. N.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/76 | KILN 1 D.E. N.E. TRUNION BRG TEMP > 180
KN1308TTDNE_HHA | Kiln1 | KILN 1 D.E. N.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/84 | KILN 1 D.E. N.E. TRUNION BRG TEMP > 220
KN1308TTDNW_HA | Kiln1 | KILN 1 D.E. N.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/77 | KILN 1 D.E. N.W. TRUNION BRG TEMP > 180
KN1308TTDNW_HHA | Kiln1 | KILN 1 D.E. N.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/85 | KILN 1 D.E. N.W. TRUNION BRG TEMP > 220
KN1308TTDSE_HA | Kiln1 | KILN 1 D.E. S.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/78 | KILN 1 D.E. S.E. TRUNION BRG TEMP > 180
KN1308TTDSE_HHA | Kiln1 | KILN 1 D.E. S.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/86 | KILN 1 D.E. S.E. TRUNION BRG TEMP > 220
KN1308TTDSW_HA | Kiln1 | KILN 1 D.E. S.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/79 | KILN 1 D.E. S.W. TRUNION BRG TEMP > 180
KN1308TTDSW_HHA | Kiln1 | KILN 1 D.E. S.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/87 | KILN 1 D.E. S.W. TRUNION BRG TEMP > 220
KN1308TTFNE_HA | Kiln1 | KILN 1 F.E. N.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/72 | KILN 1 F.E. N.E. TRUNION BRG TEMP > 180
KN1308TTFNE_HHA | Kiln1 | KILN 1 F.E. N.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/80 | KILN 1 F.E. N.E. TRUNION BRG TEMP > 220
KN1308TTFNW_HA | Kiln1 | KILN 1 F.E. N.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/73 | KILN 1 F.E. N.W. TRUNION BRG TEMP > 180
KN1308TTFNW_HHA | Kiln1 | KILN 1 F.E. N.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/81 | KILN 1 F.E. N.W. TRUNION BRG TEMP > 220
KN1308TTFSE_HA | Kiln1 | KILN 1 F.E. S.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/74 | KILN 1 F.E. S.E. TRUNION BRG TEMP > 180
KN1308TTFSE_HHA | Kiln1 | KILN 1 F.E. S.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/82 | KILN 1 F.E. S.E. TRUNION BRG TEMP > 220
KN1308TTFSW_HA | Kiln1 | KILN 1 F.E. S.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/75 | KILN 1 F.E. S.W. TRUNION BRG TEMP > 180
KN1308TTFSW_HHA | Kiln1 | KILN 1 F.E. S.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/83 | KILN 1 F.E. S.W. TRUNION BRG TEMP > 220
KN1308UE_IM | Kiln1 | KN1308UE Alarm State | None | PLC_DISCREAD | N107:41/0 | KN1308UE PERMISSIVE
KN1308UE_X | Kiln1 | KN1308UE AUX FDBK | Off | PLC_DISCREAD | N107:41/1 | KN1308UE STOPPED
NEL_KN1_DG1401_ZT_IND | Kiln1 | Kiln 1 DG1401 % Ind | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F8:159
NEL_KN1_DG1401_ZT_SPT | Kiln1 | Kiln 1 DG1401 % Setpoint | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F8:157
NEL_KN1_DG1420_ZT_IND | Kiln1 | Kiln 1 DG1420 % Ind | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F8:158
NEL_KN1_DG1420_ZT_SPT | Kiln1 | Kiln 1 DG1420 % Setpoint | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F8:156
NEL_KN1_RA1317A_AUTO | Kiln1 | Kiln 1 RA1317A Rotary Airlock Auto | Off | KILN1_BH_READ | NEL_KN1_RA1317A_AUTO | Kiln 1 Dust System RA1317A Auto
NEL_KN1_RA1317A_AUX | Kiln1 | Kiln 1 RA1317A Rotary Airlock Aux | Off | KILN1_BH_READ | NEL_KN1_RA1317A_AUX | Kiln 1 Dust System RA1317A Stopped
NEL_KN1_RA1317A_PBE_HMI | Kiln1 | Kiln 1 RA1317A Rotary Airlock Start | None | KILN1_BH_WRITE | NEL_KN1_RA1317A_PBE_HMI
NEL_KN1_RA1317A_PBS_HMI | Kiln1 | Kiln 1 RA1317A Rotary Airlock Stop | None | KILN1_BH_WRITE | NEL_KN1_RA1317A_PBS_HMI
NEL_KN1_SC1603_QT_IND | Kiln1 | WF 1601 AND WF16A KILN 1 TONS PER HOUR | TPH | 15 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_SC1603_QT.IND | WF 2601A TONS PER HOUR
NEL_KN1_SC1603_ST_SPT | Kiln1 | WF 1-601 AND WF 1-1601A FEED RATE SETPOINT | TPH | 15 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_SC1603_ST.SPT | WF 1-601 FEED RATE SETPOINT
NEL_KN1_SC1613_AUX | Kiln1 | SC1613 KILN 1 FUEL SCREW AUX FDBK | Off | USCNEL101 | NEL_KN1_SC1613.AUX | SC613 STOPPED
NEL_KN1_SC1613_FLT | Kiln1 | SC1613 KILN 1 FUEL FAULT | On | USCNEL101 | NEL_KN1_SC1613.FLT | SC1613 FAULTED
NEL_KN1_SC1613_FTS_ALM | Kiln1 | SC1613 KILN 1 FUEL SCREW FTS ALM | On | USCNEL101 | NEL_KN1_SC1613.FTS_ALM | SC613 FAILED TO START
NEL_KN1_SC1613_IT_IND | Kiln1 | SC1613 KILN 1 FUEL AMPS | AMPS | 25 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_SC1613_IT.IND
NEL_KN1_SC1613_MLOCK | Kiln1 | SC1613 KILN 1 FUEL MLOCK | Off | USCNEL101 | NEL_KN1_SC1613.MLOCK | SC1613 MLOCK NOT MET
NEL_KN1_SC1613_OVL_ALM | Kiln1 | SC1613 KILN 1 FUEL OVL ALM | On | USCNEL101 | NEL_KN1_SC1613.OVL_ALM | SC1613 OVERLOAD ALM
NEL_KN1_SC1613_PBE_HMI | Kiln1 | SC1613 KILN 1 FUEL SCREW PBE HMI | None | USCNEL101 | NEL_KN1_SC1613.PBE_HMI | SC613
NEL_KN1_SC1613_PBS_HMI | Kiln1 | SC1613 KILN 1 FUEL SCREW PBS HMI | None | USCNEL101 | NEL_KN1_SC1613.PBS_HMI | SC613
NEL_KN1_SC1613_PLOCK | Kiln1 | SC1613 KILN 1 FUEL PLOCK | Off | USCNEL101 | NEL_KN1_SC1613.PLOCK | SC1613 PLOCK NOT MET
NEL_KN1_SC1613_RDY | Kiln1 | SC1613 KILN 1 FUEL SCREW READY | Off | USCNEL101 | NEL_KN1_SC1613.RDY | SC1613 NOT READY
NEL_KN1_SC1613_SLOCK | Kiln1 | SC1613 KILN 1 FUEL SLOCK | Off | USCNEL101 | NEL_KN1_SC1613.SLOCK | SC1613 SLOCK NOT MET
NEL_KN1_SC1613_SS_ALM | Kiln1 | SC1613 KILN 1 FUEL SS ALM | On | USCNEL101 | NEL_KN1_SC1613.SS_ALM | SC1613 MOTION SWITCH FAILURE
NEL_KN1_SC1613_SS_BYP | Kiln1 | SC1613 KILN 1 FUEL SS BYPASS | On | USCNEL101 | NEL_KN1_SC1613.SS_BYP | SC1613 MOTION SWITCH BYPASSED
NEL_KN1_SC1613_SS_BYP_PB | Kiln1 | SC1613 KILN 1 FUEL SS BYPASS PB | None | USCNEL101 | NEL_KN1_SC1613.SS_BYP_PB | SC1613 MOTION SWITCH BYPASSED
NEL_KN1_SPC_CEM_ALM | Kiln1 | Kiln 1 SPC CO Violation | On | KILN1_BH_ALARM | NEL_KN1_SPC_CEM.ALM | K1 CO SPC VIOLATION. LOG EVENT.
NEL_KN1_SPC_CEM_ALM_CNT_PREV | Kiln1 | Kiln 1 SPC CO Violation Count Yesterday | TOT | 999 | 0 | 0 | 0 | KILN1_BH_READ | NEL_KN1_SPC_CEM.ALM_CNT_PREV | Kiln 1 SPC CO Violation Count Yesterday
NEL_KN1_SPC_QC_ALM | Kiln1 | Kiln 1 SPC Quality Violation | On | KILN1_BH_ALARM | NEL_KN1_SPC_QC.ALM | K1 QUALITY SPC VIOLATION. LOG EVENT.
NEL_KN1_SPC_QC_ALM_CNT_PREV | Kiln1 | Kiln 1 SPC QC Violation Count Yesterday | TOT | 999 | 0 | 0 | 0 | KILN1_BH_READ | NEL_KN1_SPC_QC.ALM_CNT_PREV | Kiln 1 SPC QC Violation Count Yesterday
NEL_KN1_SPC_TEMP_ALM | Kiln1 | Kiln 1 SPC Temperature Violation | On | KILN1_BH_ALARM | NEL_KN1_SPC_TEMP.ALM | K1 TEMPERATURE SPC VIOLATION. LOG EVENT.
NEL_KN1_SPC_TEMP_ALM_CNT_PREV | Kiln1 | Kiln 1 SPC TEMP Violation Count Yesterday | TOT | 999 | 0 | 0 | 0 | KILN1_BH_READ | NEL_KN1_SPC_TEMP.ALM_CNT_PREV | Kiln 1 SPC TEMP Violation Count Yesterday
NEL_KN1_WF1601_AUX | Kiln1 | WF1601 KILN 1 COAL #1 BIN AUX FDBK | Off | USCNEL101 | NEL_KN1_WF1601.AUX | WF1601 STOPPED
NEL_KN1_WF1601_FLT | Kiln1 | WF1601 KILN 1 COAL #1 BIN FAULT | On | USCNEL101 | NEL_KN1_WF1601.FLT | WF1601 FAULT ALM
NEL_KN1_WF1601_FTS_ALM | Kiln1 | WF1601 KILN 1 COAL #1 BIN FTS ALM | On | USCNEL101 | NEL_KN1_WF1601.FTS_ALM | WF1601 FAILED TO START
NEL_KN1_WF1601_IT_IND | Kiln1 | WF1601 KILN 1 COAL #1 BIN AMPS | AMPS | 25 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_IT.IND
NEL_KN1_WF1601_MLOCK | Kiln1 | WF1601 KILN 1 COAL #1 BIN MLOCK | Off | USCNEL101 | NEL_KN1_WF1601.MLOCK | WF1601 MLOCK NOT MET
NEL_KN1_WF1601_OVL_ALM | Kiln1 | WF1601 KILN 1 COAL #1 BIN OVL AML | On | USCNEL101 | NEL_KN1_WF1601.OVL_ALM | WF1601 OVL ALM
NEL_KN1_WF1601_PBE_HMI | Kiln1 | WF1601 KILN 1 COAL #1 BIN PBE HMI | None | USCNEL101 | NEL_KN1_WF1601.PBE_HMI | WF1601
NEL_KN1_WF1601_PBS_HMI | Kiln1 | WF1601 KILN 1 COAL #1 BIN PBS HMI | None | USCNEL101 | NEL_KN1_WF1601.PBS_HMI | WF1601
NEL_KN1_WF1601_PLOCK | Kiln1 | WF1601 KILN 1 COAL #1 BIN PLOCK | Off | USCNEL101 | NEL_KN1_WF1601.PLOCK | WF1601 PLOCK NOT MET
NEL_KN1_WF1601_QT_AH | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED RATE HI ALM | On | USCNEL101 | NEL_KN1_WF1601_QT.AH | WF1601 FEED RATE HI
NEL_KN1_WF1601_QT_AH_SPT | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED RATE HI ALM SPT | TPH | 10 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT.AH_SPT
NEL_KN1_WF1601_QT_AL | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED RATE LO ALM SPT | On | USCNEL101 | NEL_KN1_WF1601.QT_AL | WF1601 FEED RATE LOW
NEL_KN1_WF1601_QT_AL_SPT | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED RATE LO ALM SPT | TPH | 10 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT.AL_SPT
NEL_KN1_WF1601_QT_IND | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED RATE TPH | TPH | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT.IND
NEL_KN1_WF1601_QT_PCT_SPT | Kiln1 | WF 1-601 FEED PERCENT SETPOINT | % | 100 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT.PCT_SPT | WF 1-601 FEED RATE SETPOINT
NEL_KN1_WF1601_QT_SPT | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED RATE TPH SPT | TPH | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT.SPT
NEL_KN1_WF1601_QT_TOT | Kiln1 | WF1601 KILN 1 COAL #1 BIN FEED TOTALIZER | TONS | 9999 | 0 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601_QT.TOT
NEL_KN1_WF1601_RDY | Kiln1 | WF1601 KILN 1 COAL #1 BIN READY | Off | USCNEL101 | NEL_KN1_WF1601.RDY | WF1601 NOT READY
NEL_KN1_WF1601_SLOCK | Kiln1 | WF1601 KILN 1 COAL #1 BIN SLOCK | Off | USCNEL101 | NEL_KN1_WF1601.SLOCK | WF1601 SLOCK NOT MET
NEL_KN1_WF1601_SSA_HMI | Kiln1 | WF1601 KILN 1 COAL #1 BIN SSA HMI | Off | USCNEL101 | NEL_KN1_WF1601.SSA_HMI | WF1601 IN MANUAL
NEL_KN1_WF1601A_AUX | Kiln1 | WF1601A KILN 1 COKE #2 BIN AUX FDBK | Off | USCNEL101 | NEL_KN1_WF1601A.AUX | WF2601A STOPPED
NEL_KN1_WF1601A_FTS_ALM | Kiln1 | WF1601A KILN 1 COKE #2 BIN FAILED TO START | On | PLC_ALARM | B101/624 | WF2601A FAILED TO START
NEL_KN1_WF1601A_PBE_HMI | Kiln1 | WF 1601A PC START | None | PLC_DISCWRITE | B100/977 | WF 1-601 PC START
NEL_KN1_WF1601A_PBS_HMI | Kiln1 | WF 1601A PC STOP | None | PLC_DISCWRITE | B100/976 | WF 1-601 PC STOP
NEL_KN1_WF1601A_PLOCK | Kiln1 | WF1601A KILN 1 COKE #2 BIN PLOCK READY | Off | USCNEL101 | NEL_KN1_WF1601A.PLOCK | WF2601A NOT READY
NEL_KN1_WF1601A_QT_AH | Kiln1 | WF 1601A HIGH COAL FEED RATE ALARM | On | PLC_ALARM | B101/625 | WF 2601A HIGH COAL FEED RATE ALARM
NEL_KN1_WF1601A_QT_AH_SPT | Kiln1 | WF 1601A MAX FEED RATE ALARM SETPOINT | TPH | 14 | 1 | 0 | 1 | PLC_INTWRITE | N7:125 | WF 2601A MAX FEED RATE ALARM SETPOINT
NEL_KN1_WF1601A_QT_AL | Kiln1 | WF 1601A LOW COAL FEED RATE ALARM | On | PLC_ALARM | B101/626 | WF 2601A LOW COAL FEED RATE ALARM
NEL_KN1_WF1601A_QT_AL_SPT | Kiln1 | WF 1601A MIN FEED RATE ALARM SETPOINT | TPH | 14 | 1 | 0 | 1 | PLC_INTWRITE | N7:126 | WF 2601A MIN FEED RATE ALARM SETPOINT
NEL_KN1_WF1601A_QT_IND | Kiln1 | WF 1601A KILN 1 COKE #2 BIN TONS PER HOUR | TPH | 15 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601A_QT.IND | WF 2601A TONS PER HOUR
NEL_KN1_WF1601A_QT_PCT_SPT | Kiln1 | WF 1601A KILN 1 COKE #2 BIN PERCENTAGE SETPOINT | % | 100 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601A_QT.PCT_SPT | WF 2601A TONS PER HOUR
NEL_KN1_WF1601A_QT_SPT | Kiln1 | WF1601A KILN 1 COKE #2 BIN FEED RATE SETPOINT | TPH | 15 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601A_QT.SPT | WF 2601A FEED RATE SETPOINT
NEL_KN1_WF1601A_QT_TOT | Kiln1 | KILN 1 COKE TOTALIZER | Ton | 9999 | 0.01 | 0 | 0 | USCNEL101 | NEL_KN1_WF1601A_QT.TOT | KILN 1 WF2601A COAL TOTALIZER
NEL_KN1_WF1601A_RDY | Kiln1 | WF1601A KILN 1 COKE #2 BIN READY | Off | USCNEL101 | NEL_KN1_WF1601A.RDY | WF2601A NOT READY
NEL_KN2_SPC_CEM_ALM_CNT_PREV | Kiln1 | Kiln 2 SPC CO Violation Count Yesterday | TOT | 999 | 0 | 0 | 0 | KILN1_BH_READ | NEL_KN2_SPC_CEM.ALM_CNT_PREV | Kiln 2 SPC CO Violation Count Yesterday
NEL_KN2_SPC_QC_ALM_CNT_PREV | Kiln1 | Kiln 2 SPC QC Violation Count Yesterday | TOT | 999 | 0 | 0 | 0 | KILN1_BH_READ | NEL_KN2_SPC_QC.ALM_CNT_PREV | Kiln 2 SPC QC Violation Count Yesterday
NEL_KN2_SPC_TEMP_ALM_CNT_PREV | Kiln1 | Kiln 2 SPC TEMP Violation Count Yesterday | TOT | 999 | 0 | 0 | 0 | KILN1_BH_READ | NEL_KN2_SPC_TEMP.ALM_CNT_PREV | Kiln 2 SPC TEMP Violation Count Yesterday
NEL_SNCR_PU6206A_AUX | Kiln1 | CIRCULATION PUMP PU6206A AUX | Off | PLC_DISCREAD | N103:9/13 | CIRCULATION PUMP PU6206A STOPPED
NEL_SNCR_PU6206B_AUX | Kiln1 | CIRCULATION PUMP PU6206B AUX | Off | PLC_DISCREAD | N103:9/14 | CIRCULATION PUMP PU6206B STOPPED
NEL_SNCR_PU6239A_AUX | Kiln1 | CIRCULATION PUMP PU6239A AUX | Off | PLC_DISCREAD | N103:9/11 | CIRCULATION PUMP PU6239A STOPPED
NEL_SNCR_PU6239B_AUX | Kiln1 | CIRCULATION PUMP PU6239B AUX | Off | PLC_DISCREAD | N103:9/12 | CIRCULATION PUMP PU6239B STOPPED
OV1310%_ACT | Kiln1 | OHMART VEGA 1-310 COOLER LEVEL | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:13 | OHMART VEGA 1-310 COOLER LEVEL
OV1310_PULS68 | Kiln1 | OHMART VEGA 1-310 COOLER LEVEL PULS 68 | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | N38:12 | OHMART VEGA 1-310 COOLER LEVEL
OV1310_PULS81 | Kiln1 | OHMART VEGA 1-310 COOLER LEVEL PULS 81 | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | N38:10 | OHMART VEGA 1-310 COOLER LEVEL
OV1310_SELECT | Kiln1 | K1 OHMART VEGA SELECT | On | PLC_DISCWRITE | B100/615
OV1310FT_ACT | Kiln1 | K1 OHMART/VEGA COOLER LEVEL - FEET | FT | 10 | 0.1 | 0 | 2 | PLC_FLTREAD | F9:96 | K1 OHMART/VEGA COOLER LEVEL - FEET
PH1305_DSTR | Kiln1 | PH 1-305 STROKE RAMP UP SET POINT | STR/HR | 250 | 1 | 0 | 0 | PLC_INTWRITE | N102:96 | PH 1-305 STROKE RAMP UP SET POINT
PH1305_EN | Kiln1 | KILN 1 PREHEATER ENABLED TO RUN | Off | PLC_DISCREAD | B3/770 | KILN 1 PREHEATER RAMS TURNED OFF!
PH1305_IM | Kiln1 | KILN 1 PREHEATER INTERLOCKS MET | None | PLC_DISCREAD | B3/773 | KILN 1 PREHEATER INTERLOCKS MET
PH1305_INTBYP | Kiln1 | PH 1-305 KILN DRIVE INTERLOCK BYPASS ON | On | PLC_DISCWRITE | B100/349 | PH 1-305 KILN DRIVE INTERLOCK BYPASS ON
PH1305_MAXDBL | Kiln1 | PH 1-305 MAXIMUM RAMS DOUBLE STROKING | None | PLC_DISCWRITE | B3/1000
PH1305_PBS | Kiln1 | KILN 1 PREHEATER START | None | PLC_DISCWRITE | B100/131 | KILN 1 PREHEATER START
PH1305_PBT | Kiln1 | KILN 1 PREHEATER STOP | None | PLC_DISCWRITE | B100/132 | KILN 1 PREHEATER STOP
PH1305_PCDSTR | Kiln1 | PH 1-305 START STROKE RAMP UP | None | PLC_DISCWRITE | B100/518 | PH 1-305 START STROKE RAMP UP
PH1305_PIN | Kiln1 | PH 1-305 ALL RAMS PINNED | On | PLC_DISCWRITE | B100/6 | PH 1-305 ALL RAMS PINNED
PH1305FILTERPD_ALM | Kiln1 | PH 1-305 RETURN OIL FILTER D/P HIGH | On | PLC_ALARM | I:44/06 | PH 1-305 RETURN OIL FILTER D/P HIGH
PH1305HYDLO_ALM | Kiln1 | PH 1-305 HYDRAULIC OIL LEVEL LOW | On | PLC_ALARM | I:44/05 | PH 1-305 HYDRAULIC OIL LEVEL LOW
PH1305HYDLOLO_ALM | Kiln1 | PH 1-305 HYDRAULIC OIL LEVEL LOW-LOW | On | PLC_ALARM | I:44/04 | PH 1-305 HYDRAULIC OIL LEVEL LOW-LOW
PH1305HYDTEMP_ALM | Kiln1 | PH 1-305 HYDRAULIC OIL TEMPERATURE LOW | On | PLC_ALARM | I:44/07 | PH 1-305 HYDRAULIC OIL TEMPERATURE LOW
PH1305R1_BYP | Kiln1 | KILN 1 PH RAM 1 PC BYPASS ON | On | PLC_DISCWRITE | B100/582 | KILN 1 PH RAM 1 PC BYPASS ON
PH1305R1_CLOSED | Kiln1 | KILN 1 PH RAM 1 CLOSED | None | PLC_DISCREAD | I:42/00 | KILN 1 PH RAM 1 CLOSED
PH1305R1_CLOSING | Kiln1 | KILN 1 PH RAM 1 CLOSING | None | PLC_DISCREAD | O:44/00 | KILN 1 PH RAM 1 CLOSING
PH1305R1_DBL | Kiln1 | KILN 1 PH RAM 1 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/583 | KILN 1 PH RAM 1 PC DOUBLE STROKE ON
PH1305R1_OPENING | Kiln1 | KILN 1 PH RAM 1 OPENING | None | PLC_DISCREAD | B101/4 | KILN 1 PH RAM 1 OPENING
PH1305R1_PIN | Kiln1 | PH 1-305 RAM 1 PINNED | On | PLC_DISCWRITE | B100/177 | PH 1-305 RAM 1 PINNED
PH1305R1_SSW | Kiln1 | KILN 1 PH RAM 1 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/00 | KILN 1 PH RAM 1 MANUAL BYPASS ON
PH1305R10_BYP | Kiln1 | KILN 1 PH RAM 10 PC BYPASS ON | On | PLC_DISCWRITE | B100/600 | KILN 1 PH RAM 10 PC BYPASS ON
PH1305R10_CLOSED | Kiln1 | KILN 1 PH RAM 10 CLOSED | None | PLC_DISCREAD | I:42/011 | KILN 1 PH RAM 10 CLOSED
PH1305R10_CLOSING | Kiln1 | KILN 1 PH RAM 10 CLOSING | None | PLC_DISCREAD | O:44/011 | KILN 1 PH RAM 10 CLOSING
PH1305R10_DBL | Kiln1 | KILN 1 PH RAM 10 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/601 | KILN 1 PH RAM 10 PC DOUBLE STROKE ON
PH1305R10_OPENING | Kiln1 | KILN 1 PH RAM 10 OPENING | None | PLC_DISCREAD | B101/013 | KILN 1 PH RAM 10 OPENING
PH1305R10_PIN | Kiln1 | PH 1-305 RAM 10 PINNED | On | PLC_DISCWRITE | B100/368 | PH 1-305 RAM 10 PINNED
PH1305R10_SSW | Kiln1 | KILN 1 PH RAM 10 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/011 | KILN 1 PH RAM 10 MANUAL BYPASS ON
PH1305R10CLOSE_ALM | Kiln1 | KILN 1 PH RAM #10 CLOSING ALARM | On | PLC_ALARM | B101:3/2 | KILN 1 PH RAM #10 CLOSING ALARM
PH1305R10OPEN_ALM | Kiln1 | KILN 1 PH RAM #10 OPENING ALARM | On | PLC_ALARM | B101:4/0 | KILN 1 PH RAM #10 OPENING ALARM
PH1305R11_BYP | Kiln1 | KILN 1 PH RAM 11 PC BYPASS ON | On | PLC_DISCWRITE | B100/602 | KILN 1 PH RAM 11 PC BYPASS ON
PH1305R11_CLOSED | Kiln1 | KILN 1 PH RAM 11 CLOSED | None | PLC_DISCREAD | I:42/12 | KILN 1 PH RAM 11 CLOSED
PH1305R11_CLOSING | Kiln1 | KILN 1 PH RAM 11 CLOSING | None | PLC_DISCREAD | O:44/12 | KILN 1 PH RAM 11 CLOSING
PH1305R11_DBL | Kiln1 | KILN 1 PH RAM 11 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/603 | KILN 1 PH RAM 11 PC DOUBLE STROKE ON
PH1305R11_OPENING | Kiln1 | KILN 1 PH RAM 11 OPENING | None | PLC_DISCREAD | B101/14 | KILN 1 PH RAM 11 OPENING
PH1305R11_PIN | Kiln1 | PH 1- 305 RAM 11 PINNED | On | PLC_DISCWRITE | B100/372 | PH 1- 305 RAM 11 PINNED
PH1305R11_SSW | Kiln1 | KILN 1 PH RAM 11 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/12 | KILN 1 PH RAM 11 MANUAL BYPASS ON
PH1305R11CLOSE_ALM | Kiln1 | KILN 1 PH RAM #11 CLOSING ALARM | On | PLC_ALARM | B101:3/3 | KILN 1 PH RAM #11 CLOSING ALARM
PH1305R11OPEN_ALM | Kiln1 | KILN 1 PH RAM #11 OPENING ALARM | On | PLC_ALARM | B101:4/1 | KILN 1 PH RAM #11 OPENING ALARM
PH1305R12_BYP | Kiln1 | KILN 1 PH RAM 12 PC BYPASS ON | On | PLC_DISCWRITE | B100/604 | KILN 1 PH RAM 12 PC BYPASS ON
PH1305R12_CLOSED | Kiln1 | KILN 1 PH RAM 12 CLOSED | None | PLC_DISCREAD | I:42/013 | KILN 1 PH RAM 12 CLOSED
PH1305R12_CLOSING | Kiln1 | KILN 1 PH RAM 12 CLOSING | None | PLC_DISCREAD | O:44/013 | KILN 1 PH RAM 12 CLOSING
PH1305R12_DBL | Kiln1 | KILN 1 PH RAM 12 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/605 | KILN 1 PH RAM 12 PC DOUBLE STROKE ON
PH1305R12_OPENING | Kiln1 | KILN 1 PH RAM 12 OPENING | None | PLC_DISCREAD | B101/015 | KILN 1 PH RAM 12 OPENING
PH1305R12_PIN | Kiln1 | PH 1-305 RAM 12 PINNED | On | PLC_DISCWRITE | B100/373 | PH 1-305 RAM 12 PINNED
PH1305R12_SSW | Kiln1 | KILN 1 PH RAM 12 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/013 | KILN 1 PH RAM 12 MANUAL BYPASS ON
PH1305R12CLOSE_ALM | Kiln1 | KILN 1 PH RAM #12 CLOSING ALARM | On | PLC_ALARM | B101:3/4 | KILN 1 PH RAM #12 CLOSING ALARM
PH1305R12OPEN_ALM | Kiln1 | KILN 1 PH RAM #12 OPENING ALARM | On | PLC_ALARM | B101:4/2 | KILN 1 PH RAM #12 OPENING ALARM
PH1305R13_BYP | Kiln1 | KILN 1 PH RAM 13 PC BYPASS ON | On | PLC_DISCWRITE | B100/606 | KILN 1 PH RAM 13 PC BYPASS ON
PH1305R13_CLOSED | Kiln1 | KILN 1 PH RAM 13 CLOSED | None | PLC_DISCREAD | I:42/14 | KILN 1 PH RAM 13 CLOSED
PH1305R13_CLOSING | Kiln1 | KILN 1 PH RAM 13 CLOSING | None | PLC_DISCREAD | O:44/14 | KILN 1 PH RAM 13 CLOSING
PH1305R13_DBL | Kiln1 | KILN 1 PH RAM 13 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/607 | KILN 1 PH RAM 13 PC DOUBLE STROKE ON
PH1305R13_OPENING | Kiln1 | KILN 1 PH RAM 13 OPENING | None | PLC_DISCREAD | B101/16 | KILN 1 PH RAM 13 OPENING
PH1305R13_PIN | Kiln1 | PH 1-305 RAM 13 PINNED | On | PLC_DISCWRITE | B100/374 | PH 1-305 RAM 13 PINNED
PH1305R13_SSW | Kiln1 | KILN 1 PH RAM 13 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/14 | KILN 1 PH RAM 13 MANUAL BYPASS ON
PH1305R13CLOSE_ALM | Kiln1 | KILN 1 PH RAM #13 CLOSING ALARM | On | PLC_ALARM | B101:3/5 | KILN 1 PH RAM #13 CLOSING ALARM
PH1305R13OPEN_ALM | Kiln1 | KILN 1 PH RAM #13 OPENING ALARM | On | PLC_ALARM | B101:4/3 | KILN 1 PH RAM #13 OPENING ALARM
PH1305R14_BYP | Kiln1 | KILN 1 PH RAM 14 PC BYPASS ON | On | PLC_DISCWRITE | B100/608 | KILN 1 PH RAM 14 PC BYPASS ON
PH1305R14_CLOSED | Kiln1 | KILN 1 PH RAM 14 CLOSED | None | PLC_DISCREAD | I:42/015 | KILN 1 PH RAM 14 CLOSED
PH1305R14_CLOSING | Kiln1 | KILN 1 PH RAM 14 CLOSING | None | PLC_DISCREAD | O:44/015 | KILN 1 PH RAM 14 CLOSING
PH1305R14_DBL | Kiln1 | KILN 1 PH RAM 14 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/609 | KILN 1 PH RAM 14 PC DOUBLE STROKE ON
PH1305R14_OPENING | Kiln1 | KILN 1 PH RAM 14 OPENING | None | PLC_DISCREAD | B101/017 | KILN 1 PH RAM 14 OPENING
PH1305R14_PIN | Kiln1 | PH 1-305 RAM 14 PINNED | On | PLC_DISCWRITE | B100/375 | PH 1-305 RAM 14 PINNED
PH1305R14_SSW | Kiln1 | KILN 1 PH RAM 14 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/015 | KILN 1 PH RAM 14 MANUAL BYPASS ON
PH1305R14CLOSE_ALM | Kiln1 | KILN 1 PH RAM #14 CLOSING ALARM | On | PLC_ALARM | B101:3/6 | KILN 1 PH RAM #14 CLOSING ALARM
PH1305R14OPEN_ALM | Kiln1 | KILN 1 PH RAM #14 OPENING ALARM | On | PLC_ALARM | B101:4/4 | KILN 1 PH RAM #14 OPENING ALARM
PH1305R1CLOSE_ALM | Kiln1 | KILN 1 PH RAM #1 CLOSING ALARM | On | PLC_ALARM | B101:2/9 | KILN 1 PH RAM #1 CLOSING ALARM
PH1305R1OPEN_ALM | Kiln1 | KILN 1 PH RAM #1 OPENING ALARM | On | PLC_ALARM | B101:3/7 | KILN 1 PH RAM #1 OPENING ALARM
PH1305R2_BYP | Kiln1 | KILN 1 PH RAM 2 PC BYPASS ON | On | PLC_DISCWRITE | B100/584 | KILN 1 PH RAM 2 PC BYPASS ON
PH1305R2_CLOSED | Kiln1 | KILN 1 PH RAM 2 CLOSED | None | PLC_DISCREAD | I:42/001 | KILN 1 PH RAM 2 CLOSED
PH1305R2_CLOSING | Kiln1 | KILN 1 PH RAM 2 CLOSING | None | PLC_DISCREAD | O:44/001 | KILN 1 PH RAM 2 CLOSING
PH1305R2_DBL | Kiln1 | KILN 1 PH RAM 2 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/585 | KILN 1 PH RAM 2 PC DOUBLE STROKE ON
PH1305R2_OPENING | Kiln1 | KILN 1 PH RAM 2 OPENING | None | PLC_DISCREAD | B101/005 | KILN 1 PH RAM 2 OPENING
PH1305R2_PIN | Kiln1 | PH 1-305 RAM 2 PINNED | On | PLC_DISCWRITE | B100/193 | PH 1-305 RAM 2 PINNED
PH1305R2_SSW | Kiln1 | KILN 1 PH RAM 2 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/001 | KILN 1 PH RAM 2 MANUAL BYPASS ON
PH1305R2CLOSE_ALM | Kiln1 | KILN 1 PH RAM #2 CLOSING ALARM | On | PLC_ALARM | B101:2/10 | KILN 1 PH RAM #2 CLOSING ALARM
PH1305R2OPEN_ALM | Kiln1 | KILN 1 PH RAM #2 OPENING ALARM | On | PLC_ALARM | B101:3/8 | KILN 1 PH RAM #2 OPENING ALARM
PH1305R3_BYP | Kiln1 | KILN 1 PH RAM 3 PC BYPASS ON | On | PLC_DISCWRITE | B100/586 | KILN 1 PH RAM 3 PC BYPASS ON
PH1305R3_CLOSED | Kiln1 | KILN 1 PH RAM 3 CLOSED | None | PLC_DISCREAD | I:42/02 | KILN 1 PH RAM 3 CLOSED
PH1305R3_CLOSING | Kiln1 | KILN 1 PH RAM 3 CLOSING | None | PLC_DISCREAD | O:44/02 | KILN 1 PH RAM 3 CLOSING
PH1305R3_DBL | Kiln1 | KILN 1 PH RAM 3 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/587 | KILN 1 PH RAM 3 PC DOUBLE STROKE ON
PH1305R3_OPENING | Kiln1 | KILN 1 PH RAM 3 OPENING | None | PLC_DISCREAD | B101/6 | KILN 1 PH RAM 3 OPENING
PH1305R3_PIN | Kiln1 | PH 1-305 RAM 3 PINNED | On | PLC_DISCWRITE | B100/318 | PH 1-305 RAM 3 PINNED
PH1305R3_SSW | Kiln1 | KILN 1 PH RAM 3 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/02 | KILN 1 PH RAM 3 MANUAL BYPASS ON
PH1305R3CLOSE_ALM | Kiln1 | KILN 1 PH RAM #3 CLOSING ALARM | On | PLC_ALARM | B101:2/11 | KILN 1 PH RAM #3 CLOSING ALARM
PH1305R3OPEN_ALM | Kiln1 | KILN 1 PH RAM #3 OPENING ALARM | On | PLC_ALARM | B101:3/9 | KILN 1 PH RAM #3 OPENING ALARM
PH1305R4_BYP | Kiln1 | KILN 1 PH RAM 4 PC BYPASS ON | On | PLC_DISCWRITE | B100/588 | KILN 1 PH RAM 4 PC BYPASS ON
PH1305R4_CLOSED | Kiln1 | KILN 1 PH RAM 4 CLOSED | None | PLC_DISCREAD | I:42/003 | KILN 1 PH RAM 4 CLOSED
PH1305R4_CLOSING | Kiln1 | KILN 1 PH RAM 4 CLOSING | None | PLC_DISCREAD | O:44/003 | KILN 1 PH RAM 4 CLOSING
PH1305R4_DBL | Kiln1 | KILN 1 PH RAM 4 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/589 | KILN 1 PH RAM 4 PC DOUBLE STROKE ON
PH1305R4_OPENING | Kiln1 | KILN 1 PH RAM 4 OPENING | None | PLC_DISCREAD | B101/007 | KILN 1 PH RAM 4 OPENING
PH1305R4_PIN | Kiln1 | PH 1-305 RAM 4 PINNED | On | PLC_DISCWRITE | B100/319 | PH 1-305 RAM 4 PINNED
PH1305R4_SSW | Kiln1 | KILN 1 PH RAM 4 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/003 | KILN 1 PH RAM 4 MANUAL BYPASS ON
PH1305R4CLOSE_ALM | Kiln1 | KILN 1 PH RAM #4 CLOSING ALARM | On | PLC_ALARM | B101:2/12 | KILN 1 PH RAM #4 CLOSING ALARM
PH1305R4OPEN_ALM | Kiln1 | KILN 1 PH RAM #4 OPENING ALARM | On | PLC_ALARM | B101:3/10 | KILN 1 PH RAM #3 OPENING ALARM
PH1305R5_BYP | Kiln1 | KILN 1 PH RAM 5 PC BYPASS ON | On | PLC_DISCWRITE | B100/590 | KILN 1 PH RAM 5 PC BYPASS ON
PH1305R5_CLOSED | Kiln1 | KILN 1 PH RAM 5 CLOSED | None | PLC_DISCREAD | I:42/04 | KILN 1 PH RAM 5 CLOSED
PH1305R5_CLOSING | Kiln1 | KILN 1 PH RAM 5 CLOSING | None | PLC_DISCREAD | O:44/04 | KILN 1 PH RAM 5 CLOSING
PH1305R5_DBL | Kiln1 | KILN 1 PH RAM 5 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/591 | KILN 1 PH RAM 5 PC DOUBLE STROKE ON
PH1305R5_OPENING | Kiln1 | KILN 1 PH RAM 5 OPENING | None | PLC_DISCREAD | B101/8 | KILN 1 PH RAM 5 OPENING
PH1305R5_PIN | Kiln1 | PH 1-305 RAM 5 PINNED | On | PLC_DISCWRITE | B100/354 | PH 1-305 RAM 5 PINNED
PH1305R5_SSW | Kiln1 | KILN 1 PH RAM 5 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/04 | KILN 1 PH RAM 5 MANUAL BYPASS ON
PH1305R5CLOSE_ALM | Kiln1 | KILN 1 PH RAM #5 CLOSING ALARM | On | PLC_ALARM | B101:2/13 | KILN 1 PH RAM #5 CLOSING ALARM
PH1305R5OPEN_ALM | Kiln1 | KILN 1 PH RAM #5 OPENING ALARM | On | PLC_ALARM | B101:3/11 | KILN 1 PH RAM #5 OPENING ALARM
PH1305R6_BYP | Kiln1 | KILN 1 PH RAM 6 PC BYPASS ON | On | PLC_DISCWRITE | B100/592 | KILN 1 PH RAM 6 PC BYPASS ON
PH1305R6_CLOSED | Kiln1 | KILN 1 PH RAM 6 CLOSED | None | PLC_DISCREAD | I:42/005 | KILN 1 PH RAM 6 CLOSED
PH1305R6_CLOSING | Kiln1 | KILN 1 PH RAM 6 CLOSING | None | PLC_DISCREAD | O:44/005 | KILN 1 PH RAM 6 CLOSING
PH1305R6_DBL | Kiln1 | KILN 1 PH RAM 6 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/593 | KILN 1 PH RAM 6 PC DOUBLE STROKE ON
PH1305R6_OPENING | Kiln1 | KILN 1 PH RAM 6 OPENING | None | PLC_DISCREAD | B101/009 | KILN 1 PH RAM 6 OPENING
PH1305R6_PIN | Kiln1 | PH 1-305 RAM 6 PINNED | On | PLC_DISCWRITE | B100/360 | PH 1-305 RAM 6 PINNED
PH1305R6_SSW | Kiln1 | KILN 1 PH RAM 6 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/005 | KILN 1 PH RAM 6 MANUAL BYPASS ON
PH1305R6CLOSE_ALM | Kiln1 | KILN 1 PH RAM #6 CLOSING ALARM | On | PLC_ALARM | B101:2/14 | KILN 1 PH RAM #6 CLOSING ALARM
PH1305R6OPEN_ALM | Kiln1 | KILN 1 PH RAM #6 OPENING ALARM | On | PLC_ALARM | B101:3/12 | KILN 1 PH RAM #6 OPENING ALARM
PH1305R7_BYP | Kiln1 | KILN 1 PH RAM 7 PC BYPASS ON | On | PLC_DISCWRITE | B100/594 | KILN 1 PH RAM 7 PC BYPASS ON
PH1305R7_CLOSED | Kiln1 | KILN 1 PH RAM 7 CLOSED | None | PLC_DISCREAD | I:42/06 | KILN 1 PH RAM 7 CLOSED
PH1305R7_CLOSING | Kiln1 | KILN 1 PH RAM 7 CLOSING | None | PLC_DISCREAD | O:44/06 | KILN 1 PH RAM 7 CLOSING
PH1305R7_DBL | Kiln1 | KILN 1 PH RAM 7 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/595 | KILN 1 PH RAM 7 PC DOUBLE STROKE ON
PH1305R7_OPENING | Kiln1 | KILN 1 PH RAM 7 OPENING | None | PLC_DISCREAD | B101/10 | KILN 1 PH RAM 7 OPENING
PH1305R7_PIN | Kiln1 | PH 1-305 RAM 7 PINNED | On | PLC_DISCWRITE | B100/361 | PH 1-305 RAM 7 PINNED
PH1305R7_SSW | Kiln1 | KILN 1 PH RAM 7 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/06 | KILN 1 PH RAM 7 MANUAL BYPASS ON
PH1305R7CLOSE_ALM | Kiln1 | KILN 1 PH RAM #7 CLOSING ALARM | On | PLC_ALARM | B101:2/15 | KILN 1 PH RAM #7 CLOSING ALARM
PH1305R7OPEN_ALM | Kiln1 | KILN 1 PH RAM #7 OPENING ALARM | On | PLC_ALARM | B101:3/13 | KILN 1 PH RAM #7 OPENING ALARM
PH1305R8_BYP | Kiln1 | KILN 1 PH RAM 8 PC BYPASS ON | On | PLC_DISCWRITE | B100/596 | KILN 1 PH RAM 8 PC BYPASS ON
PH1305R8_CLOSED | Kiln1 | KILN 1 PH RAM 8 CLOSED | None | PLC_DISCREAD | I:42/007 | KILN 1 PH RAM 8 CLOSED
PH1305R8_CLOSING | Kiln1 | KILN 1 PH RAM 8 CLOSING | None | PLC_DISCREAD | O:44/007 | KILN 1 PH RAM 8 CLOSING
PH1305R8_DBL | Kiln1 | KILN 1 PH RAM 8 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/597 | KILN 1 PH RAM 8 PC DOUBLE STROKE ON
PH1305R8_OPENING | Kiln1 | KILN 1 PH RAM 8 OPENING | None | PLC_DISCREAD | B101/011 | KILN 1 PH RAM 8 OPENING
PH1305R8_PIN | Kiln1 | PH 1-305 RAM 8 PINNED | On | PLC_DISCWRITE | B100/362 | PH 1-305 RAM 8 PINNED
PH1305R8_SSW | Kiln1 | KILN 1 PH RAM 8 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/007 | KILN 1 PH RAM 8 MANUAL BYPASS ON
PH1305R8CLOSE_ALM | Kiln1 | KILN 1 PH RAM #8 CLOSING ALARM | On | PLC_ALARM | B101:3/0 | KILN 1 PH RAM #8 CLOSING ALARM
PH1305R8OPEN_ALM | Kiln1 | KILN 1 PH RAM #8 OPENING ALARM | On | PLC_ALARM | B101:3/14 | KILN 1 PH RAM #8 OPENING ALARM
PH1305R9_BYP | Kiln1 | KILN 1 PH RAM 9 PC BYPASS ON | On | PLC_DISCWRITE | B100/598 | KILN 1 PH RAM 9 PC BYPASS ON
PH1305R9_CLOSED | Kiln1 | KILN 1 PH RAM 9 CLOSED | None | PLC_DISCREAD | I:42/10 | KILN 1 PH RAM 9 CLOSED
PH1305R9_CLOSING | Kiln1 | KILN 1 PH RAM 9 CLOSING | None | PLC_DISCREAD | O:44/10 | KILN 1 PH RAM 9 CLOSING
PH1305R9_DBL | Kiln1 | KILN 1 PH RAM 9 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/599 | KILN 1 PH RAM 9 PC DOUBLE STROKE ON
PH1305R9_OPENING | Kiln1 | KILN 1 PH RAM 9 OPENING | None | PLC_DISCREAD | B101/12 | KILN 1 PH RAM 9 OPENING
PH1305R9_PIN | Kiln1 | PH 1-305 RAM 9 PINNED | On | PLC_DISCWRITE | B100/367 | PH 1-305 RAM 9 PINNED
PH1305R9_SSW | Kiln1 | KILN 1 PH RAM 9 MANUAL BYPASS ON | Off | PLC_ALARM | I:43/10 | KILN 1 PH RAM 9 MANUAL BYPASS ON
PH1305R9CLOSE_ALM | Kiln1 | KILN 1 PH RAM #9 CLOSING ALARM | On | PLC_ALARM | B101:3/1 | KILN 1 PH RAM #9 CLOSING ALARM
PH1305R9OPEN_ALM | Kiln1 | KILN 1 PH RAM #9 OPENING ALARM | On | PLC_ALARM | B101:3/15 | KILN 1 PH RAM #9 OPENING ALARM
PH1305RAM# | Kiln1 | PH 1-305 ACTIVE RAM # |  | 14 | 1 | 0 | 0 | PLC_INTREAD | N7:42 | PH 1-305 ACTIVE RAM #
PH1305STROKE_SP | Kiln1 | PH 1-305 STROKE RATE PC SETPOINT | STR/HR | 250 | 1 | 0 | 1 | PLC_INTWRITE | N102:43 | PH 1-305 STROKE RATE PC SETPOINT
PH1306_2_TT_AH | Kiln1 | Kiln 1 Preheater Outlet Temp Hi Alarm | On | PLC_ALARM | B3/1259 | Kiln 1 Preheater Outlet Temp Hi Alarm
PH1306PT_1 | Kiln1 | PH 1-306 INLET PRESSURE | " WC | 5 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:171 | PH 1-306 INLET PRESSURE
PH1306PT_2 | Kiln1 | PH 1-306 OUTLET PRESSURE | " WC | 60 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:172 | PH 1-306 OUTLET PRESSURE
PH1306TT_1 | Kiln1 | PH 1-306 INLET TEMP | °F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N60:7 | PH 1-306 INLET TEMP
PH1306TT_1_STREND | Kiln1 | KILN 1 PREHEATER INLET TEMPERATURE |  | 2300 | 5 | 0 | KILN 1 PREHEATER INLET TEMPERATURE | 0 | 0 | 0
PH1306TT_1_TREND | Kiln1 | KILN 1 PREHEATER INLET TEMPERATURE |  | 2400 | 5 | 0 | KILN 1 PREHEATER INLET TEMPERATURE | 0 | 0 | 0
PH1306TT_2 | Kiln1 | PH 1-306 OUTLET TEMP | °F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N59:02 | PH 1-306 OUTLET TEMP
PH1306TT_2_TREND | Kiln1 | KILN 1 PREHEATER OUTLET TEMPERATURE |  | 800 | 5 | 0 | KILN 1 PREHEATER OUTLET TEMPERATURE | 0 | 0 | 0
PH1RA_P1 | Kiln1 | PREHEATER #1 STROKES/HOUR REGISTER | ST/HR | 9999 | 1 | 0 | 0 | PLC_INTREAD | N7:22 | PREHEATER #1 STROKES/HOUR REGISTER
PM1305_PBS | Kiln1 | PM 1-305 PC START | None | PLC_DISCWRITE | B100/147 | PM 1-305 PC START
PM1305_PBT | Kiln1 | PM 1-305 PC STOP | None | PLC_DISCWRITE | B100/148 | PM 1-305 PC STOP
PM13051_FTS | Kiln1 | PM 1-305-1 FAILED TO START | On | PLC_ALARM | B101/197 | PM 1-305-1 FAILED TO START
PM13051_IM | Kiln1 | PM 1305-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/66 | PM 1305-1 INTERLOCKS MET
PM13051_PT | Kiln1 | PM 1-305-1 PRESSURE | PSI | 3000 | 5 | 0 | 0 | PLC_FLTREAD | F9:02 | PM 1-305-1 PRESSURE
PM13051_SSA_HMI | Kiln1 | PM1305_1 hydralic pump 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1300 | PM1305_1 hydralic pump 0=Auto 1=Man
PM13051_SSW | Kiln1 | PM 1305-1 AUTO ON | None | PLC_DISCREAD | I:44/00 | PM 1305-1 AUTO ON
PM13051DEADHEAD_ALM | Kiln1 | KILN 1 PM 1305-1 DEAD HEADED | On | PLC_ALARM | B101/20 | KILN 1 PM 1305-1 DEAD HEADED
PM13051MS_X | Kiln1 | PREHEATER #1 HYD PUMP 1 STATUS-ON | Off | PLC_DISCREAD | I:025/04 | PM 1-305-1 STOPPED
PM13052_FTS | Kiln1 | PM 1-305-2 FAILED TO START | On | PLC_ALARM | B101/198 | PM 1-305-2 FAILED TO START
PM13052_IM | Kiln1 | PM 1305-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/67 | PM 1305-2 INTERLOCKS MET
PM13052_PT | Kiln1 | PM 1-305-2 PRESSURE | PSI | 3000 | 5 | 0 | 0 | PLC_FLTREAD | F9:03 | PM 1-305-2 PRESSURE
PM13052_SSA_HMI | Kiln1 | PM1305_2 hydralic pump 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1305 | PM1305_2 hydralic pump 0=Auto 1=Man
PM13052_SSW | Kiln1 | PM 1305-2 AUTO ON | None | PLC_DISCREAD | I:44/01 | PM 1305-2 AUTO ON
PM13052DEADHEAD_ALM | Kiln1 | KILN 1 PM 1305-2 DEAD HEADED | On | PLC_ALARM | B101/21 | KILN 1 PM 1305-2 DEAD HEADED
PM13052MS_X | Kiln1 | PM 1305-2 AUX CONTACT | Off | PLC_DISCREAD | I:025/03 | PM 1-305-2 STOPPED
PM1313D_LAST | Kiln1 | PM 1-313-D1&2 LAST PUMP TO RUN | None | PLC_DISCREAD | B3/547 | PM 1-313-D1&2 LAST PUMP TO RUN
PM1313D1_AUTO | Kiln1 | PM 1-313-D1 IN AUTO POSITION | None | PLC_DISCREAD | I:73/6 | PM 1-313-D1 IN AUTO POSITION
PM1313D1_DISC | Kiln1 | PM 1-313-D1 DISCONNECT | None | PLC_DISCREAD | I:73/7 | PM 1-313-D1 DISCONNECT
PM1313D1_IM | Kiln1 | PM 1-313-D1 INTERLOCKS MET | None | PLC_DISCREAD | B3/281 | PM 1-313-D1 INTERLOCKS MET
PM1313D1_IT | Kiln1 | PM 1-313-D1 AMPS | AMPS | 15 | 0.25 | 0 | 0 | PLC_FLTREAD | F9:306 | PM 1-313-D1 AMPS
PM1313D1_PBS | Kiln1 | PM 1-313-D1 PC START | None | PLC_DISCWRITE | B100/399 | PM 1-313-D1 PC START
PM1313D1_PBT | Kiln1 | PM 1-313-D1 PC STOP | None | PLC_DISCWRITE | B100/398 | PM 1-313-D1 PC STOP
PM1313D1FTS_ALM | Kiln1 | PM 1-313-D1 FAILED TO START | On | PLC_ALARM | B101/223 | PM 1-313-D1 FAILED TO START
PM1313D1MS_X | Kiln1 | PM 1-313-D1 AUX FDBK | Off | PLC_DISCREAD | I:73/10 | PM 1-313-D1 STOPPED
PM1313D2_AUTO | Kiln1 | PM 1-313-D2 IN AUTO POSITION | None | PLC_DISCREAD | I:73/11 | PM 1-313-D2 IN AUTO POSITION
PM1313D2_DISC | Kiln1 | PM 1-313-D2 DISCONNECT | None | PLC_DISCREAD | I:73/12 | PM 1-313-D2 DISCONNECT
PM1313D2_IM | Kiln1 | PM 1-313-D2 INTERLOCKS MET | None | PLC_DISCREAD | B3/545 | PM 1-313-D2 INTERLOCKS MET
PM1313D2_IT | Kiln1 | PM 1-313-D2 AMPS | AMPS | 15 | 0.25 | 0 | 0 | PLC_FLTREAD | F9:307 | PM 1-313-D2 AMPS
PM1313D2_PBS | Kiln1 | PM 1-313-D2 PC START | None | PLC_DISCWRITE | B100/474 | PM 1-313-D2 PC START
PM1313D2_PBT | Kiln1 | PM 1-313-D2 PC STOP | None | PLC_DISCWRITE | B100/473 | PM 1-313-D2 PC STOP
PM1313D2FTS_ALM | Kiln1 | PM 1-313-D2 FAILED TO START | On | PLC_ALARM | B101/224 | PM 1-313-D2 FAILED TO START
PM1313D2MS_X | Kiln1 | PM 1-313-D2 AUX FDBK | Off | PLC_DISCREAD | I:73/13 | PM 1-313-D2 STOPPED
PM1314A_IM | Kiln1 | PM 1-314-A INTERLOCKS MET | None | PLC_DISCREAD | B3/266 | PM 1-314-A INTERLOCKS MET
PM1314A_PBS | Kiln1 | PM 1-314-A PC START | None | PLC_DISCWRITE | B100/380 | PM 1-314-A PC START
PM1314A_PBT | Kiln1 | PM 1-314-A PC STOP | None | PLC_DISCWRITE | B100/359 | PM 1-314-A PC STOP
PM1314AFTS_ALM | Kiln1 | PM 1-314-A FAILED TO START | On | PLC_ALARM | B101/234 | PM 1-314-A FAILED TO START
PM1314AMS_X | Kiln1 | PM 1-314-A AUX FDBK | Off | PLC_DISCREAD | I:25/11 | PM 1-314-A STOPPED
PM1326_LAST | Kiln1 | PM 1-326 LAST PUMP ON | None | PLC_DISCREAD | B100/528 | PM 1-326 LAST PUMP ON
PM16021_IM | Kiln1 | PM 1-602-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/1523 | PM 1-602-1 INTERLOCKS MET
PM16021_PBS | Kiln1 | PM 1-602-1 PC START | None | PLC_DISCWRITE | B100/898 | PM 1-602-1 PC START
PM16021_PBT | Kiln1 | PM 1-602-1 PC STOP | None | PLC_DISCWRITE | B100/896 | PM 1-602-1 PC STOP
PM16021_TT | Kiln1 | PM 1-602-1 LUBE TEMPERATURE | °F | 1000 | 2 | 0 | 0 | PLC_INTREAD | N57:7 | PM 1-602-1 TEMPERATURE
PM16021FTS_ALM | Kiln1 | PM 1-602-1 FAILED TO START | On | PLC_ALARM | B101/592 | PM 1-602-1 FAILED TO START
PM16021MS_X | Kiln1 | PM 1-602-1 AUX FDBK | Off | PLC_DISCREAD | I:107/14 | PM 1-602-1 STOPPED
PM16022_IM | Kiln1 | PM 1-602-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/1523 | PM 1-602-2 INTERLOCKS MET
PM16022_PBS | Kiln1 | PM 1-602-2 PC START | None | PLC_DISCWRITE | B100/899 | PM 1-602-2 PC START
PM16022_PBT | Kiln1 | PM 1-602-2 PC STOP | None | PLC_DISCWRITE | B100/897 | PM 1-602-2 PC STOP
PM16022_TT | Kiln1 | PM 1-602-2 LUBE TEMPERATURE | °F | 1000 | 2 | 0 | 0 | PLC_INTREAD | N57:6 | PM 1-602-2 TEMPERATURE
PM16022FTS_ALM | Kiln1 | PM 1-602-2 FAILED TO START | On | PLC_ALARM | B101/593 | PM 1-602-2 FAILED TO START
PM16022MS_X | Kiln1 | PM 1-602-2 AUX FDBK | Off | PLC_DISCREAD | I:107/15 | PM 1-602-2 STOPPED
PM4610_K1FLOW | Kiln1 | PM 610-1&2 #2 DIESEL TO KILN 1 | GPM | 35 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:153 | PM 610-1&2 #2 DIESEL TO KILN 1
PM4610_K1TOT | Kiln1 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 1 | GAL | 50000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:387 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 1
PM4610_K1TOTYEST | Kiln1 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 1 YESTERDAY | GAL | 50000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:389 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 1 YESTERDAY
PM4610_K2FLOW | Kiln1 | PM 610-1&2 #2 DIESEL TO KILN 2 | GPM | 35 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:151 | PM 610-1&2 #2 DIESEL TO KILN 2
PM4610_K2TOT | Kiln1 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 2 | GAL | 50000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:367 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 2
PM4610_K2TOTYEST | Kiln1 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 2 YESTERDAY | GAL | 50000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:390 | PM 610-1&2 #2 TOTAL DIESEL TO KILN 2 YESTERDAY
PM4610SEL_K1 | Kiln1 | PM 610 SELECT KILN 1 FOR DIESEL FEED | None | PLC_DISCWRITE | B100/520 | PM 610 SELECT KILN 1 FOR DIESEL FEED
RA1319MS_X | Kiln1 | RA 1-319 AUX FDBK | Off | PLC_DISCREAD | I:24/04 | RA 1-319 STOPPED
RA1604_IM | Kiln1 | RA 1604 INTERLOCKS MET | None | PLC_DISCREAD | B3/255 | RA 1604 INTERLOCKS MET
RA1604_PBS | Kiln1 | RA 1-604 PC START | None | PLC_DISCWRITE | B100/523 | RA 1-604 PC START
RA1604_PBT | Kiln1 | RA 1-604 PC STOP | None | PLC_DISCWRITE | B100/524 | RA 1-604 PC STOP
RA1604_SSA_HMI | Kiln1 | RA1-604 Coal classifier rotary airlock0=Auto 1=Man | None | PLC_DISCWRITE | b3/1340 | RA1-604 Coal classifier rotary airlock 0=Auto 1=Man
RA1604FTS_ALM | Kiln1 | RA 1-604 FAILED TO START | On | PLC_ALARM | B101/258 | RA 1-604 FAILED TO START
RA1604MS_X | Kiln1 | RA 1-604 FDBK | Off | PLC_DISCREAD | I:106/05 | RA 1-604 STOPPED
RATE_K1LIME | Kiln1 | KILN 1 LIME PRODUCTION RATE | TPH | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:231 | KILN 1 LIME PRODUCTION RATE
RK1313_EN | Kiln1 | RK 1-313 ENABLED TO RUN | None | PLC_DISCWRITE | B100/114 | RK 1-313 ENABLED TO RUN
RK1313_IM | Kiln1 | RK 1-313 INTERLOCKS MET | None | PLC_DISCREAD | B3/726 | RK 1-313 INTERLOCKS MET
RK1313_RAKE# | Kiln1 | KILN 1 GRAVEL BED ACTIVE RAKE MODULE # | MODULE | 10 | 0 | 0 | 0 | PLC_INTREAD | N7:63 | KILN 1 GRAVEL BED ACTIVE RAKE MODULE #
RK13131_AUTO | Kiln1 | RK 1-313-1 IN AUTO POSITION | None | PLC_DISCREAD | I:73/14 | RK 1-313-1 IN AUTO POSITION
RK13131_DISC | Kiln1 | RK 1-313-1 DISCONNECT | None | PLC_DISCREAD | I:73/15 | RK 1-313-1 DISCONNECT
RK13131_IM | Kiln1 | RK 1-313-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/360 | RK 1-313-1 INTERLOCKS MET
RK13131_IT | Kiln1 | RK 1-313-1 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:308 | RK 1-313-1 AMPS
RK13131_MSBYP | Kiln1 | RK 1-313-1 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/323 | RK 1-313-1 MOTION SWITCH BYPASSED
RK13131_STARTTM | Kiln1 | RK 1-313-1 DELAY START TIMER DN | None | PLC_DISCREAD | T4:530.DN | RK 1-313-1 DELAY START TIMER DN
RK13131_TOTTM | Kiln1 | RK 1-313-1 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:540.DN | RK 1-313-1 RUN TIMER RUNNING
RK131310_AUTO | Kiln1 | RK 1-313-10 IN AUTO POSITION | None | PLC_DISCREAD | I:76/00 | RK 1-313-10 IN AUTO POSITION
RK131310_DISC | Kiln1 | RK 1-313-10 DISCONNECT | None | PLC_DISCREAD | I:76/01 | RK 1-313-10 DISCONNECT
RK131310_IM | Kiln1 | RK 1-313-10 INTERLOCKS MET | None | PLC_DISCREAD | B3/484 | RK 1-313-10 INTERLOCKS MET
RK131310_IT | Kiln1 | RK 1-313-10 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:317 | RK 1-313-10 AMPS
RK131310_MSBYP | Kiln1 | RK 1-313-10 MOTION SWITCH BYPASSED | On | PLC_DISCREAD | B100/469 | RK 1-313-10 MOTION SWITCH BYPASSED
RK131310_STARTTM | Kiln1 | RK 1-313-10 DELAY START TIMER DN | None | PLC_DISCREAD | T4:539.DN | RK 1-313-10 DELAY START TIMER DN
RK131310_TOTTM | Kiln1 | RK 1-313-10 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:549.DN | RK 1-313-10 RUN TIMER RUNNING
RK131310FTS_ALM | Kiln1 | RK 1-313-10 FAILED TO START! | On | PLC_ALARM | B101/219 | RK 1-313-10 FAILED TO START!
RK131310MS_X | Kiln1 | RK 1-313-10 AUX FDBK | None | PLC_DISCREAD | I:076/02 | RK 1-313-10 AUX FDBK
RK131310MSF_ALM | Kiln1 | RK 1-313-10 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/220 | RK 1-313-10 MOTION SWITCH FAILURE!
RK131310OFF_ALM | Kiln1 | RK 1-313-10 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/160 | RK 1-313-10 IN STARTER OFF OR TRIPPED
RK13131FTS_ALM | Kiln1 | RK 1-313-1 FAILED TO START! | On | PLC_ALARM | B101/201 | RK 1-313-1 FAILED TO START!
RK13131MS_X | Kiln1 | RK 1-313-1 AUX FDBK | None | PLC_DISCREAD | I:073/16 | RK 1-313-1 AUX FDBK
RK13131MSF_ALM | Kiln1 | RK 1-313-1 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/202 | RK 1-313-1 MOTION SWITCH FAILURE!
RK13131OFF_ALM | Kiln1 | RK 1-313-1 STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/151 | RK 1-313-1 STARTER OFF OR TRIPPED
RK13132_AUTO | Kiln1 | RK 1-313-2 IN AUTO POSITION | None | PLC_DISCREAD | I:74/0 | RK 1-313-2 IN AUTO POSITION
RK13132_DISC | Kiln1 | RK 1-313-2 DISCONNECT | None | PLC_DISCREAD | I:74/01 | RK 1-313-2 DISCONNECT
RK13132_IM | Kiln1 | RK 1-313-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/276 | RK 1-313-2 INTERLOCKS MET
RK13132_IT | Kiln1 | RK 1-313-2 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:309 | RK 1-313-2 AMPS
RK13132_MSBYP | Kiln1 | RK 1-313-2 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/324 | RK 1-313-2 MOTION SWITCH BYPASSED
RK13132_STARTTM | Kiln1 | RK 1-313-2 DELAY START TIMER DN | None | PLC_DISCREAD | T4:531.DN | RK 1-313-2 DELAY START TIMER DN
RK13132_TOTTM | Kiln1 | RK 1-313-2 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:541.DN | RK 1-313-2 RUN TIMER RUNNING
RK13132FTS_ALM | Kiln1 | RK 1-313-2 FAILED TO START! | On | PLC_ALARM | B101/203 | RK 1-313-2 FAILED TO START!
RK13132MS_X | Kiln1 | RK 1-313-2 AUX FDBK | None | PLC_DISCREAD | I:074/02 | RK 1-313-2 AUX FDBK
RK13132MSF_ALM | Kiln1 | RK 1-313-2 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/204 | RK 1-313-2 MOTION SWITCH FAILURE!
RK13132OFF_ALM | Kiln1 | RK 1-313-2 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/152 | RK 1-313-2 IN STARTER OFF OR TRIPPED
RK13133_AUTO | Kiln1 | RK 1-313-3 IN AUTO POSITION | None | PLC_DISCREAD | I:74/4 | RK 1-313-3 IN AUTO POSITION
RK13133_DISC | Kiln1 | RK 1-313-3 DISCONNECT | None | PLC_DISCREAD | I:74/05 | RK 1-313-3 DISCONNECT
RK13133_IM | Kiln1 | RK 1-313-3 INTERLOCKS MET | None | PLC_DISCREAD | B3/339 | RK 1-313-3 INTERLOCKS MET
RK13133_IT | Kiln1 | RK 1-313-3 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:310 | RK 1-313-3 AMPS
RK13133_MSBYP | Kiln1 | RK 1-313-3 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/325 | RK 1-313-3 MOTION SWITCH BYPASSED
RK13133_STARTTM | Kiln1 | RK 1-313-3 DELAY START TIMER DN | None | PLC_DISCREAD | T4:532.DN | RK 1-313-3 DELAY START TIMER DN
RK13133_TOTTM | Kiln1 | RK 1-313-3 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:542.DN | RK 1-313-3 RUN TIMER RUNNING
RK13133FTS_ALM | Kiln1 | RK 1-313-3 FAILED TO START! | On | PLC_ALARM | B101/205 | RK 1-313-3 FAILED TO START!
RK13133MS_X | Kiln1 | RK 1-313-3 AUX FDBK | None | PLC_DISCREAD | I:074/06 | RK 1-313-3 AUX FDBK
RK13133MSF_ALM | Kiln1 | RK 1-313-3 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/206 | RK 1-313-3 MOTION SWITCH FAILURE!
RK13133OFF_ALM | Kiln1 | RK 1-313-3 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/153 | RK 1-313-3 IN STARTER OFF OR TRIPPED
RK13134_AUTO | Kiln1 | RK 1-313-4 IN AUTO POSITION | None | PLC_DISCREAD | I:74/10 | RK 1-313-4 IN AUTO POSITION
RK13134_DISC | Kiln1 | RK 1-313-4 DISCONNECT | None | PLC_DISCREAD | I:74/11 | RK 1-313-4 DISCONNECT
RK13134_IM | Kiln1 | RK 1-313-4 INTERLOCKS MET | None | PLC_DISCREAD | B3/363 | RK 1-313-4 INTERLOCKS MET
RK13134_IT | Kiln1 | RK 1-313-4 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:311 | RK 1-313-4 AMPS
RK13134_MSBYP | Kiln1 | RK 1-313-4 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/326 | RK 1-313-4 MOTION SWITCH BYPASSED
RK13134_STARTTM | Kiln1 | RK 1-313-4 DELAY START TIMER DN | None | PLC_DISCREAD | T4:533.DN | RK 1-313-4 DELAY START TIMER DN
RK13134_TOTTM | Kiln1 | RK 1-313-4 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:543.DN | RK 1-313-4 RUN TIMER RUNNING
RK13134FTS_ALM | Kiln1 | RK 1-313-4 FAILED TO START! | On | PLC_ALARM | B101/207 | RK 1-313-4 FAILED TO START!
RK13134MS_X | Kiln1 | RK 1-313-4 AUX FDBK | None | PLC_DISCREAD | I:074/12 | RK 1-313-4 AUX FDBK
RK13134MSF_ALM | Kiln1 | RK 1-313-4 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/208 | RK 1-313-4 MOTION SWITCH FAILURE!
RK13134OFF_ALM | Kiln1 | RK 1-313-4 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/154 | RK 1-313-4 IN STARTER OFF OR TRIPPED
RK13135_AUTO | Kiln1 | RK 1-313-5 IN AUTO POSITION | None | PLC_DISCREAD | I:74/14 | RK 1-313-5 IN AUTO POSITION
RK13135_DISC | Kiln1 | RK 1-313-5 DISCONNECT | None | PLC_DISCREAD | I:74/15 | RK 1-313-5 DISCONNECT
RK13135_IM | Kiln1 | RK 1-313-5 INTERLOCKS MET | None | PLC_DISCREAD | B3/381 | RK 1-313-5 INTERLOCKS MET
RK13135_IT | Kiln1 | RK 1-313-5 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:312 | RK 1-313-5 AMPS
RK13135_MSBYP | Kiln1 | RK 1-313-5 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/327 | RK 1-313-5 MOTION SWITCH BYPASSED
RK13135_STARTTM | Kiln1 | RK 1-313-5 DELAY START TIMER DN | None | PLC_DISCREAD | T4:534.DN | RK 1-313-5 DELAY START TIMER DN
RK13135_TOTTM | Kiln1 | RK 1-313-5 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:544.DN | RK 1-313-5 RUN TIMER RUNNING
RK13135FTS_ALM | Kiln1 | RK 1-313-5 FAILED TO START! | On | PLC_ALARM | B101/209 | RK 1-313-5 FAILED TO START!
RK13135MS_X | Kiln1 | RK 1-313-5 AUX FDBK | None | PLC_DISCREAD | I:074/16 | RK 1-313-5 AUX FDBK
RK13135MSF_ALM | Kiln1 | RK 1-313-5 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/210 | RK 1-313-5 MOTION SWITCH FAILURE!
RK13135OFF_ALM | Kiln1 | RK 1-313-5 STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/155 | RK 1-313-5 STARTER OFF OR TRIPPED
RK13136_AUTO | Kiln1 | RK 1-313-6 IN AUTO POSITION | None | PLC_DISCREAD | I:75/00 | RK 1-313-6 IN AUTO POSITION
RK13136_DISC | Kiln1 | RK 1-313-6 DISCONNECT | None | PLC_DISCREAD | I:75/01 | RK 1-313-6 DISCONNECT
RK13136_IM | Kiln1 | RK 1-313-6 INTERLOCKS MET | None | PLC_DISCREAD | B3/382 | RK 1-313-6 INTERLOCKS MET
RK13136_IT | Kiln1 | RK 1-313-6 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:313 | RK 1-313-6 AMPS
RK13136_MSBYP | Kiln1 | RK 1-313-6 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/352 | RK 1-313-6 MOTION SWITCH BYPASSED
RK13136_STARTTM | Kiln1 | RK 1-313-6 DELAY START TIMER DN | None | PLC_DISCREAD | T4:535.DN | RK 1-313-6 DELAY START TIMER DN
RK13136_TOTTM | Kiln1 | RK 1-313-6 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:545.DN | RK 1-313-6 RUN TIMER RUNNING
RK13136FTS_ALM | Kiln1 | RK 1-313-6 FAILED TO START! | On | PLC_ALARM | B101/211 | RK 1-313-6 FAILED TO START!
RK13136MS_X | Kiln1 | RK 1-313-6 AUX FDBK | None | PLC_DISCREAD | I:075/02 | RK 1-313-6 AUX FDBK
RK13136MSF_ALM | Kiln1 | RK 1-313-6 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/212 | RK 1-313-6 MOTION SWITCH FAILURE!
RK13136OFF_ALM | Kiln1 | RK 1-313-6 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/156 | RK 1-313-6 IN STARTER OFF OR TRIPPED
RK13137_AUTO | Kiln1 | RK 1-313-7 IN AUTO POSITION | None | PLC_DISCREAD | I:75/04 | RK 1-313-7 IN AUTO POSITION
RK13137_DISC | Kiln1 | RK 1-313-7 DISCONNECT | None | PLC_DISCREAD | I:75/05 | RK 1-313-7 DISCONNECT
RK13137_IM | Kiln1 | RK 1-313-7 INTERLOCKS MET | None | PLC_DISCREAD | B3/450 | RK 1-313-7 INTERLOCKS MET
RK13137_IT | Kiln1 | RK 1-313-7 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:314 | RK 1-313-7 AMPS
RK13137_MSBYP | Kiln1 | RK 1-313-7 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/353 | RK 1-313-7 MOTION SWITCH BYPASSED
RK13137_STARTTM | Kiln1 | RK 1-313-7 DELAY START TIMER DN | None | PLC_DISCREAD | T4:536.DN | RK 1-313-7 DELAY START TIMER DN
RK13137_TOTTM | Kiln1 | RK 1-313-7 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:546.DN | RK 1-313-7 RUN TIMER RUNNING
RK13137FTS_ALM | Kiln1 | RK 1-313-7 FAILED TO START! | On | PLC_ALARM | B101/213 | RK 1-313-7 FAILED TO START!
RK13137MS_X | Kiln1 | RK 1-313-7 AUX FDBK | None | PLC_DISCREAD | I:075/06 | RK 1-313-7 AUX FDBK
RK13137MSF_ALM | Kiln1 | RK 1-313-7 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/214 | RK 1-313-7 MOTION SWITCH FAILURE!
RK13137OFF_ALM | Kiln1 | RK 1-313-7 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/157 | RK 1-313-7 IN STARTER OFF OR TRIPPED
RK13138_AUTO | Kiln1 | RK 1-313-8 IN AUTO POSITION | None | PLC_DISCREAD | I:75/10 | RK 1-313-8 IN AUTO POSITION
RK13138_DISC | Kiln1 | RK 1-313-8 DISCONNECT | None | PLC_DISCREAD | I:75/11 | RK 1-313-8 DISCONNECT
RK13138_IM | Kiln1 | RK 1-313-8 INTERLOCKS MET | None | PLC_DISCREAD | B3/454 | RK 1-313-8 INTERLOCKS MET
RK13138_IT | Kiln1 | RK 1-313-8 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:315 | RK 1-313-8 AMPS
RK13138_MSBYP | Kiln1 | RK 1-313-8 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/383 | RK 1-313-8 MOTION SWITCH BYPASSED
RK13138_STARTTM | Kiln1 | RK 1-313-8 DELAY START TIMER DN | None | PLC_DISCREAD | T4:537.DN | RK 1-313-8 DELAY START TIMER DN
RK13138_TOTTM | Kiln1 | RK 1-313-8 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:547.DN | RK 1-313-8 RUN TIMER RUNNING
RK13138FTS_ALM | Kiln1 | RK 1-313-8 FAILED TO START! | On | PLC_ALARM | B101/215 | RK 1-313-8 FAILED TO START!
RK13138MS_X | Kiln1 | RK 1-313-8 AUX FDBK | None | PLC_DISCREAD | I:075/12 | RK 1-313-8 AUX FDBK
RK13138MSF_ALM | Kiln1 | RK 1-313-8 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/216 | RK 1-313-8 MOTION SWITCH FAILURE!
RK13138OFF_ALM | Kiln1 | RK 1-313-8 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/158 | RK 1-313-8 IN STARTER OFF OR TRIPPED
RK13139_AUTO | Kiln1 | RK 1-313-9 IN AUTO POSITION | None | PLC_DISCREAD | I:75/14 | RK 1-313-9 IN AUTO POSITION
RK13139_DISC | Kiln1 | RK 1-313-9 DISCONNECT | None | PLC_DISCREAD | I:75/15 | RK 1-313-9 DISCONNECT
RK13139_IM | Kiln1 | RK 1-313-9 INTERLOCKS MET | None | PLC_DISCREAD | B3/455 | RK 1-313-9 INTERLOCKS MET
RK13139_IT | Kiln1 | RK 1-313-9 AMPS | AMPS | 10 | 0.2 | 0 | 0 | PLC_FLTREAD | F9:316 | RK 1-313-9 AMPS
RK13139_MSBYP | Kiln1 | RK 1-313-9 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/387 | RK 1-313-9 MOTION SWITCH BYPASSED
RK13139_STARTTM | Kiln1 | RK 1-313-9 DELAY START TIMER DN | None | PLC_DISCREAD | T4:538.DN | RK 1-313-9 DELAY START TIMER DN
RK13139_TOTTM | Kiln1 | RK 1-313-9 RUN TIMER RUNNING | None | PLC_DISCREAD | T4:548.DN | RK 1-313-9 RUN TIMER RUNNING
RK13139FTS_ALM | Kiln1 | RK 1-313-9 FAILED TO START! | On | PLC_ALARM | B101/217 | RK 1-313-9 FAILED TO START!
RK13139MS_X | Kiln1 | RK 1-313-9 AUX FDBK | None | PLC_DISCREAD | I:075/16 | RK 1-313-9 AUX FDBK
RK13139MSF_ALM | Kiln1 | RK 1-313-9 MOTION SWITCH FAILURE! | On | PLC_ALARM | B101/218 | RK 1-313-9 MOTION SWITCH FAILURE!
RK13139OFF_ALM | Kiln1 | RK 1-313-9 IN STARTER OFF OR TRIPPED | On | PLC_ALARM | B101/159 | RK 1-313-9 IN STARTER OFF OR TRIPPED
SB1304HILEVEL_TIMER | Kiln1 | SB 1-304 HIGH LEVEL TIMER | SEC | 32000 | 0 | 0 | 0 | PLC_INTREAD | T4:100.ACC | SB 1-304 HIGH LEVEL TIMER
SB1304HL_ALM | Kiln1 | KILN 1 STONE BIN HIGH LEVEL! | On | PLC_ALARM | B101:2/2 | KILN 1 STONE BIN HIGH LEVEL!
SB1304HL1HR_ALM | Kiln1 | NO KILN 1 STONE BIN HIGH LEVEL FOR 1 HOUR! | On | PLC_ALARM | B101:2/3 | NO KILN 1 STONE BIN HIGH LEVEL FOR 1 HOUR!
SB1304LL_ALM | Kiln1 | KILN 1 STONE BIN LOW LEVEL ! | On | PLC_ALARM | B100/74 | KILN 1 STONE BIN LOW LEVEL !
SC1313A1_AUTO | Kiln1 | SC 1-313-A1 IN AUTO POSITION | None | PLC_DISCREAD | I:72/00 | SC 1-313-A1 IN AUTO POSITION
SC1313A1_DISC | Kiln1 | SC 1-313-A1 DISCONNECT | None | PLC_DISCREAD | I:72/01 | SC 1-313-A1 DISCONNECT
SC1313A1_IM | Kiln1 | SC 1-313-A1 INTERLOCKS MET | None | PLC_DISCREAD | B3/278 | SC 1-313-A1 INTERLOCKS MET
SC1313A1_PBS | Kiln1 | SC 1-313-A1 PC START | None | PLC_DISCWRITE | B100/393 | SC 1-313-A1 PC START
SC1313A1_PBT | Kiln1 | SC 1-313-A1 PC STOP | None | PLC_DISCWRITE | B100/392 | SC 1-313-A1 PC STOP
SC1313A1FTS_ALM | Kiln1 | SC 1-313-A1 FAILED TO START | On | PLC_ALARM | B101/225 | SC 1-313-A1 FAILED TO START
SC1313A1MS_BYP | Kiln1 | SC 1-313-A1 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/416 | SC 1-313-A1 MOTION SWITCH BYPASS
SC1313A1MS_X | Kiln1 | SC 1-313-A1 AUX FDBK | None | PLC_DISCREAD | I:72/02 | SC 1-313-A1 STOPPED
SC1313A1MSF_ALM | Kiln1 | SC 1-313-A1 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/226 | SC 1-313-A1 MOTION SWITCH FAILURE
SC1313A2_AUTO | Kiln1 | SC 1-313-A2 IN AUTO POSITION | None | PLC_DISCREAD | I:72/04 | SC 1-313-A2 IN AUTO POSITION
SC1313A2_DISC | Kiln1 | SC 1-313-A1 DISCONNECT | None | PLC_DISCREAD | I:72/05 | SC 1-313-A1 DISCONNECT
SC1313A2_IM | Kiln1 | SC 1-313-A2 INTERLOCKS MET | None | PLC_DISCREAD | B3/279 | SC 1-313-A2 INTERLOCKS MET
SC1313A2_PBS | Kiln1 | SC 1-313-A2 PC START | None | PLC_DISCWRITE | B100/395 | SC 1-313-A2 PC START
SC1313A2_PBT | Kiln1 | SC 1-313-A2 PC STOP | None | PLC_DISCWRITE | B100/394 | SC 1-313-A2 PC STOP
SC1313A2FTS_ALM | Kiln1 | SC 1-313-A2 FAILED TO START | On | PLC_ALARM | B101/227 | SC 1-313-A2 FAILED TO START
SC1313A2MS_BYP | Kiln1 | SC 1-313-A2 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/417 | SC 1-313-A2 MOTION SWITCH BYPASS
SC1313A2MS_X | Kiln1 | SC 1-313-A2 AUX FDBK | None | PLC_DISCREAD | I:72/6 | SC 1-313-A2 STOPPED
SC1313A2MSF_ALM | Kiln1 | SC 1-313-A2 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/228 | SC 1-313-A2 MOTION SWITCH FAILURE
SC1313A3_AUTO | Kiln1 | SC 1-313-A3 IN AUTO POSITION | None | PLC_DISCREAD | I:72/10 | SC 1-313-A3 IN AUTO POSITION
SC1313A3_DISC | Kiln1 | SC 1-313-A3 DISCONNECT | None | PLC_DISCREAD | I:72/11 | SC 1-313-A3 DISCONNECT
SC1313A3_IM | Kiln1 | SC 1-313-A3 INTERLOCKS MET | None | PLC_DISCREAD | B3/280 | SC 1-313-A3 INTERLOCKS MET
SC1313A3_PBS | Kiln1 | SC 1-313-A3 PC START | None | PLC_DISCWRITE | B100/397 | SC 1-313-A3 PC START
SC1313A3_PBT | Kiln1 | SC 1-313-A3 PC STOP | None | PLC_DISCWRITE | B100/396 | SC 1-313-A3 PC STOP
SC1313A3FTS_ALM | Kiln1 | SC 1-313-A3 FAILED TO START | On | PLC_ALARM | B101/229 | SC 1-313-A3 FAILED TO START
SC1313A3MS_BYP | Kiln1 | SC 1-313-A3 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/418 | SC 1-313-A3 MOTION SWITCH BYPASS
SC1313A3MS_X | Kiln1 | SC 1-313-A3 AUX FDBK | None | PLC_DISCREAD | I:72/12 | SC 1-313-A3 STOPPED
SC1313A3MSF_ALM | Kiln1 | SC 1-313-A3 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/230 | SC 1-313-A3 MOTION SWITCH FAILURE
SC1313B_AUTO | Kiln1 | SC 1-313-B IN AUTO POSITION | None | PLC_DISCREAD | I:72/14 | SC 1-313-B IN AUTO POSITION
SC1313B_DISC | Kiln1 | SC 1-313-B DISCONNECT | None | PLC_DISCREAD | I:72/15 | SC 1-313-B DISCONNECT
SC1313B_IM | Kiln1 | SC 1-313-B INTERLOCKS MET | None | PLC_DISCREAD | B3/277 | SC 1-313-B INTERLOCKS MET
SC1313B_PBS | Kiln1 | SC 1-313-B PC START | None | PLC_DISCWRITE | B100/391 | SC 1-313-B PC START
SC1313B_PBT | Kiln1 | SC 1-313-B PC STOP | None | PLC_DISCWRITE | B100/390 | SC 1-313-B PC STOP
SC1313BFTS_ALM | Kiln1 | SC 1-313-B FAILED TO START | On | PLC_ALARM | B101/231 | SC 1-313-B FAILED TO START
SC1313BMS_BYP | Kiln1 | SC 1-313-B MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/409 | SC 1-313-B MOTION SWITCH BYPASS
SC1313BMS_X | Kiln1 | SC 1-313-B AUX FDBK | None | PLC_DISCREAD | I:072/16 | SC 1-313-B STOPPED
SC1313BMSF_ALM | Kiln1 | SC 1-313-B MOTION SWITCH FAILURE | On | PLC_ALARM | B101/232 | SC 1-313-B MOTION SWITCH FAILURE
SC1316_IM | Kiln1 | SC 1-316 INTERLOCKS MET | None | PLC_DISCREAD | B3/273 | SC 1-316 INTERLOCKS MET
SC1316_PBS | Kiln1 | SC 1-316 PC START | None | PLC_ALARM | B100/370 | SC 1-316 PC START
SC1316_PBT | Kiln1 | SC 1-316 PC STOP | None | PLC_DISCWRITE | B100/315 | SC 1-316 PC STOP
SC1316A_IM | Kiln1 | SC 1-316-A INTERLOCKS MET | None | PLC_DISCREAD | B3/275 | SC 1-316-A INTERLOCKS MET
SC1316A_PBS | Kiln1 | SC 1-316-A PC START | None | PLC_DISCWRITE | B100/382 | SC 1-316-A PC START
SC1316A_PBT | Kiln1 | SC 1-316-A PC STOP | None | PLC_DISCWRITE | B100/381 | SC 1-316-A PC STOP
SC1316AFTS_ALM | Kiln1 | SC 1-318 FAILED TO START | On | PLC_ALARM | B101/237 | SC 1-318 FAILED TO START
SC1316AMS_BYP | Kiln1 | SC 1-316-A MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/415 | SC 1-316-A MOTION SWITCH BYPASS
SC1316AMS_X | Kiln1 | SC 1-316-A FDBK | Off | PLC_DISCREAD | I:24/01 | SC 1-316-A STOPPED
SC1316AMSF_ALM | Kiln1 | SC 1-316-A MOTION SWITCH FAILURE | On | PLC_ALARM | B101/238 | SC 1-316-A MOTION SWITCH FAILURE
SC1316FTS_ALM | Kiln1 | SC 1-316 FAILED TO START | On | PLC_ALARM | B101/235 | SC 1-316 FAILED TO START
SC1316MS_BYP | Kiln1 | SC1-316 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/542 | SC 1-316 MOTION SWITCH BYPASS
SC1316MS_X | Kiln1 | SC 1-316 FDBK | Off | PLC_DISCREAD | I:24/00 | SC 1-316 STOPPED
SC1316MSF_ALM | Kiln1 | SC1-318 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/270 | SC 1-316 MOTION SWITCH FAILURE
SC1318_IM | Kiln1 | SC 1-318 INTERLOCKS MET | None | PLC_DISCREAD | B3/274 | SC 1-318 INTERLOCKS MET
SC1318_PBS | Kiln1 | SC 1-318 PC START | None | PLC_DISCWRITE | B100/379 | SC 1-318 PC START
SC1318_PBT | Kiln1 | SC 1-318 PC STOP | None | PLC_DISCWRITE | B100/371 | SC 1-318 PC STOP
SC1318FTS_ALM | Kiln1 | SC 1-318 FAILED TO START | On | PLC_ALARM | B101/241 | SC 1-318 FAILED TO START
SC1318MS_BYP | Kiln1 | SC1-318 MOTION SWITCH BYPASS | On | PLC_DISCWRITE | B100/543 | SC 1-318 MOTION SWITCH BYPASS
SC1318MS_X | Kiln1 | SC 1-318 FDBK | Off | PLC_DISCREAD | I:24/03 | SC 1-318 STOPPED
SC1318MSF_ALM | Kiln1 | SC1-318 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/271 | SC 1-318 MOTION SWITCH FAILURE
SC1613_IM | Kiln1 | SC 1-613-A INTERLOCKS MET | None | PLC_DISCREAD | B3/259 | SC 1-613-A INTERLOCKS MET
SC1613_PBS | Kiln1 | SC 1-613-A PC START | None | PLC_DISCWRITE | B100/453 | SC 1-613-A PC START
SC1613_PBT | Kiln1 | SC 1-613-A PC STOP | None | PLC_DISCWRITE | B100/443 | SC 1-613-A PC STOP
SC1613_SSA_HMI | Kiln1 | SC 1-613 Kiln 1 fuel screw 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1350 | SC 1-613 Kiln 1 fuel screw 0=Auto 1=Man
SC1613A_AUTO | Kiln1 | SC 1-613-A IN AUTO | None | PLC_DISCREAD | I:102/10 | SC 1-613-A IN AUTO
SC1613A_BYP | Kiln1 | SC 1-613-A ZERO SPEED BYPASS | None | PLC_DISCWRITE | B100/84 | SC 1-613-A ZERO SPEED BYPASS
SC1613A_IT | Kiln1 | SC 1-613-A Amps | Amps | 15 | 0.25 | 0 | 0 | PLC_FLTREAD | F9:6 | SC 1-613-A High Amps!
SC1613AMSF_ALM | Kiln1 | SC 1-613-A ZERO SPEED FAILURE! | On | PLC_ALARM | B101/135 | SC 1-613-A ZERO SPEED FAILURE!
SC1613FTS_ALM | Kiln1 | SC 1-613-A FAILED TO START | On | PLC_ALARM | B101/260 | SC 1-613-A FAILED TO START
SC1613MS_X | Kiln1 | SC 1-613-A AUX FDBK | Off | PLC_DISCREAD | I:102/6 | SC 1-613-A STOPPED
SV1614_ZS_ALM | Kiln1 | SV 1-614 BURNER COOLER VALVE FAILURE | On | PLC_ALARM | B3:44/12 | SV 1-614 BURNER COOLER VALVE FAILURE
SV1614_ZSC | Kiln1 | Burner cooling fan valve closed limit | None | PLC_DISCREAD | I:35/00 | IV 1-215 CLOSED
SV1614_ZSO | Kiln1 | Kiln 1 burner cooling fan valve open limit switch | Off | PLC_DISCREAD | I:35/01 | IV 1-215 CLOSED!
TE13051 | Kiln1 | TE 1-305-1 READING PH 1305 RAM 1 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N59:0 | TE 1-305-1 READING PH 1305 RAM 1
TE130511 | Kiln1 | TE 1-305-11 READING PH 1305 RAM 11 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N60:5 | TE 1-305-11 READING PH 1305 RAM 11
TE130513 | Kiln1 | TE 1-305-13 READING PH 1305 RAM 13 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N60:6 | TE 1-305-13 READING PH 1305 RAM 13
TE13053 | Kiln1 | TE 1-305-3 READING PH 1305 RAM 3 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N59:3 | TE 1-305-3 READING PH 1305 RAM 3
TE13055 | Kiln1 | TE 1-305-5 READING PH 1305 RAM 5 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N60:2 | TE 1-305-5 READING PH 1305 RAM 5
TE13057 | Kiln1 | TE 1-305-7 READING PH 1305 RAM 7 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N60:3 | TE 1-305-7 READING PH 1305 RAM 7
TE13059 | Kiln1 | TE 1-305-9 READING PH 1305 RAM 9 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N60:4 | TE 1-305-9 READING PH 1305 RAM 9
TE13131_ACT | Kiln1 | TE 1-313-1 GRAVEL BED MOD 1 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:3 | TE 1-313-1 GRAVEL BED MOD 1 TEMP
TE131310_ACT | Kiln1 | TE 1-313-10 GRAVEL BED MOD 10 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:45 | TE 1-313-10 GRAVEL BED MOD 10 TEMP
TE13132_ACT | Kiln1 | TE 1-313-2 GRAVEL BED MOD 2 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:4 | TE 1-313-2 GRAVEL BED MOD 2 TEMP
TE13133_ACT | Kiln1 | TE 1-313-3 GRAVEL BED MOD 3 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:5 | TE 1-313-3 GRAVEL BED MOD 3 TEMP
TE13134_ACT | Kiln1 | TE 1-313-4 GRAVEL BED MOD 4 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:6 | TE 1-313-4 GRAVEL BED MOD 4 TEMP
TE13135_ACT | Kiln1 | TE 1-313-5 GRAVEL BED MOD 5 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:7 | TE 1-313-5 GRAVEL BED MOD 5 TEMP
TE13136_ACT | Kiln1 | TE 1-313-6 GRAVEL BED MOD 6 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:8 | TE 1-313-6 GRAVEL BED MOD 6 TEMP
TE13137_ACT | Kiln1 | TE 1-313-7 GRAVEL BED MOD 7 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:9 | TE 1-313-7 GRAVEL BED MOD 7 TEMP
TE13138_ACT | Kiln1 | TE 1-313-8 GRAVEL BED MOD 8 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:10 | TE 1-313-8 GRAVEL BED MOD 8 TEMP
TE13139_ACT | Kiln1 | TE 1-313-9 GRAVEL BED MOD 9 TEMP | F | 600 | 2 | 0 | 0 | PLC_INTREAD | N32:44 | TE 1-313-9 GRAVEL BED MOD 9 TEMP
TG1313ALM_TM | Kiln1 | TG 1-313 ALARM TIME | sec | 10 | 1 | 0 | 0 | PLC_INTREAD | N102:94 | TG 1-313 ALARM TIME
TG1313B1_OPEN | Kiln1 | TG 1-313-B1 OPEN | None | PLC_DISCREAD | I:76/5 | TG 1-313-B1 OPEN
TG1313B10_OPEN | Kiln1 | TG 1-313-B10 OPEN | None | PLC_DISCREAD | I:77/07 | TG 1-313-B10 OPEN
TG1313B10OPEN_ALM | Kiln1 | GB 1-313 MOD 10 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/465 | GB 1-313 MOD 10 BOT TIPPING GATE DID NOT OPEN
TG1313B1OPEN_ALM | Kiln1 | GB 1-313 MOD 1 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/451 | GB 1-313 MOD 1 BOT TIPPING GATE DID NOT OPEN
TG1313B2_OPEN | Kiln1 | TG 1-313-B2 OPEN | None | PLC_DISCREAD | I:76/7 | TG 1-313-B2 OPEN
TG1313B2OPEN_ALM | Kiln1 | GB 1-313 MOD 2 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/461 | GB 1-313 MOD 2 BOT TIPPING GATE DID NOT OPEN
TG1313B3_OPEN | Kiln1 | TG 1-313-B3 OPEN | None | PLC_DISCREAD | I:76/11 | TG 1-313-B3 OPEN
TG1313B3OPEN_ALM | Kiln1 | GB 1-313 MOD 3 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/452 | GB 1-313 MOD 3 BOT TIPPING GATE DID NOT OPEN
TG1313B4_OPEN | Kiln1 | TG 1-313-B4 OPEN | None | PLC_DISCREAD | I:76/13 | TG 1-313-B4 OPEN
TG1313B4OPEN_ALM | Kiln1 | GB 1-313 MOD 4 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/462 | GB 1-313 MOD 4 BOT TIPPING GATE DID NOT OPEN
TG1313B5_OPEN | Kiln1 | TG 1-313-B5 OPEN | None | PLC_DISCREAD | I:76/15 | TG 1-313-B5 OPEN
TG1313B5OPEN_ALM | Kiln1 | GB 1-313 MOD 5 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/453 | GB 1-313 MOD 5 BOT TIPPING GATE DID NOT OPEN
TG1313B6_OPEN | Kiln1 | TG 1-313-B6 OPEN | None | PLC_DISCREAD | I:76/17 | TG 1-313-B6 OPEN
TG1313B6OPEN_ALM | Kiln1 | GB 1-313 MOD 6 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/463 | GB 1-313 MOD 6 BOT TIPPING GATE DID NOT OPEN
TG1313B7_OPEN | Kiln1 | TG 1-313-B7 OPEN | None | PLC_DISCREAD | I:77/01 | TG 1-313-B7 OPEN
TG1313B7OPEN_ALM | Kiln1 | GB 1-313 MOD 7 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/454 | GB 1-313 MOD 7 BOT TIPPING GATE DID NOT OPEN
TG1313B8_OPEN | Kiln1 | TG 1-313-B8 OPEN | None | PLC_DISCREAD | I:77/03 | TG 1-313-B8 OPEN
TG1313B8OPEN_ALM | Kiln1 | GB 1-313 MOD 8 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/464 | GB 1-313 MOD 8 BOT TIPPING GATE DID NOT OPEN
TG1313B9_OPEN | Kiln1 | TG 1-313-B9 OPEN | None | PLC_DISCREAD | I:77/05 | TG 1-313-B9 OPEN
TG1313B9OPEN_ALM | Kiln1 | GB 1-313 MOD 9 BOT TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/455 | GB 1-313 MOD 9 BOT TIPPING GATE DID NOT OPEN
TG1313BN_EN | Kiln1 | TG 1-313-BN (MOD2-10) ENABLED TO OPEN | None | PLC_DISCREAD | O:77/5 | TG 1-313-BN (MOD2-10) ENABLED TO OPEN
TG1313BS_EN | Kiln1 | TG 1-313-BS (MOD1-9) ENABLED TO OPEN | None | PLC_DISCREAD | O:77/3 | TG 1-313-BS (MOD1-9) ENABLED TO OPEN
TG1313CYC_TM | Kiln1 | TG 1-313 CYCLE TIME | sec | 240 | 1 | 0 | 0 | PLC_INTREAD | N102:93 | TG 1-313 CYCLE TIME
TG1313T1_OPEN | Kiln1 | TG 1-313-T1 OPEN | None | PLC_DISCREAD | I:76/4 | TG 1-313-T1 OPEN
TG1313T10_OPEN | Kiln1 | TG 1-313-T10 OPEN | None | PLC_DISCREAD | I:77/06 | TG 1-313-T10 OPEN
TG1313T10OPEN_ALM | Kiln1 | GB 1-313 MOD 10 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/460 | GB 1-313 MOD 10 TOP TIPPING GATE DID NOT OPEN
TG1313T1OPEN_ALM | Kiln1 | GB 1-313 MOD 1 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/446 | GB 1-313 MOD 1 TOP TIPPING GATE DID NOT OPEN
TG1313T2_OPEN | Kiln1 | TG 1-313-T2 OPEN | None | PLC_DISCREAD | I:76/6 | TG 1-313-T2 OPEN
TG1313T2OPEN_ALM | Kiln1 | GB 1-313 MOD 2 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/456 | GB 1-313 MOD 2 TOP TIPPING GATE DID NOT OPEN
TG1313T3_OPEN | Kiln1 | TG 1-313-T3 OPEN | None | PLC_DISCREAD | I:76/10 | TG 1-313-T3 OPEN
TG1313T3OPEN_ALM | Kiln1 | GB 1-313 MOD 3 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/447 | GB 1-313 MOD 3 TOP TIPPING GATE DID NOT OPEN
TG1313T4_OPEN | Kiln1 | TG 1-313-T4 OPEN | None | PLC_DISCREAD | I:76/12 | TG 1-313-T4 OPEN
TG1313T4OPEN_ALM | Kiln1 | GB 1-313 MOD 4 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/457 | GB 1-313 MOD 4 TOP TIPPING GATE DID NOT OPEN
TG1313T5_OPEN | Kiln1 | TG 1-313-T5 OPEN | None | PLC_DISCREAD | I:76/14 | TG 1-313-T5 OPEN
TG1313T5OPEN_ALM | Kiln1 | GB 1-313 MOD 5 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/448 | GB 1-313 MOD 5 TOP TIPPING GATE DID NOT OPEN
TG1313T6_OPEN | Kiln1 | TG 1-313-T6 OPEN | None | PLC_DISCREAD | I:76/16 | TG 1-313-T6 OPEN
TG1313T6OPEN_ALM | Kiln1 | GB 1-313 MOD 6 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/458 | GB 1-313 MOD 6 TOP TIPPING GATE DID NOT OPEN
TG1313T7_OPEN | Kiln1 | TG 1-313-T7 OPEN | None | PLC_DISCREAD | I:77/00 | TG 1-313-T7 OPEN
TG1313T7OPEN_ALM | Kiln1 | GB 1-313 MOD 7 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/449 | GB 1-313 MOD 7 TOP TIPPING GATE DID NOT OPEN
TG1313T8_OPEN | Kiln1 | TG 1-313-T8 OPEN | None | PLC_DISCREAD | I:77/02 | TG 1-313-T8 OPEN
TG1313T8OPEN_ALM | Kiln1 | GB 1-313 MOD 8 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/459 | GB 1-313 MOD 8 TOP TIPPING GATE DID NOT OPEN
TG1313T9_OPEN | Kiln1 | TG 1-313-T9 OPEN | None | PLC_DISCREAD | I:77/04 | TG 1-313-T9 OPEN
TG1313T9OPEN_ALM | Kiln1 | GB 1-313 MOD 9 TOP TIPPING GATE DID NOT OPEN | On | PLC_ALARM | B101/450 | GB 1-313 MOD 9 TOP TIPPING GATE DID NOT OPEN
TG1313TN_EN | Kiln1 | TG 1-313-TN (MOD2-10) ENABLED TO OPEN | None | PLC_DISCREAD | O:77/4 | TG 1-313-TN (MOD2-10) ENABLED TO OPEN
TG1313TS_EN | Kiln1 | TG 1-313-TS (MOD1-9) ENABLED TO OPEN | None | PLC_DISCREAD | O:77/2 | TG 1-313-TS (MOD1-9) ENABLED TO OPEN
TOT_DAY_K1LIME | Kiln1 | KILN 1 TOT TON LIME YESTERDAY | TON | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:234 | KILN 1 TOT TON LIME YESTERDAY
TOT_DAY_K1LIMERECLAMATION | Kiln1 | KILN 1 TOT TON LIME TO RECLAMATION YESTERDAY | TON | 2100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:415 | KILN 1 TOT TON LIME TO RECLAMATION YESTERDAY
TOT_DAY_K1LIMESILO3 | Kiln1 | KILN 1 TOT TON LIME TO SILO 3 YESTERDAY | TON | 2100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:416 | KILN 1 TOT TON LIME TO SILO 3 YESTERDAY
TOT_K1LIME | Kiln1 | KILN 1 LIME TOTALIZER | TON | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:233 | KILN 1 LIME TOTALIZER
VF1340_AUTO | Kiln1 | VF 1340 AUTO/MANUAL | None | PLC_DISCWRITE | B100/515 | VF 1340 AUTO/MANUAL
VF1340_HITEMP | Kiln1 | VF 1-340 HIGH TEMPERATURE SP | deg F | 800 | 1 | 0 | 0 | PLC_INTWRITE | N102:36 | VF 1-340 HIGH TEMPERATURE SP
VF1340_PC_AM | Kiln1 | VF 1340 PC PID AUTO/MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100:3/15 | VF 1340 PC PID AUTO/MANUAL 1=AUTO 0=MANUAL
VF1340_TOBC4401 | Kiln1 | VF 1340 SET TO BC 401 | None | PLC_DISCREAD | B100/511 | VF 1340 SET TO BC 401
VF1340_TOBOTH | Kiln1 | VF 1340 TO PC 4420 AND BC 4401 | None | PLC_DISCREAD | B100/513 | VF 1340 TO PC 4420 AND BC 4401
VF1340_TOPC4420 | Kiln1 | VF 1340 TO PC 4420 | None | PLC_DISCREAD | B100/512 | VF 1340 TO PC 4420
VF1340A_HI | Kiln1 | VF 1-340-A HIGH SPEED SP | % Speed | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:30 | VF 1-340-A HIGH SPEED SP
VF1340A_IM | Kiln1 | VF 1-340-A INTERLOCKS MET | None | PLC_DISCREAD | B3/251 | VF 1-340-A INTERLOCKS MET
VF1340A_LOW | Kiln1 | VF 1-340-A LOW SPEDD SP | % Speed | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:31 | VF 1-340-A LOW SPEDD SP
VF1340A_LOWLOW | Kiln1 | VF 1-340-A LOW LOW SPEED SP | % Speed | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:34 | VF 1-340-A LOW LOW SPEED SP
VF1340A_MANSPD | Kiln1 | VF 1340-A MANUAL SPEED SP | % Speed | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:37 | VF 1340-A MANUAL SPEED SP
VF1340A_NOTPLUGGED | Kiln1 | VF 1-340-A NOT PLUGGED - RESET ALARM | On | PLC_DISCWRITE | B100/54 | VF 1-340-A NOT PLUGGED - RESET ALARM
VF1340A_PBS | Kiln1 | VF 1340-A PC START | None | PLC_DISCWRITE | B100/483 | VF 1340-A PC START
VF1340A_PBT | Kiln1 | VF 1340-A PC STOP | None | PLC_DISCWRITE | B100/484 | VF 1340-A PC STOP
VF1340A_PLUGGED | Kiln1 | VF 1-340-A POSSIBLY PLUGGED - CHECK FEEDER FLOW | None | PLC_ALARM | B101/120 | VF 1-340-A POSSIBLY PLUGGED - CHECK FEEDER FLOW
VF1340A_TT | Kiln1 | VF 1340-A TEMPERATURE | °F | 2000 | 1 | 0 | 0 | PLC_INTREAD | N39:4 | VF 1340-A TEMPERATURE
VF1340AFTS_ALM | Kiln1 | VF 1-340-A FAILED TO START | On | PLC_ALARM | B101/250 | VF 1-340-A FAILED TO START
VF1340AHI_SP | Kiln1 | VF 1340-A HI SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:119 | VF 1340-A HI SPEED SP
VF1340AHITEMP_ALM | Kiln1 | VF 1-340-A TEMP > 450 F - TAKE CORRECTIVE ACTION!! | Off | PLC_ALARM | B101/116 | VF 1-340-A TEMP > 450 F - TAKE CORRECTIVE ACTION!!
VF1340ALOW_SP | Kiln1 | VF 1340-A LOW SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:125 | VF 1340-A LOW SPEED SP
VF1340AMS_X | Kiln1 | VF 1-340-A AUX FDBK | Off | PLC_DISCREAD | I:37/00 | VF 1-340-A STOPPED
VF1340APID_ACT | Kiln1 | VF 1340-A ACTUAL SPEED % | % | 4095 | 1 | 0 | 0 | PLC_INTWRITE | N35:0 | VF 1340-A ACTUAL SPEED %
VF1340B_HI | Kiln1 | VF 1340-B HIGH SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:12 | VF 1340-B HIGH SPEED SP
VF1340B_IM | Kiln1 | VF 1340-B INTERLOCKS MET | None | PLC_DISCREAD | B3/252 | VF 1340-B INTERLOCKS MET
VF1340B_LOW | Kiln1 | VF 1340-B LOW SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:13 | VF 1340-B LOW SPEED SP
VF1340B_LOWLOW | Kiln1 | VF 1340-B LOW LOW SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:14 | VF 1340-B LOW LOW SPEED SP
VF1340B_MANSPD | Kiln1 | VF 1340-B MANUAL SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:38 | VF 1340-B MANUAL SPEED SP
VF1340B_NOTPLUGGED | Kiln1 | VF 1-340-B NOT PLUGGED - RESET ALARM | On | PLC_DISCWRITE | B100/55 | VF 1-340-B NOT PLUGGED - RESET ALARM
VF1340B_PBS | Kiln1 | VF 1340-B PC START | None | PLC_DISCWRITE | B100/488 | VF 1340-B PC START
VF1340B_PBT | Kiln1 | VF 1340-B PC STOP | None | PLC_DISCWRITE | B100/489 | VF 1340-B PC STOP
VF1340B_PLUGGED | Kiln1 | VF 1-340-B POSSIBLY PLUGGED - CHECK FEEDER FLOW | None | PLC_ALARM | B101/121 | VF 1-340-B POSSIBLY PLUGGED - CHECK FEEDER FLOW
VF1340B_TT | Kiln1 | VF 1340-B TEMPERATURE | °F | 2000 | 1 | 0 | 0 | PLC_INTREAD | N39:5 | VF 1340-B TEMPERATURE
VF1340BFTS_ALM | Kiln1 | VF 1-340-B FAILED TO START | On | PLC_ALARM | B101/251 | VF 1-340-B FAILED TO START
VF1340BHI_SP | Kiln1 | VF 1340-B HI SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:127 | VF 1340-B HI SPEED SP
VF1340BHITEMP_ALM | Kiln1 | VF 1-340-B TEMP > 450 F - TAKE CORRECTIVE ACTION!! | Off | PLC_ALARM | B101/117 | VF 1-340-B TEMP > 450 F - TAKE CORRECTIVE ACTION!!
VF1340BLOW_SP | Kiln1 | VF 1340-B LOW SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:128 | VF 1340-B LOW SPEED SP
VF1340BMS_X | Kiln1 | VF 1-340-B AUX FDBK | Off | PLC_DISCREAD | I:37/01 | VF 1-340-B STOPPED
VF1340BPID_ACT | Kiln1 | VF 1340-B ACTUAL SPEED % | % | 4095 | 1 | 0 | 0 | PLC_INTREAD | N35:01 | VF 1340-B ACTUAL SPEED %
VF1340C_HI | Kiln1 | VF 1340-C HIGH SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:17 | VF 1340-C HIGH SPEED SP
VF1340C_IM | Kiln1 | VF 1340-C INTERLOCKS MET | None | PLC_DISCREAD | B3/253 | VF 1340-C INTERLOCKS MET
VF1340C_LOW | Kiln1 | VF 1340-C LOW SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:18 | VF 1340-C LOW SPEED SP
VF1340C_LOWLOW | Kiln1 | VF 1340-C LOW LOW SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:19 | VF 1340-C LOW LOW SPEED SP
VF1340C_MANSPD | Kiln1 | VF 1340-C MANUAL SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:39 | VF 1340-C MANUAL SPEED SP
VF1340C_NOTPLUGGED | Kiln1 | VF 1-340-C NOT PLUGGED - RESET ALARM | On | PLC_DISCWRITE | B100/56 | VF 1-340-C NOT PLUGGED - RESET ALARM
VF1340C_PBS | Kiln1 | VF 1340-C PC START | None | PLC_DISCWRITE | B100/493 | VF 1340-C PC START
VF1340C_PBT | Kiln1 | VF 1340-C PC STOP | None | PLC_DISCWRITE | B100/494 | VF 1340-C PC STOP
VF1340C_PLUGGED | Kiln1 | VF 1-340-C POSSIBLY PLUGGED - CHECK FEEDER FLOW | None | PLC_ALARM | B101/122 | VF 1-340-C POSSIBLY PLUGGED - CHECK FEEDER FLOW
VF1340C_TT | Kiln1 | VF 1340-C TEMPERATURE | °F | 2000 | 1 | 0 | 0 | PLC_INTREAD | N39:6 | VF 1340-C TEMPERATURE
VF1340CFTS_ALM | Kiln1 | VF 1-340-C FAILED TO START | On | PLC_ALARM | B101/252 | VF 1-340-C FAILED TO START
VF1340CHI_SP | Kiln1 | VF 1340-C HI SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:129 | VF 1340-C HI SPEED SP
VF1340CHITEMP_ALM | Kiln1 | VF 1-340-C TEMP > 450 F - TAKE CORRECTIVE ACTION!! | Off | PLC_ALARM | B101/118 | VF 1-340-C TEMP > 450 F - TAKE CORRECTIVE ACTION!!
VF1340CLOW_SP | Kiln1 | VF 1340-C LOW SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:130 | VF 1340-C LOW SPEED SP
VF1340CMS_X | Kiln1 | VF 1-340-C AUX FDBK | Off | PLC_DISCREAD | I:37/02 | VF 1-340-C STOPPED
VF1340CPID_ACT | Kiln1 | VF 1340-C ACTUAL SPEED % | % | 4095 | 1 | 0 | 0 | PLC_INTREAD | N35:2 | VF 1340-C ACTUAL SPEED %
VF1340D_HI | Kiln1 | VF 1340-D HIGH SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:24 | VF 1340-D HIGH SPEED SP
VF1340D_IM | Kiln1 | VF 1340-D INTERLOCKS MET | None | PLC_DISCREAD | B3/254 | VF 1340-D INTERLOCKS MET
VF1340D_LOW | Kiln1 | VF 1340-D LOW SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:25 | VF 1340-D LOW SPEED SP
VF1340D_LOWLOW | Kiln1 | VF 1340-D LOW LOW SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:26 | VF 1340-D LOW LOW SPEED SP
VF1340D_MANSPD | Kiln1 | VF 1340-D MANUAL SPEED SP | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:40 | VF 1340-D MANUAL SPEED SP
VF1340D_NOTPLUGGED | Kiln1 | VF 1-340-D NOT PLUGGED - RESET ALARM | On | PLC_DISCWRITE | B100/57 | VF 1-340-D NOT PLUGGED - RESET ALARM
VF1340D_PBS | Kiln1 | VF 1340-D PC START | None | PLC_DISCWRITE | B100/498 | VF 1340-D PC START
VF1340D_PBT | Kiln1 | VF 1340-D PC STOP | None | PLC_DISCWRITE | B100/499 | VF 1340-D PC STOP
VF1340D_PLUGGED | Kiln1 | VF 1-340-D POSSIBLY PLUGGED - CHECK FEEDER FLOW | None | PLC_ALARM | B101/123 | VF 1-340-D POSSIBLY PLUGGED - CHECK FEEDER FLOW
VF1340D_TT | Kiln1 | VF 1340-D TEMPERATURE | °F | 2000 | 1 | 0 | 0 | PLC_INTREAD | N39:7 | VF 1340-D TEMPERATURE
VF1340DFTS_ALM | Kiln1 | VF 1-340-D FAILED TO START | On | PLC_ALARM | B101/253 | VF 1-340-D FAILED TO START
VF1340DHI_SP | Kiln1 | VF 1340-D HI SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:131 | VF 1340-D HI SPEED SP
VF1340DHITEMP_ALM | Kiln1 | VF 1-340-D TEMP > 450 F - TAKE CORRECTIVE ACTION!! | Off | PLC_ALARM | B101/119 | VF 1-340-D TEMP > 450 F - TAKE CORRECTIVE ACTION!!
VF1340DLOW_SP | Kiln1 | VF 1340-D LOW SPEED SP | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:181 | VF 1340-D LOW SPEED SP
VF1340DMS_X | Kiln1 | VF 1-340-D AUX FDBK | Off | PLC_DISCREAD | I:37/03 | VF 1-340-D STOPPED
VF1340DPID_ACT | Kiln1 | VF 1340-D ACTUAL SPEED % | % | 4095 | 1 | 0 | 0 | PLC_INTREAD | N35:03 | VF 1340-D ACTUAL SPEED %
VF1340PCPID_SP | Kiln1 | VF 1340 PC PID SP COOLER 0-100% | % | 100 | 0.1 | 0 | 0 | PLC_FLTWRITE | F9:97 | VF 1340 PC PID SP COOLER 0-100%
VF1340PID_%RUN | Kiln1 | KILN 1 COOLER PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:279 | KILN 1 COOLER PID % RUNTIME - TODAY
VF1340PID_%RUN_YEST | Kiln1 | KILN 1 COOLER PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:297 | KILN 1 COOLER PID % RUNTIME - PAST
VF1340PID_AM | Kiln1 | VF 1340 PID IN AUTO/MANUAL 0=AUTO 1=MANUAL | None | PLC_DISCREAD | N91:0/1 | VF 1340 PID IN AUTO/MANUAL 0=AUTO 1=MANUAL
VF1340PID_AVAIL | Kiln1 | KILN 1 COOLER PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:278 | KILN 1 COOLER PID AVAIL RUN HOURS - TODAY
VF1340PID_AVAIL_YEST | Kiln1 | KILN 1 COOLER PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:296 | KILN 1 COOLER PID AVAIL RUN HOURS - PAST
VF1340PID_CV | Kiln1 | VF 1340 PID CV (% VF SPEED) |  | 4095 | 1 | 0 | 0 | PLC_INTWRITE | N91:24 | VF 1340 PID CV (% VF SPEED)
VF1340PID_DB | Kiln1 | VF 1340 PID DEADBAND |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:9 | VF 1340 PID DEADBAND
VF1340PID_DR | Kiln1 | VF 1340 PID DERIVATIVE RATE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:5 | VF 1340 PID DERIVATIVE RATE
VF1340PID_ER | Kiln1 | VF 1340 PID ERROR |  | 4095 | 1 | 0 | -4095 | PLC_INTREAD | N91:15 | VF 1340 PID ERROR
VF1340PID_PG | Kiln1 | VF 1340 PID PROPORTIONAL GAIN |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:3 | VF 1340 PID PROPORTIONAL GAIN
VF1340PID_PV | Kiln1 | VF 1340 PID PROCESS VAR. (COOLER LVL) |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:23 | VF 1340 PID PROCESS VAR. (COOLER LVL)
VF1340PID_RT | Kiln1 | VF 1340 PID RT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:4 | VF 1340 PID RT
VF1340PID_SP | Kiln1 | VF 1340 PID SET POINT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:02 | VF 1340 PID SET POINT
VF1340PID_TB | Kiln1 | VF 1340 PID TIEBACK |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N91:25 | VF 1340 PID TIEBACK
VF1340PID_UT | Kiln1 | VF 1340 PID UPDATE TIMER |  | 5000 | 1 | 0 | 0 | PLC_INTREAD | T4:268.PRE | VF 1340 PID UPDATE TIMER
VF1340TRANS_ALM | Kiln1 | VF 1-340 BELT 401 AND 420 TRANSPORT FAULT | Off | PLC_ALARM | B101/29 | VF 1-340 BELT 401 AND 420 TRANSPORT FAULT
WF1601_IM | Kiln1 | WF 1-601 INTERLOCKS MET | None | USCNEL101 | NEL_KN1_WF1601.PLOCK | WF 1-601 INTERLOCKS MET
WF1601_OFF6HRS | Kiln1 | WF 1-601 has been off for 6 hours | None | PLC_DISCREAD | T4:704.DN
WF1601_PBE | Kiln1 | WF 1-601 PC START | None | USCNEL101 | NEL_KN1_WF1601.PBE_HMI | WF 1-601 PC START
WF1601_PBS | Kiln1 | WF 1-601 PC STOP | None | USCNEL101 | NEL_KN1_WF1601.PBS_HMI | WF 1-601 PC STOP
WF1601_SP | Kiln1 | WF 1-601 FEED RATE SETPOINT | TPH | 15 | 0.01 | 0 | 0 | PLC_FLTWRITE | F71:01 | WF 1-601 FEED RATE SETPOINT
WF1601_SSA_HMI | Kiln1 | WF 1-601 Kiln 1 fuel weigh feeder 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1355 | WF 1-601 Kiln 1 fuel weigh feeder 0=Auto 1=Man
WF1601_TOT | Kiln1 | KILN 1 COAL TOTALIZER | Ton | 200 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:15 | KILN 1 COAL TOTALIZER
WF1601_TOT_DAY | Kiln1 | WF 1-601 TOTALIZER DAILY | Ton | 200 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:122 | WF 1-601 TOTALIZER DAILY
WF1601_WT | Kiln1 | WF 1-601 TONS PER HOUR | TPH | 15 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:166 | WF 1-601 TONS PER HOUR
WF1601A_IM | Kiln1 | WF 1-601A INTERLOCKS MET | None | USCNEL101 | NEL_KN1_WF1601A.PLOCK | WF 1-601 INTERLOCKS MET
WF1601A_PBE | Kiln1 | WF 1-601A PC START | None | USCNEL101 | NEL_KN1_WF1601A.PBE_HMI | WF 1-601 PC START
WF1601A_PBS | Kiln1 | WF 1-601A PC STOP | None | USCNEL101 | NEL_KN1_WF1601A.PBS_HMI | WF 1-601 PC STOP
WF1601ALMSP_MAX | Kiln1 | WF 1-601 MAX FEED RATE ALARM SETPOINT | TPH | 14 | 1 | 0 | 1 | PLC_INTWRITE | N7:26 | WF 1-601 MAX FEED RATE ALARM SETPOINT
WF1601ALMSP_MIN | Kiln1 | WF 1-601 MIN FEED RATE ALARM SETPOINT | TPH | 14 | 1 | 0 | 1 | PLC_INTWRITE | N7:25 | WF 1-601 MIN FEED RATE ALARM SETPOINT
WF1601APID_AM | Kiln1 | WF 1-601A PID INDICATOR AUTO=0 MANUAL = 1 | None | USCNEL101 | NEL_KN1_WF1601A_QT.PID_SSA_HMI | WF 1-601 PID INDICATOR AUTO=0 MANUAL = 1
WF1601APID_TOG | Kiln1 | WF 1-601A PID PC TOGGLE ON/OFF | None | USCNEL101 | NEL_KN1_WF1601A_QT.PID_SSA_HMI | WF 1-601 PID PC TOGGLE ON/OFF
WF1601FTS_ALM | Kiln1 | WF 1-601 FAILED TO START | On | PLC_ALARM | B101/256 | WF 1-601 FAILED TO START
WF1601HIGHFEED_ALM | Kiln1 | WF 1-601 HIGH COAL FEED RATE ALARM | On | PLC_ALARM | B101/22 | WF 1-601 HIGH COAL FEED RATE ALARM
WF1601HIPID_SP | Kiln1 | WF 1-601 HI SPEED PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N76:11 | WF 1-601 HI SPEED PID SP
WF1601LOWFEED_ALM | Kiln1 | WF 1-601 LOW COAL FEED RATE ALARM | On | PLC_ALARM | B101/023 | WF 1-601 LOW COAL FEED RATE ALARM
WF1601LOWPID_SP | Kiln1 | WF 1-601 LOW PID SPEED SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N76:12 | WF 1-601 LOW PID SPEED SP
WF1601MS_X | Kiln1 | WF 1-601 AUX FDBK | Off | PLC_DISCREAD | I:37/13 | WF 1-601 STOPPED
WF1601PID_%RUN | Kiln1 | KILN 1 FUEL BELT PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:281 | KILN 1 FUEL BELT PID % RUNTIME - TODAY
WF1601PID_%RUN_YEST | Kiln1 | KILN 1 FUEL BELT PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:299 | KILN 1 FUEL BELT PID % RUNTIME - PAST
WF1601PID_AM | Kiln1 | WF 1-601 PID INDICATOR AUTO=0 MANUAL = 1 | None | USCNEL101 | NEL_KN1_WF1601_QT.PID_SSA_HMI | WF 1-601 PID INDICATOR AUTO=0 MANUAL = 1
WF1601PID_AVAIL | Kiln1 | KILN 1 FUEL BELT PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:280 | KILN 1 FUEL BELT PID AVAIL RUN HOURS - TODAY
WF1601PID_AVAIL_YEST | Kiln1 | KILN 1 FUEL BELT PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:298 | KILN 1 FUEL BELT PID AVAIL RUN HOURS - PAST
WF1601PID_CV | Kiln1 | WF 1-601 PID CV (WF 1-601 %) |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N76:24 | WF 1-601 PID CV (WF 1-601 %)
WF1601PID_DB | Kiln1 | WF 1-601 PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N76:9 | WF 1-601 PID DEADBAND
WF1601PID_DR | Kiln1 | WF 1-601 PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N76:5 | WF 1-601 PID DR
WF1601PID_ER | Kiln1 | WF 1-601 PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N76:15 | WF 1-601 PID ERROR
WF1601PID_PG | Kiln1 | WF 1-601 PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N76:3 | WF 1-601 PID PG
WF1601PID_PV | Kiln1 | WF 1-601 PID PV (TPH) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N76:23 | WF 1-601 PID PV (TPH) 0-4095
WF1601PID_RT | Kiln1 | WF 1-601 PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N76:4 | WF 1-601 PID RT
WF1601PID_SP | Kiln1 | WF 1-601 PID SP - SP = WF1601_SP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N76:2 | WF 1-601 PID SP - SP = WF1601_SP
WF1601PID_TB | Kiln1 | WF 1-601 PID TB (WF 1-601 %) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N76:25 | WF 1-601 PID TB (WF 1-601 %) 0-4095
WF1601PID_TOG | Kiln1 | WF 1-601 PID PC TOGGLE ON/OFF | None | USCNEL101 | NEL_KN1_WF1601_QT.PID_SSA_HMI | WF 1-601 PID PC TOGGLE ON/OFF
WF1601PID_UT | Kiln1 | WF 1-601 PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | N76:13 | WF 1-601 PID UPDATE TIME
WF1601WT_TREND | Kiln1 | KILN 1 COAL MILL FEEDRATE |  | 10 | 0.1 | 0 | KILN 1 COAL MILL FEEDRATE | 0 | 0 | 0
WF2601A_PBS | Kiln1 | WF 2-601A PC START | None | USCNEL202 | NEL_KN2_WF2601A.PBE_HMI | WF 1-601 PC START
WF2601A_PBT | Kiln1 | WF 2-601A PC STOP | None | USCNEL101 | NEL_KN2_WF2601A.PBS_HMI | WF 1-601 PC STOP
WF2601B_PBS | Kiln1 | WF 2-601B PC START | None | USCNEL202 | NEL_KN2_WF2601B.PBE_HMI | WF 1-601 PC START
WF2601B_PBT | Kiln1 | WF 2-601B PC STOP | None | USCNEL101 | NEL_KN2_WF2601B.PBS_HMI | WF 1-601 PC STOP
WP_1326_3_MINUTE_WARNING | Kiln1 | WP 1-326-1&2 OFF FOR 3 MINUTES | On | PLC_ALARM | B101:36/14 | WP 1-326-1&2 OFF FOR 3 MINUTES!! TAKE CORRECTIVE ACTION!!
WP_1326_4_MINUTE_WARNING | Kiln1 | WP 1-326-1&2 OFF FOR 4 MINUTES. START PUMPS! | On | PLC_ALARM | B101:36/15 | WP 1-326-1&2 OFF FOR 4 MINUTES!!! TAKE CORRECTIVE ACTION!!!!
WP13261_IM | Kiln1 | WP 1-326-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/264 | WP 1-326-1 INTERLOCKS MET
WP13261_PBS | Kiln1 | WP 1-326-1 PC START | None | PLC_DISCWRITE | B100/377 | WP 1-326-1 PC START
WP13261_PBT | Kiln1 | WP 1-326-1 PC STOP | None | PLC_DISCWRITE | B100/356 | WP 1-326-1 PC STOP
WP13261_SSA_HMI | Kiln1 | WP1326_1 water pump 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1310 | WP1326_1 water pump 0=Auto 1=Man
WP13261FTS_ALM | Kiln1 | WP 1-326-1 FAILED TO START | On | PLC_ALARM | B101/245 | WP 1-326-1 FAILED TO START
WP13261MS_X | Kiln1 | WP 1-326-1 AUX FDBK | Off | PLC_DISCREAD | I:25/06 | WP 1-326-1 STOPPED
WP13262_IM | Kiln1 | WP 1-326-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/265 | WP 1-326-2 INTERLOCKS MET
WP13262_PBS | Kiln1 | WP 1-326-2 PC START | None | PLC_DISCWRITE | B100/378 | WP 1-326-2 PC START
WP13262_PBT | Kiln1 | WP 1-326-2 PC STOP | None | PLC_DISCWRITE | B100/357 | WP 1-326-2 PC STOP
WP13262_SSA_HMI | Kiln1 | WP1326_2 water pump 0=Auto 1=Man | None | PLC_DISCWRITE | b3/1315 | WP1326_2 water pump 0=Auto 1=Man
WP13262FTS_ALM | Kiln1 | WP 1-326-2 FAILED TO START | On | PLC_ALARM | B101/247 | WP 1-326-2 FAILED TO START
WP13262MS_X | Kiln1 | WP 1-326-2 AUX FDBK | Off | PLC_DISCREAD | I:25/07 | WP 1-326-2 STOPPED
WP1326OFF5MIN_ALM | Kiln1 | WP 1-326-1 & -2 OFF FOR FIVE MINUTES | On | PLC_ALARM | B101/246 | WP 1-326-1 & -2 OFF FOR FIVE MINUTES
YTDK1COOLERLVLPID_AVAIL | Kiln1 | KILN 1 COOLER LEVEL PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:800
YTDK1COOLERLVLPID_RUNTIME | Kiln1 | KILN 1 COOLER LEVEL PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:801
YTDK1FTSPID_AVAIL | Kiln1 | KILN 1 FEED TO SPEED PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:806
YTDK1FTSPID_RUNTIME | Kiln1 | KILN 1 FEED TO SPEED PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:807
YTDK1FUELWBPID_AVAIL | Kiln1 | KILN 1 FUEL WB PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:802
YTDK1FUELWBPID_RUNTIME | Kiln1 | KILN 1 FUEL WB PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:803
YTDK1HOODDRAFTPID_AVAIL | Kiln1 | KILN 1 HOODDRAFT PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:804
YTDK1HOODDRAFTPID_RUNTIME | Kiln1 | KILN 1 HOODDRAFT PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:805
YTDK1KILNEXITPID_AVAIL | Kiln1 | KILN 1 KILN EXIT PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:808
YTDK1KILNEXITPID_RUNTIME | Kiln1 | KILN 1 KILN EXIT PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:809
YTDK1TEMPTEEPID_AVAIL | Kiln1 | KILN 1 TEMP TEE PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:810
YTDK1TEMPTEEPID_RUNTIME | Kiln1 | KILN 1 TEMP TEE PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:811
YTDK2FTSPID_RUNTIME | Kiln1 | KILN 2 FEED TO SPEED PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:819
YTDK2HOODDRAFTPID_RUNTIME | Kiln1 | KILN 2 HOODDRAFT PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:817
BBT_313_1 | KILN1_BH | KILN 1 BH LEAK DETECTOR | % | 100 | 0.02 | 0 | 0 | KILN1_BH_READ | BBT_313_1 | KILN 1 BH DETECTING BAG LEAKS
BH_ROW_INDEX | KILN1_BH | KILN I BH ROW INDEX NUMBER |  | 18 | 1 | 0 | 1 | KILN1_BH_READ | BH_ROW_INDEX | 2
CA1_345_AUX | KILN1_BH | CA 1_345 C KILN1 BH COMPRESSOR AUX FDBK | Off | KILN1_BH_READ | CA1_345_AUX | CA 1-323-C STOPPED
CA1_345_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | CA1_345.FTS_ALM | KILN1 BH COMPRESSOR FAILED TO START
CA1_345_PBS | KILN1_BH | K1 BH COMPRESSOR START | None | KILN1_BH_WRITE | CA1_345.PBS
CA1_345_PRESSURE | KILN1_BH | KILN 1 BH COMPRESSOR PRESSURE | " psi | 100 | 0.02 | 0 | 0 | KILN1_BH_READ | CA1_345_PRESSURE | KILN 1 BH COMPRESSOR PRESSURE LOW
CA1_345_PRESSURE1 | KILN1_BH | KILN1 BH AIR COMPRESSOR PRESSURE (PSI) | On | KILN1_BH_READ | CA1_345_PRESSURE1 | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIHIGH SHUTDOWN IN 3MIN
CLX_NELSON1 | KILN1_BH | BIT TXFR FROM NELCLX TO NELSON 1 TO CHECK COMMS | None | KILN1_BH_ALARM | CLX_NELSON1
CLX_NELSON2 | KILN1_BH | BIT TXFR FROM NELCLX TO NELSON 2 TO CHECK COMMS | None | KILN1_BH_ALARM | CLX_NELSON2
CLX_NELSON3 | KILN1_BH | BIT TXFR FROM NELCLX TO NELSON 3 TO CHECK COMMS | None | KILN1_BH_ALARM | CLX_NELSON3
CLX_NELSON4 | KILN1_BH | BIT TXFR FROM NELCLX TO NELSON 4 TO CHECK COMMS | None | KILN1_BH_ALARM | CLX_NELSON4
DM1_313_PID_AM | KILN1_BH | DM1_313_PID A/M KILN 1 BAGHOUSE BLEED AIR DAMPER 1 | None | KILN1_BH_READ | DM1_313_PID.MO | DM1_313_PID A/M KILN 1 BAGHOUSE BLEED AIR DAMPER 1=MAN 0=AUTO
DM1_313_PID_CV | KILN1_BH | DM1_313 POSITION KILN 1 BLEED AIR DAMPER | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | DM1_313_PID_CV | 2
DM1_313_PID_KD | KILN1_BH | DM1_313_PID DERIVATIVE GAIN KILN 1 BAGHOUSE BLEED |  | 4095 | 1 | 0 | 0 | KILN1_BH_READ | DM1_313_PID.KD | 2
DM1_313_PID_KI | KILN1_BH | DM1_313_PID INTEGRAL GAIN KILN 1 BAGHOUSE BLEED AI |  | 4095 | 1 | 0 | 0 | KILN1_BH_READ | DM1_313_PID.KI | 2
DM1_313_PID_KP | KILN1_BH | DM1_313_PID PROPORTIONAL GAIN KILN 1 BAGHOUSE BLEE |  | 4095 | 1 | 0 | 0 | KILN1_BH_READ | DM1_313_PID.KP | 2
DM1_313_PID_PV | KILN1_BH | DM1_313_PID PROCESS VARIALBLE KILN 1 BAGHOUSE BLEE |  | 4095 | 1 | 0 | 0 | KILN1_BH_READ | DM1_313_PID_PV | 2
DM1_313_PID_SP | KILN1_BH | DM1_313_PID SETPOINT KILN 1 BAGHOUSE BLEED AIR DAM |  | 4095 | 1 | 0 | 0 | KILN1_BH_READ | DM1_313_PID.SP | 2
DM1_313_PID_TIE | KILN1_BH | DM1_313_PID TIEBACK VARIALBLE KILN 1 BAGHOUSE BLEE |  | 4095 | 1 | 0 | 0 | KILN1_BH_READ | DM1_313_PID_TIE | 2
DM1_313_PIDTEMPSP | KILN1_BH | TE1_313 PID INLET TEMP. SETPOINT BAGHOUSE BLEED AI | °F | 500 | 2 | 0 | 0 | KILN1_BH_WRITE | DM1_313_PIDTEMPSP | 2
DM1_313_POSITION_FDBK | KILN1_BH | DM1_313 POSITION KILN 1 BLEED AIR DAMPER | % | 100 | 0 | 0 | 0 | KILN1_BH_READ | DM1_313_POSITION_FDBK | 2
DP_313_PCSETPOINT | KILN1_BH | KILN 1 BH DIFFERENTIAL PRESSURE PC SETPOINT | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_WRITE | DP_313_PCSETPOINT | 2
DPT_313_1 | KILN1_BH | DPT_313_1 KILN 1 DUST COLLECTOR MOD.1 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_1 | 2
DPT_313_10 | KILN1_BH | DPT_313_10 KILN 1 DUST COLLECTOR MOD.10 DIFFERENTI | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_10 | 2
DPT_313_11 | KILN1_BH | KILN 1 BAGHOUSE DIFF. PRESS | "WC | 10 | 0 | 0 | 0 | KILN1_BH_READ | DPT_313_11 | KILN 1 BAGHOUSE DIFF. PRESS
DPT_313_11_HIGH | KILN1_BH | KILN1 BH HIGH DIFFERENTIAL PRESSURE ALARM | On | KILN1_BH_ALARM | DPT_313_11_HIGH | KILN1 BH HIGH DIFFERENTIAL PRESSURE ALARM
DPT_313_2 | KILN1_BH | DPT_313_2 KILN 1 DUST COLLECTOR MOD.2 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_2 | 2
DPT_313_3 | KILN1_BH | DPT_313_3 KILN 1 DUST COLLECTOR MOD.3 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_3 | 2
DPT_313_4 | KILN1_BH | DPT_313_4 KILN 1 DUST COLLECTOR MOD.4 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_4 | 2
DPT_313_5 | KILN1_BH | DPT_313_5 KILN 1 DUST COLLECTOR MOD.5 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_5 | 2
DPT_313_6 | KILN1_BH | DPT_313_6 KILN 1 DUST COLLECTOR MOD.6 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_6 | 2
DPT_313_7 | KILN1_BH | DPT_313_7 KILN 1 DUST COLLECTOR MOD.7 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_7 | 2
DPT_313_8 | KILN1_BH | DPT_313_8 KILN 1 DUST COLLECTOR MOD.8 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_8 | 2
DPT_313_9 | KILN1_BH | DPT_313_9 KILN 1 DUST COLLECTOR MOD.9 DIFFERENTIAL | "W.C. | 10 | 0.1 | 0 | 0 | KILN1_BH_READ | DPT_313_9 | 2
DRIVE_CONTROL | KILN1_BH | KILN 1 ID FAN MESSAGE CONTROL | None | KILN1_BH_WRITE | DRIVE_CONTROL.DN
FN1_314_ALM_FNBTEMPSHTDWN_FS | KILN1_BH | FN1_314 ALARM KILN 1 FARSIDE FAN BEARING TEMP - SH | On | KILN1_BH_ALARM | FN1_314_ALM_FNBTEMPSHTDWN_FS | K1 ID FAN NORTH BEARING TEMP HIHI - SHUTDOWN FAN
FN1_314_ALM_FNBTEMPSHTDWN_MS | KILN1_BH | FN1_314 ALARM KILN 1 MOTORSIDE FAN BEARING TEMP - | On | KILN1_BH_ALARM | FN1_314_ALM_FNBTEMPSHTDWN_MS | K1 ID FAN SOUTH BEARING TEMP HIHI - SHUTDWN FAN!!
FN1_314_ALM_HI_VIB1 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM FAR END HOR | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB1 | K1 ID FAN MOTOR HI VIB1 ALARM
FN1_314_ALM_HI_VIB2 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM FAR END VER | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB2 | K1 ID FAN MOTOR HI VIB2 ALARM
FN1_314_ALM_HI_VIB3 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM FAN END HOR | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB3 | K1 ID FAN MOTOR HI VIB3 ALARM
FN1_314_ALM_HI_VIB4 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM FAN END VER | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB4 | K1 ID FAN MOTOR HI VIB4 ALARM
FN1_314_ALM_HI_VIB5 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM MOTORSIDE H | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB5 | K1 ID FAN MOTOR HI VIB5 ALARM
FN1_314_ALM_HI_VIB6 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM MOTORSIDE V | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB6 | K1 ID FAN MOTOR HI VIB6 ALARM
FN1_314_ALM_HI_VIB7 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM FAR SIDE HO | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB7 | K1 ID FAN MOTOR HI VIB7 ALARM
FN1_314_ALM_HI_VIB8 | KILN1_BH | KILN 1 ID FAN MOTOR HI VIBRATION ALARM FAR SIDE VE | On | KILN1_BH_ALARM | FN1_314_ALM_HI_VIB8 | K1 ID FAN MOTOR HI VIB8 ALARM
FN1_314_ALM_HI_WDGTEMP10 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH MOTOR WINDING TEM | On | KILN1_BH_ALARM | FN1_314_ALM_HI_WDGTEMP10 | K1 ID FAN HIGH MOTOR WINDING TEMP10
FN1_314_ALM_HI_WDGTEMP5 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH MOTOR WINDING TEM | On | KILN1_BH_ALARM | FN1_314_ALM_HI_WDGTEMP5 | K1 ID FAN HIGH MOTOR WINDING TEMP5
FN1_314_ALM_HI_WDGTEMP6 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH MOTOR WINDING TEM | On | KILN1_BH_ALARM | FN1_314_ALM_HI_WDGTEMP6 | K1 ID FAN HIGH MOTOR WINDING TEMP6
FN1_314_ALM_HI_WDGTEMP7 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH MOTOR WINDING TEM | On | KILN1_BH_ALARM | FN1_314_ALM_HI_WDGTEMP7 | K1 ID FAN HIGH MOTOR WINDING TEMP7
FN1_314_ALM_HI_WDGTEMP8 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH MOTOR WINDING TEM | On | KILN1_BH_ALARM | FN1_314_ALM_HI_WDGTEMP8 | K1 ID FAN HIGH MOTOR WINDING TEMP8
FN1_314_ALM_HI_WDGTEMP9 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH MOTOR WINDING TEM | On | KILN1_BH_ALARM | FN1_314_ALM_HI_WDGTEMP9 | K1 ID FAN HIGH MOTOR WINDING TEMP9
FN1_314_ALM_HIFNBTEMP_FS | KILN1_BH | FN1_314 ALARM KILN 1 HIGH FAN BEARING TEMP FAR SID | On | KILN1_BH_ALARM | FN1_314_ALM_HIFNBTEMP_FS | K1 ID FAN HI FAN BEARING TEMP NORTH
FN1_314_ALM_HIFNBTEMP_MS | KILN1_BH | FN1_314 ALARM KILN 1 HIGH FAN BEARING TEMP MOTORSI | On | KILN1_BH_ALARM | FN1_314_ALM_HIFNBTEMP_MS | K1 ID FAN SOUTH BEARING TEMP HI
FN1_314_ALM_HIHI_VIB1 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM FAR EN | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB1 | K1 ID FAN MOTOR HIHI VIB1 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB2 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM FAR EN | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB2 | K1 ID FAN MOTOR HIHI VIB2 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB3 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM FAN EN | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB3 | K1 ID FAN MOTOR HIHI VIB3 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB4 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM FAN EN | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB4 | K1 ID FAN MOTOR HIHI VIB4 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB5 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM MTRSID | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB5 | K1 ID FAN MOTOR HIHI VIB5 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB6 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM MTRSID | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB6 | K1 ID FAN MOTOR HIHI VIB6 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB7 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM FARSID | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB7 | K1 ID FAN MOTOR HIHI VIB7 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_VIB8 | KILN1_BH | KILN 1 ID FAN MOTOR HIHIGH VIBRATION ALARM FARSID | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_VIB8 | K1 ID FAN MOTOR HIHI VIB8 - SHUTDOWN 3 MIN
FN1_314_ALM_HIHI_WDGTEMP10 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_WDGTEMP10 | K1 ID FAN MOTOR WINDING TEMP HIHI - SHUTDWN IN 3MIN
FN1_314_ALM_HIHI_WDGTEMP5 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_WDGTEMP5 | K1 ID FAN MOTOR WINDING TEMP HIHI - SHUTDWN IN 3MIN
FN1_314_ALM_HIHI_WDGTEMP6 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_WDGTEMP6 | K1 ID FAN MOTOR WINDING TEMP HIHI - SHUTDWN IN 3MIN
FN1_314_ALM_HIHI_WDGTEMP7 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_WDGTEMP7 | K1 ID FAN MOTOR WINDING TEMP HIHI - SHUTDWN IN 3MIN
FN1_314_ALM_HIHI_WDGTEMP8 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_WDGTEMP8 | K1 ID FAN MOTOR WINDING TEMP HIHI - SHUTDWN IN 3MIN
FN1_314_ALM_HIHI_WDGTEMP9 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP HIH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHI_WDGTEMP9 | K1 ID FAN MOTOR WINDING TEMP HIHI - SHUTDWN IN 3MIN
FN1_314_ALM_HIHIFNBTEMP_FS | KILN1_BH | FN1_314 ALARM KILN1 FAN BEARING TEMP FARSIDE HIHI | On | KILN1_BH_ALARM | FN1_314_ALM_HIHIFNBTEMP_FS | K1 FAN NORTH BEARING TEMP HIHI FAN WILL SHUTDWN 3 MIN.
FN1_314_ALM_HIHIFNBTEMP_MS | KILN1_BH | FN1_314 ALARM KILN1 FAN BEARING TEMP MOTORSIDE$NH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHIFNBTEMP_MS | K1 ID FAN SOUTH BEARING TEMP HIHI FAN WILL SHUTDWN 3 MIN.
FN1_314_ALM_HIHIMTRBTEMP_FNS | KILN1_BH | FN1_314 ALARM KILN 1 FAN MOTOR BEARING TEMP HIHIGH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHIMTRBTEMP_FNS | K1 ID FAN NORTH MOTOR BEARING TEMP HIHI FAN WILL SHUTDWN 3 MIN.
FN1_314_ALM_HIHIMTRBTEMP_FS | KILN1_BH | FN1_314 ALARM KILN 1 FAN MOTOR BEARING TEMP HIHIGH | On | KILN1_BH_ALARM | FN1_314_ALM_HIHIMTRBTEMP_FS | K1 ID FAN SOUTH MOTOR BEARING TEMP HIHI FAN WILL SHUTDWN 3 MIN.
FN1_314_ALM_HIMTRBTEMP_FNS | KILN1_BH | FN1_314 ALARM KILN 1 FAN MOTOR BEARING TEMP HIGH F | On | KILN1_BH_ALARM | FN1_314_ALM_HIMTRBTEMP_FNS | K1 ID FAN NORTH MOTOR BEARING TEMP HIGH
FN1_314_ALM_HIMTRBTEMP_FS | KILN1_BH | FN1_314 ALARM KILN 1 FAN MOTOR BEARING TEMP HIGH F | On | KILN1_BH_ALARM | FN1_314_ALM_HIMTRBTEMP_FS | K1 FAN SOUTH MOTOR BEARING TEMP HIGH
FN1_314_ALM_MTRBTEMPSHTDWN_FNS | KILN1_BH | FN1_314 ALARM KILN 1 FAN MOTOR BEARING TEMP - SHUT | On | KILN1_BH_ALARM | FN1_314_ALM_MTRBTEMPSHTDWN_FNS | K1 ID FAN NORTH MOTOR BEARING TEMP HIHI - SHUTDWN FAN!!
FN1_314_ALM_MTRBTEMPSHTDWN_FS | KILN1_BH | FN1_314 ALARM KILN 1 FAN MOTOR BEARING TEMP - SHUT | On | KILN1_BH_ALARM | FN1_314_ALM_MTRBTEMPSHTDWN_FS | K1 ID FAN SOUTH MOTOR BEARING TEMP HIHI - SHUTDWN FAN!!
FN1_314_AUX | KILN1_BH | FN1_314 KILN 1 ID FAN AUXILLARY FEEDBACK | Off | KILN1_BH_READ | FN1_314_AUX | KILN 1 ID FAN STOPPED!!
FN1_314_DRIVE_CUR | KILN1_BH | FN1_314 ID FAN Drive Output Current | Amp | 999 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_DRIVE_CUR | 2
FN1_314_DRIVE_CUR_AH | KILN1_BH | FN1_314 ID FAN Drive Current High Alarm | On | KILN1_BH_READ | FN1_314_DRIVE_CUR_AH | KILN 1 ID FAN HI CURRENT
FN1_314_DRIVE_CUR_AHH | KILN1_BH | FN1_314 ID FAN Drive Current Hi Hi Alarm | On | KILN1_BH_READ | FN1_314_DRIVE_CUR_AHH | KILN 1 ID FAN HI HI CURRENT
FN1_314_DRIVE_FAULTED | KILN1_BH | FN1_314 KILN 1 ID FAN PF7000 DRIVE FAULTED | On | KILN1_BH_READ | FN1_314_DRIVE_FAULTED | KILN 1 ID FAN DRIVE FAULTED
FN1_314_DRIVE_KW | KILN1_BH | FN1_314 ID FAN Drive Output Current | KW | 250 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_DRIVE_KW | 2
FN1_314_DRIVE_READY | KILN1_BH | FN1_314 KILN 1 ID FAN PF7000 DRIVE READY | None | KILN1_BH_READ | FN1_314_DRIVE_READY | KILN 1 ID FAN DRIVE READY
FN1_314_DRIVE_REF | KILN1_BH | FN1_314 ID FAN Drive Output Frequency | Hz | 100 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_DRIVE_REF | 2
FN1_314_DRIVE_RPM | KILN1_BH | FN1_314 ID FAN MOTOR RPM | RPM | 2000 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_DRIVE_RPM | 2
FN1_314_DRIVE_VAC | KILN1_BH | FN1_314 ID FAN Drive Output VAC | VAC | 10000 | 0 | 0 | 0 | KILN1_BH_READ | FN1_314_DRIVE_VAC | 2
FN1_314_DRIVETEMP_HIGH | KILN1_BH | K1 ID FAN DRIVE RECTIFIER OR INVERTER TEMP HIGH | On | KILN1_BH_ALARM | FN1_314_DRIVETEMP_HIGH | K1 ID FAN DRIVE TEMP HIGH - CHECK A/C UNIT IN MCR8
FN1_314_FTS_ALM | KILN1_BH | FN1_314 KILN 1 ID FAN FAILED TO START ALARM | On | KILN1_BH_ALARM | FN1_314.FTS_ALM | K1 ID FAN FAILED TO START
FN1_314_IM | KILN1_BH | FN1_314 KILN 1 ID FAN INTERLOCKSMET | None | KILN1_BH_READ | FN1_314.IM | FN1_314 KILN 1 ID FAN INTERLOCKSMET
FN1_314_PBS | KILN1_BH | FN1_314 KILN 1 ID FAN PC START | None | KILN1_BH_WRITE | FN1_314.PBS | FN1_314 KILN 1 ID FAN PC START
FN1_314_PBT | KILN1_BH | FN1_314 KILN 1 ID FAN PC STOP | Off | KILN1_BH_WRITE | FN1_314.PBT | FN1_314 KILN 1 ID FAN STOPPED
FN1_314_PCSP | KILN1_BH | FN1_314 KILN1 ID FAN PC SETPOINT (0 - 100%) | % | 100 | 1 | 0 | 10 | KILN1_BH_WRITE | FN1_314_PCSP | 2
FN1_314_RT_RST | KILN1_BH | FN1_314 KILN 1 ID FAN Hours reset button | Off | KILN1_BH_WRITE | FN1_314_RT_RST | KILN 1 ID FAN STOPPED!!
FN1_314_SHTDWNALM_VIB1 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM FAR END HORI | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB1 | K1 ID FAN MOTOR VIB1 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_VIB2 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM FAR END VERT | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB2 | K1 ID FAN MOTOR VIB2 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_VIB3 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM FAN END HORI | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB3 | K1 ID FAN MOTOR VIB3 HIHI - SHUTDOWN FAN!!
FN1_314_SHTDWNALM_VIB4 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM FAN END VERT | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB4 | K1 ID FAN MOTOR VIB4 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_VIB5 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM MOTORSIDE HO | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB5 | K1 ID FAN MOTOR VIB5 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_VIB6 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM MOTORSIDE VE | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB6 | K1 ID FAN MOTOR VIB6 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_VIB7 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM FAR SIDE HOR | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB7 | K1 ID FAN MOTOR VIB7 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_VIB8 | KILN1_BH | KILN 1 ID FAN MOTOR VIBRATION ALARM FAR SIDE VER | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_VIB8 | K1 ID FAN MOTOR VIB8 HIHI - SHUTDWN FAN!!
FN1_314_SHTDWNALM_WDGTEMP10 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP SHU | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_WDGTEMP10 | K1 ID FAN MOTOR WINDING TEMP10 HIHI SHTDWN FAN
FN1_314_SHTDWNALM_WDGTEMP5 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP SHU | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_WDGTEMP5 | K1 ID FAN MOTOR WINDING TEMP6 HIHI SHUTDWN FAN
FN1_314_SHTDWNALM_WDGTEMP6 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP SHU | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_WDGTEMP6 | K1 ID FAN MOTOR WINDING TEMP6 HIHI SHUTDWN FAN
FN1_314_SHTDWNALM_WDGTEMP7 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP SHU | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_WDGTEMP7 | K1 ID FAN MOTOR WINDING TEMP7 HIHI SHUTDWN FAN
FN1_314_SHTDWNALM_WDGTEMP8 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP SHU | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_WDGTEMP8 | K1 ID FAN MOTOR WINDING TEMP8 HIHI SHUTDWN FAN
FN1_314_SHTDWNALM_WDGTEMP9 | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN MOTOR WINDING TEMP SHU | On | KILN1_BH_ALARM | FN1_314_SHTDWNALM_WDGTEMP9 | K1 ID FAN MOTOR WINDING TEMP9 HIHI SHUTDWN FAN
FN1_314_SSA_HMI | KILN1_BH | FN1_314 KILN 1 ID FAN 0=Auto 1=Man | Off | KILN1_BH_READ | FN1_314_SSA_HMI | KILN 1 ID FAN STOPPED!!
FN1_314_TLOCK | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH TEMP | On | KILN1_BH_ALARM | FN1_314_TLOCK | K1 ID FAN HIGH MOTOR WINDING TEMP10
FN1_314_VIB_ALM | KILN1_BH | FN1_314 ALARM KILN 1 ID FAN HIGH VIBRATION | On | KILN1_BH_ALARM | FN1_314_VIB_ALM | K1 ID FAN HIGH MOTOR WINDING TEMP10
FN1314_HITEMP_TIMERDN | KILN1_BH | K1 ID FAN HIBEARING TEMP 3MIN DONE | None | KILN1_BH_ALARM | Local_Timer(0).DN | FN 1-314 SPEED SET TO ZERO
FN1314_HITEMP_TIMERDN1 | KILN1_BH | K1 ID FAN MOTOR HIBEARING TEMP 3MIN DONE | None | KILN1_BH_ALARM | Local_Timer(1).DN | FN 1-314 SPEED SET TO ZERO
FN1314_HITEMP_TIMERDN2 | KILN1_BH | K1 ID MOTOR HIHIWDG TEMP 3MIN DONE | None | KILN1_BH_ALARM | Local_Timer(2).DN | FN 1-314 SPEED SET TO ZERO
FN1314_HITEMP_TIMERDN3 | KILN1_BH | K1 ID MOTOR HIHIVIB TEMP 3MIN DONE | None | KILN1_BH_ALARM | Local_Timer(3).DN | FN 1-314 SPEED SET TO ZERO
INV_LIME_PCTFULL | KILN1_BH |  | PCT | 100 | 0 | 0 | 0 | KILN1_BH_READ | INV_LIME_PCTFULL.IND
KILN1_BH_CLEANING | KILN1_BH |  | None | KILN1_BH_WRITE | KILN1_BH_CLEANING
KILN1_BH_CLEANING_MODE_WWTOG | KILN1_BH | KILN 1 BH CLEANING MODE WW TOGGLE 1=ONLINE | On | KILN1_BH_WRITE | KILN1_BH_CLEANING_MODE_WWTOG | KILN 1 BH CLEANING MODE SET TO ONLINE
KILN1_BH_CLEANING_PRESSUREMODE | KILN1_BH | KILN 1 BH CLEANING MODE WW TOGGLE 1= PRESSURE | On | KILN1_BH_WRITE | KILN1_BH_CLEANING_PRESSUREMODE | KILN 1 BH CLEANING MODE SET PRESSURE MODE
KILN1_BH_MOD_ALM | KILN1_BH | KILN 1 BH - AT LEAST ONE MODULE OUT OF SERVICE | On | KILN1_BH_ALARM | KILN1_BH_MOD_ALM | KILN 1 BH - AT LEAST ONE MODULE OUT OF SERVICE
KILN1_BH_MOD_INDEX | KILN1_BH | KILN I BH MODULE INDEX NUMBER |  | 10 | 1 | 0 | 1 | KILN1_BH_READ | KILN1_BH_MOD_INDEX | 2
KILN1_BH_MOD_NUMBER | KILN1_BH | KILN I BH MODULE NUMBER |  | 10 | 1 | 0 | 1 | KILN1_BH_READ | KILN1_BH_MOD_NUMBER | 2
KILN1_BH_MOD1_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD1_CLOSE_ISOVALVE
KILN1_BH_MOD1_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD1_CLOSE_POPVALVE
KILN1_BH_MOD1_CONTROL | KILN1_BH | KILN 1 BH MODULE 1 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD1_CONTROL | KILN 1 BH MODULE 1 SEQUENCER CONTROL
KILN1_BH_MOD1_DONE | KILN1_BH | KILN 1 BH MODULE 1 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD1_DONE | KILN 1 BH MODULE 1 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD1_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD1 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD1_HPPR_HILEVEL | K1 BH MOD1 HI HOPPER LEVEL ALARM
KILN1_BH_MOD1_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD1_ISOVALVE_CLOSED
KILN1_BH_MOD1_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD1_ISOVALVE_OPEN
KILN1_BH_MOD1_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 1 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD1_POPVALVE | KILN 1 BH CLOSE MODULE 1 POPPET VALVE
KILN1_BH_MOD1_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 1 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD1_POPVALVE_ALM | KILN 1 BH MODULE 1 POPPET VALVE ALARM
KILN1_BH_MOD1_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD1_POPVALVE_CLOSED
KILN1_BH_MOD1_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD1_POPVALVE_OPEN
KILN1_BH_MOD1_POPVALVE_WWTOG | KILN1_BH | KILN1 BH MODULE 1 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD1_POPVALVE_WWTOG | KILN1 BH MODULE 1 POPPET VALVE WW TOGGLE
KILN1_BH_MOD1_RUN_SEQ | KILN1_BH | KILN1 BH MODULE 1 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD1_RUN_SEQ | KILN1 BH MODULE 1 RUN SEQUENCER
KILN1_BH_MOD10_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD10_CLOSE_ISOVALVE
KILN1_BH_MOD10_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD10_CLOSE_POPVALVE
KILN1_BH_MOD10_CONTROL | KILN1_BH | KILN 1 BH MODULE 10 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD10_CONTROL | KILN 1 BH MODULE 10 SEQUENCER CONTROL
KILN1_BH_MOD10_DONE | KILN1_BH | KILN 1 BH MODULE 10 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD10_DONE | KILN 1 BH MODULE 10 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD10_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD10 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD10_HPPR_HILEVEL | KILN1 BH MOD10 HI HOPPER LEVEL ALARM
KILN1_BH_MOD10_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD10_ISOVALVE_CLOSED
KILN1_BH_MOD10_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD10_ISOVALVE_OPEN
KILN1_BH_MOD10_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 10 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD10_POPVALVE | KILN 1 BH CLOSE MODULE 10 POPPET VALVE
KILN1_BH_MOD10_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 10 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD10_POPVALVE_ALM | KILN 1 BH MODULE 10 POPPET VALVE ALARM
KILN1_BH_MOD10_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD10_POPVALVE_CLOSED
KILN1_BH_MOD10_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD10_POPVALVE_OPEN
KILN1_BH_MOD10_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 10 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD10_POPVALVE_WWTOG | KILN 1 BH MODULE 10 POPPET VALVE WW TOGGLE
KILN1_BH_MOD10_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 10 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD10_RUN_SEQ | KILN 1 BH MODULE 10 RUN SEQUENCER
KILN1_BH_MOD10_SEQ_RUN | KILN1_BH | KILN 1 BH RUN MODULE 10 SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD10_SEQ_RUN | KILN 1 BH RUN MODULE 10 SEQUENCER
KILN1_BH_MOD2_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD2_CLOSE_ISOVALVE
KILN1_BH_MOD2_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD2_CLOSE_POPVALVE
KILN1_BH_MOD2_CONTROL | KILN1_BH | KILN 1 BH MODULE 2 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD2_CONTROL | KILN 1 BH MODULE 2 SEQUENCER CONTROL
KILN1_BH_MOD2_DONE | KILN1_BH | KILN 1 BH MODULE 2 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD2_DONE | KILN 1 BH MODULE 2 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD2_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD2 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD2_HPPR_HILEVEL | KILN1 BH MOD2 HI HOPPER LEVEL ALARM
KILN1_BH_MOD2_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD2_ISOVALVE_CLOSED
KILN1_BH_MOD2_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD2_ISOVALVE_OPEN
KILN1_BH_MOD2_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 2 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD2_POPVALVE | KILN 1 BH CLOSE MODULE 2 POPPET VALVE
KILN1_BH_MOD2_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 2 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD2_POPVALVE_ALM | KILN 1 BH MODULE 2 POPPET VALVE ALARM
KILN1_BH_MOD2_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD2_POPVALVE_CLOSED
KILN1_BH_MOD2_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD2_POPVALVE_OPEN
KILN1_BH_MOD2_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 2 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD2_POPVALVE_WWTOG | KILN 1 BH MODULE 2 POPPET VALVE WW TOGGLE
KILN1_BH_MOD2_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 2 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD2_RUN_SEQ | KILN 1 BH MODULE 2 RUN SEQUENCER
KILN1_BH_MOD3_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD3_CLOSE_ISOVALVE
KILN1_BH_MOD3_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD3_CLOSE_POPVALVE
KILN1_BH_MOD3_CONTROL | KILN1_BH | KILN 1 BH MODULE 3 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD3_CONTROL | KILN 1 BH MODULE 3 SEQUENCER CONTROL
KILN1_BH_MOD3_DONE | KILN1_BH | KILN 1 BH MODULE 3 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD3_DONE | KILN 1 BH MODULE 3 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD3_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD3 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD3_HPPR_HILEVEL | KILN1 BH MOD3 HI HOPPER LEVE ALARM
KILN1_BH_MOD3_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD3_ISOVALVE_CLOSED
KILN1_BH_MOD3_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD3_ISOVALVE_OPEN
KILN1_BH_MOD3_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 3 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD3_POPVALVE | KILN 1 BH CLOSE MODULE 3 POPPET VALVE
KILN1_BH_MOD3_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE3 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD3_POPVALVE_ALM | KILN 1 BH MODULE3 POPPET VALVE ALARM
KILN1_BH_MOD3_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD3_POPVALVE_CLOSED
KILN1_BH_MOD3_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD3_POPVALVE_OPEN
KILN1_BH_MOD3_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 3 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD3_POPVALVE_WWTOG | KILN 1 BH MODULE 3 POPPET VALVE WW TOGGLE
KILN1_BH_MOD3_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 3 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD3_RUN_SEQ | KILN 1 BH MODULE 3 RUN SEQUENCER
KILN1_BH_MOD4_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD4_CLOSE_ISOVALVE
KILN1_BH_MOD4_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD4_CLOSE_POPVALVE
KILN1_BH_MOD4_CONTROL | KILN1_BH | KILN 1 BH MODULE 4 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD4_CONTROL | KILN 1 BH MODULE 4 SEQUENCER CONTROL
KILN1_BH_MOD4_DONE | KILN1_BH | KILN 1 BH MODULE 4 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD4_DONE | KILN 1 BH MODULE 4 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD4_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD4 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD4_HPPR_HILEVEL | KILN1 BH MOD4 HI HOPPER LEVEL ALARM
KILN1_BH_MOD4_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD4_ISOVALVE_CLOSED
KILN1_BH_MOD4_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD4_ISOVALVE_OPEN
KILN1_BH_MOD4_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 4 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD4_POPVALVE | KILN 1 BH CLOSE MODULE 4 POPPET VALVE
KILN1_BH_MOD4_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 4 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD4_POPVALVE_ALM | KILN 1 BH MODULE 4 POPPET VALVE ALARM
KILN1_BH_MOD4_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD4_POPVALVE_CLOSED
KILN1_BH_MOD4_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD4_POPVALVE_OPEN
KILN1_BH_MOD4_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 4 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD4_POPVALVE_WWTOG | KILN 1 BH MODULE 4 POPPET VALVE WW TOGGLE
KILN1_BH_MOD4_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 4 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD4_RUN_SEQ | KILN 1 BH MODULE 4 RUN SEQUENCER
KILN1_BH_MOD5_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD5_CLOSE_ISOVALVE
KILN1_BH_MOD5_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD5_CLOSE_POPVALVE
KILN1_BH_MOD5_CONTROL | KILN1_BH | KILN 1 BH MODULE 5 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD5_CONTROL | KILN 1 BH MODULE 5 SEQUENCER CONTROL
KILN1_BH_MOD5_DONE | KILN1_BH | KILN 1 BH MODULE 5 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD5_DONE | KILN 1 BH MODULE 5 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD5_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD5 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD5_HPPR_HILEVEL | KILN1 BH MOD5 HI HOPPER LEVEL ALARM
KILN1_BH_MOD5_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD5_ISOVALVE_CLOSED
KILN1_BH_MOD5_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD5_ISOVALVE_OPEN
KILN1_BH_MOD5_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 5 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD5_POPVALVE | KILN 1 BH CLOSE MODULE 5 POPPET VALVE
KILN1_BH_MOD5_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 5 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD5_POPVALVE_ALM | KILN 1 BH MODULE 5 POPPET VALVE ALARM
KILN1_BH_MOD5_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD5_POPVALVE_CLOSED
KILN1_BH_MOD5_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD5_POPVALVE_OPEN
KILN1_BH_MOD5_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 5 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD5_POPVALVE_WWTOG | KILN 1 BH MODULE 5 POPPET VALVE WW TOGGLE
KILN1_BH_MOD5_RUN_SEQ | KILN1_BH | KILN1 BH MODULE 5 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD5_RUN_SEQ | KILN1 BH MODULE 5 RUN SEQUENCER
KILN1_BH_MOD6_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD6_CLOSE_ISOVALVE
KILN1_BH_MOD6_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD6_CLOSE_POPVALVE
KILN1_BH_MOD6_CONTROL | KILN1_BH | KILN 1 BH MODULE 6 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD6_CONTROL | KILN 1 BH MODULE 6 SEQUENCER CONTROL
KILN1_BH_MOD6_DONE | KILN1_BH | KILN 1 BH MODULE 6 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD6_DONE | KILN 1 BH MODULE 6 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD6_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD6 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD6_HPPR_HILEVEL | KILN1 BH MOD6 HI HOPPER LEVEL ALARM
KILN1_BH_MOD6_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD6_ISOVALVE_CLOSED
KILN1_BH_MOD6_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD6_ISOVALVE_OPEN
KILN1_BH_MOD6_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 6 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD6_POPVALVE | KILN 1 BH CLOSE MODULE 6 POPPET VALVE
KILN1_BH_MOD6_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 6 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD6_POPVALVE_ALM | KILN 1 BH MODULE 6 POPPET VALVE ALARM
KILN1_BH_MOD6_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD6_POPVALVE_CLOSED
KILN1_BH_MOD6_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD6_POPVALVE_OPEN
KILN1_BH_MOD6_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 6 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD6_POPVALVE_WWTOG | KILN 1 BH MODULE 6 POPPET VALVE WW TOGGLE
KILN1_BH_MOD6_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 6 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD6_RUN_SEQ | KILN 1 BH MODULE 6 RUN SEQUENCER
KILN1_BH_MOD7_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD7_CLOSE_ISOVALVE
KILN1_BH_MOD7_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD7_CLOSE_POPVALVE
KILN1_BH_MOD7_CONTROL | KILN1_BH | KILN 1 BH MODULE 7 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD7_CONTROL | KILN 1 BH MODULE 7 SEQUENCER CONTROL
KILN1_BH_MOD7_DONE | KILN1_BH | KILN 1 BH MODULE 7 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD7_DONE | KILN 1 BH MODULE 7 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD7_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD7 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD7_HPPR_HILEVEL | KILN1 BH MOD7 HI HOPPER LEVEL ALARM
KILN1_BH_MOD7_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD7_ISOVALVE_CLOSED
KILN1_BH_MOD7_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD7_ISOVALVE_OPEN
KILN1_BH_MOD7_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 7 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD7_POPVALVE | KILN 1 BH CLOSE MODULE 7 POPPET VALVE
KILN1_BH_MOD7_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 7 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD7_POPVALVE_ALM | KILN 1 BH MODULE 7 POPPET VALVE ALARM
KILN1_BH_MOD7_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD7_POPVALVE_CLOSED
KILN1_BH_MOD7_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD7_POPVALVE_OPEN
KILN1_BH_MOD7_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 7 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD7_POPVALVE_WWTOG | KILN 1 BH MODULE 7 POPPET VALVE WW TOGGLE
KILN1_BH_MOD7_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 7 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD7_RUN_SEQ | KILN 1 BH MODULE 7 RUN SEQUENCER
KILN1_BH_MOD8_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD8_CLOSE_ISOVALVE
KILN1_BH_MOD8_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD8_CLOSE_POPVALVE
KILN1_BH_MOD8_CONTROL | KILN1_BH | KILN 1 BH MODULE 8 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD8_CONTROL | KILN 1 BH MODULE 8 SEQUENCER CONTROL
KILN1_BH_MOD8_DONE | KILN1_BH | KILN 1 BH MODULE 8 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD8_DONE | KILN 1 BH MODULE 8 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD8_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD8 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD8_HPPR_HILEVEL | KILN1 BH MOD8 HI HOPPER LEVEL ALARM
KILN1_BH_MOD8_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD8_ISOVALVE_CLOSED
KILN1_BH_MOD8_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD8_ISOVALVE_OPEN
KILN1_BH_MOD8_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 8 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD8_POPVALVE | KILN 1 BH CLOSE MODULE 8 POPPET VALVE
KILN1_BH_MOD8_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 8 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD8_POPVALVE_ALM | KILN 1 BH MODULE 8 POPPET VALVE ALARM
KILN1_BH_MOD8_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD8_POPVALVE_CLOSED
KILN1_BH_MOD8_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD8_POPVALVE_OPEN
KILN1_BH_MOD8_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 8 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD8_POPVALVE_WWTOG | KILN 1 BH MODULE 8 POPPET VALVE WW TOGGLE
KILN1_BH_MOD8_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 8 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD8_RUN_SEQ | KILN 1 BH MODULE 8 RUN SEQUENCER
KILN1_BH_MOD9_CLOSE_ISOVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD9_CLOSE_ISOVALVE
KILN1_BH_MOD9_CLOSE_POPVALVE | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD9_CLOSE_POPVALVE
KILN1_BH_MOD9_CONTROL | KILN1_BH | KILN 1 BH MODULE 9 SEQUENCER CONTROL | None | KILN1_BH_READ | KILN1_BH_MOD9_CONTROL | KILN 1 BH MODULE 9 SEQUENCER CONTROL
KILN1_BH_MOD9_DONE | KILN1_BH | KILN 1 BH MODULE 9 VALVES PULSING SQUENCER DONE | None | KILN1_BH_READ | KILN1_BH_MOD9_DONE | KILN 1 BH MODULE 9 VALVES PULSING SQUENCER DONE
KILN1_BH_MOD9_HPPR_HILEVEL | KILN1_BH | KILN1 BH MOD9 HOPPER HIGH LEVEL ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD9_HPPR_HILEVEL | KILN1 BH MOD9 HI HOPPER LEVEL ALARM
KILN1_BH_MOD9_ISOVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD9_ISOVALVE_CLOSED
KILN1_BH_MOD9_ISOVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD9_ISOVALVE_OPEN
KILN1_BH_MOD9_POPVALVE | KILN1_BH | KILN 1 BH CLOSE MODULE 9 POPPET VALVE | None | KILN1_BH_WRITE | KILN1_BH_MOD9_POPVALVE | KILN 1 BH CLOSE MODULE 9 POPPET VALVE
KILN1_BH_MOD9_POPVALVE_ALM | KILN1_BH | KILN 1 BH MODULE 9 POPPET VALVE ALARM | On | KILN1_BH_ALARM | KILN1_BH_MOD9_POPVALVE_ALM | KILN 1 BH MODULE 9 POPPET VALVE ALARM
KILN1_BH_MOD9_POPVALVE_CLOSED | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD9_POPVALVE_CLOSED
KILN1_BH_MOD9_POPVALVE_OPEN | KILN1_BH |  | None | KILN1_BH_READ | KILN1_BH_MOD9_POPVALVE_OPEN
KILN1_BH_MOD9_POPVALVE_WWTOG | KILN1_BH | KILN 1 BH MODULE 9 POPPET VALVE WW TOGGLE | None | KILN1_BH_WRITE | KILN1_BH_MOD9_POPVALVE_WWTOG | KILN 1 BH MODULE 9 POPPET VALVE WW TOGGLE
KILN1_BH_MOD9_RUN_SEQ | KILN1_BH | KILN 1 BH MODULE 9 RUN SEQUENCER | None | KILN1_BH_READ | KILN1_BH_MOD9_RUN_SEQ | KILN 1 BH MODULE 9 RUN SEQUENCER
KILN1_BH_PCSTART | KILN1_BH | KILN 1 BAGHOUSE SYSTEM AUTO PC START | None | KILN1_BH_WRITE | KILN1_BH_PCSTART | KILN 1 BAGHOUSE SYSTEM PC START
KILN1_BH_PCSTOP | KILN1_BH | KILN 1 BAGHOUSE SYSTEM AUTO PC STOP | None | KILN1_BH_WRITE | KILN1_BH_PCSTOP | KILN 1 BAGHOUSE SYSTEM PC STOP
KILN1_BH_POP_PCRESET | KILN1_BH | KILN 1 BH POPPETS VALVE PC RESET | On | KILN1_BH_WRITE | KILN1_BH_POP_PCRESET | KILN 1 BH POPPETS VALVE RESET
KILN1_BH_POP_RESET | KILN1_BH | KILN 1 BH ONE SHOT POPPETS RESET WHEN SET TO ONLIN | None | KILN1_BH_READ | KILN1_BH_POP_RESET | KILN 1 BH POPPETS RESET WHEN SET TO ONLINE MODE
MCR_8_CN12_GOOD | KILN1_BH | RACK 12 IN MCR 8 NOT COMMUNICATING!! | Off | KILN1_BH_ALARM | MCR_8_CN12_GOOD | RACK CN12 IN MCR 8 NOT COMMUNICATING!!
MCR_8_CN13_GOOD | KILN1_BH | RACK 13 IN MCR 8 NOT COMMUNICATING!! | Off | KILN1_BH_ALARM | MCR_8_CN13_GOOD | RACK CN13 IN MCR 8 NOT COMMUNICATING!!
MCR_8_CN14_GOOD | KILN1_BH | RACK 14 IN MCR 8 NOT COMMUNICATING!! | Off | KILN1_BH_ALARM | MCR_8_CN14_GOOD | ANALOG RACK 14 IN MCR 8 NOT COMMUNICATING!!
MCR4_CN10_GOOD | KILN1_BH | KILN1 BH RACK IN MCR 4 NOT COMMUNICATING!! | Off | KILN1_BH_ALARM | MCR4_CN10_GOOD | KILN1 BH RACK IN MCR 4 NOT COMMUNICATING!!
NEL_2_313_PT | KILN1_BH | KIL1 | PSI | 150 | 5 | 0 | 0 | PLC_FLTREAD | F8:92 | 2-313-AIR PRESSURE
NEL_K1_BH_CYC_CNT | KILN1_BH | Kiln 1 Baghouse Daily Cycle Count | Cycles | 1000 | 0 | 0 | 0 | KILN1_BH_READ | NEL_K1_BH_CYC.ACC
NEL_K2_BH_CYC_CNT | KILN1_BH | Kiln 2 Baghouse Daily Cycle Count | Cycles | 1000 | 0 | 0 | 0 | PLC_INTREAD | N64:40
PLC5_CLX_MSG | KILN1_BH | KILN1 BH CLX COMMUNICATION WITH PLC5! | None | KILN1_BH_WRITE | PLC5_CLX_MSG.DN
POPVALVE5_WWTOG | KILN1_BH |  | None | KILN1_BH_WRITE | POPVALVE5_WWTOG | KILN 1 BH MODULE 6 POPPET VALVE WW TOGGLE
RA1_313_1_AUTO | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_1_AUTO
RA1_313_1_AUX | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_1_AUX | KILN1 BH MOD 1 ROTARY AIRLOCK STOPPED
RA1_313_1_FTS_ALM | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK FAILED TO START | On | KILN1_BH_ALARM | RA1_313_1.FTS_ALM | KILN1 BH RA313_1 FTS ALARM
RA1_313_1_IM | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK INTERLOCKS MET | None | KILN1_BH_READ | RA1_313_1.IM
RA1_313_1_MS | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_1_MS
RA1_313_1_MSF_ALM | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK MOTION SWITCH FA | On | KILN1_BH_ALARM | RA1_313_1.MSF_ALM | KILN1 BH RA313_1 MSF ALARM
RA1_313_1_MSF_BYP | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK MOTION SWITCH FA | None | KILN1_BH_WRITE | RA1_313_1.MSFBYP
RA1_313_1_PBS | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK PC START | None | KILN1_BH_WRITE | RA1_313_1.PBS
RA1_313_1_PBT | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK PC STOP | None | KILN1_BH_WRITE | RA1_313_1.PBT | RA1_313_1 MODULE 1 ROTARY AIRLOCK PC STOP
RA1_313_1_RUN | KILN1_BH | RA1_313_1 MODULE 1 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_1_RUN | RA1_313_1 MODULE 1 ROTARY AIRLOCK RUN
RA1_313_10_AUTO | KILN1_BH | RA1_313_10 MODULE 10 ROTARY AIRLOCK IN AUTO POSITI | None | KILN1_BH_READ | RA1_313_10_AUTO
RA1_313_10_AUX | KILN1_BH | RA1_313_10 MODULE 10 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_10_AUX | KIN1 BH MOD10 ROTARY AIRLOCK STOPPED
RA1_313_10_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_10.FTS_ALM | KILN1 BH RA313_10 FTS ALARM
RA1_313_10_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_10.IM
RA1_313_10_MS | KILN1_BH | RA1_313_10 MODULE 10 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_10_MS
RA1_313_10_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_10.MSF_ALM | KILN1 BH RA313_10 MSF ALARM
RA1_313_10_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_10.MSFBYP
RA1_313_10_PBS | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_10.PBS
RA1_313_10_PBT | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_10.PBT
RA1_313_10_RUN | KILN1_BH | RA1_313_10 MODULE 10 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_10_RUN
RA1_313_2_AUTO | KILN1_BH | RA1_313_2 MODULE 2 ROTARY AIRLOCK IN AUTO POSITIO | None | KILN1_BH_READ | RA1_313_2_AUTO
RA1_313_2_AUX | KILN1_BH | RA1_313_2 MODULE 2 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_2_AUX | KILN1 BH MOD 2 ROTARY AIRLOCK STOPPED
RA1_313_2_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_2.FTS_ALM
RA1_313_2_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_2.IM
RA1_313_2_MS | KILN1_BH | RA1_313_2 MODULE 2 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_2_MS | RA1_313_2 MODULE 2 ROTARY AIRLOCK MOTION SWITCH
RA1_313_2_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_2.MSF_ALM | KILN1 BH RA313_2 MSF ALARM
RA1_313_2_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_2.MSFBYP
RA1_313_2_PBS | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_2.PBS
RA1_313_2_PBT | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_2.PBT
RA1_313_2_RUN | KILN1_BH | RA1_313_2 MODULE 2 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_2_RUN | RA1_313_2 MODULE 2 ROTARY AIRLOCK RUN
RA1_313_3_AUTO | KILN1_BH | RA1_313_3 MODULE 3 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_3_AUTO | RA1_313_3 MODULE 3 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_3_AUX | KILN1_BH | RA1_313_3 MODULE 3 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_3_AUX | KILN1 BH MOD 3 ROTARY AIRLOCK STOPPED
RA1_313_3_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_3.FTS_ALM | KILN1 BH RA313_3 FTS ALARM
RA1_313_3_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_3.IM
RA1_313_3_MS | KILN1_BH | RA1_313_3 MODULE 3 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_3_MS | RA1_313_3 MODULE 3 ROTARY AIRLOCK MOTION SWITCH
RA1_313_3_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_3.MSF_ALM | RA313_3 MSF ALARM
RA1_313_3_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_3.MSFBYP
RA1_313_3_PBS | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_3.PBS
RA1_313_3_PBT | KILN1_BH |  | None | KILN1_BH_WRITE | RA1_313_3.PBT
RA1_313_3_RUN | KILN1_BH | RA1_313_3 MODULE 3 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_3_RUN | RA1_313_3 MODULE 3 ROTARY AIRLOCK RUN
RA1_313_4_AUTO | KILN1_BH | RA1_313_4 MODULE 4 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_4_AUTO | RA1_313_4 MODULE 4 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_4_AUX | KILN1_BH | RA1_313_4 MODULE 4 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_4_AUX | KILN1 BH MOD 4 ROTARY AIRLOCK STOPPED
RA1_313_4_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_4.FTS_ALM
RA1_313_4_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_4.IM
RA1_313_4_MS | KILN1_BH | RA1_313_4 MODULE 4 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_4_MS | RA1_313_4 MODULE 4 ROTARY AIRLOCK MOTION SWITCH
RA1_313_4_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_4.MSF_ALM
RA1_313_4_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | RA1_313_4.MSFBYP
RA1_313_4_PBS | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_4.PBS
RA1_313_4_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_4.PBT
RA1_313_4_RUN | KILN1_BH | RA1_313_4 MODULE 4 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_4_RUN | RA1_313_4 MODULE 4 ROTARY AIRLOCK RUN
RA1_313_5_AUTO | KILN1_BH | RA1_313_5 MODULE 5 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_5_AUTO | RA1_313_5 MODULE 5 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_5_AUX | KILN1_BH | RA1_313_5 MODULE 5 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_5_AUX | KILN1 BH MOD 5 ROTARY AIRLOCK STOPPED
RA1_313_5_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_5.FTS_ALM
RA1_313_5_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_5.IM
RA1_313_5_MS | KILN1_BH | RA1_313_5 MODULE 5 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_5_MS | RA1_313_5 MODULE 5 ROTARY AIRLOCK MOTION SWITCH
RA1_313_5_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_5.MSF_ALM
RA1_313_5_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | RA1_313_5.MSFBYP
RA1_313_5_PBS | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_5.PBS
RA1_313_5_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_5.PBT
RA1_313_5_RUN | KILN1_BH | RA1_313_5 MODULE 5 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_5_RUN | RA1_313_5 MODULE 5 ROTARY AIRLOCK RUN
RA1_313_6_AUTO | KILN1_BH | RA1_313_6 MODULE 6 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_6_AUTO | RA1_313_6 MODULE 6 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_6_AUX | KILN1_BH | RA1_313_6 MODULE 6 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_6_AUX | KILN1 BH MOD 6 ROTARY AIRLOCK STOPPED
RA1_313_6_FTS_ALM | KILN1_BH | RA1_313_6 Failed to Start Alarm | On | KILN1_BH_ALARM | RA1_313_6.FTS_ALM
RA1_313_6_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_6.IM
RA1_313_6_MS | KILN1_BH | RA1_313_6 MODULE 6 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_6_MS | RA1_313_6 MODULE 6 ROTARY AIRLOCK MOTION SWITCH
RA1_313_6_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_6.MSF_ALM
RA1_313_6_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | RA1_313_6.MSFBYP
RA1_313_6_PBS | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_6.PBS
RA1_313_6_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_6.PBT
RA1_313_6_RUN | KILN1_BH | RA1_313_6 MODULE 6 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_6_RUN | RA1_313_6 MODULE 6 ROTARY AIRLOCK RUN
RA1_313_7_AUTO | KILN1_BH | RA1_313_7 MODULE 7 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_7_AUTO | RA1_313_7 MODULE 7 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_7_AUX | KILN1_BH | RA1_313_ 7MODULE 7 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_7_AUX | KILN1 BH MOD 7 ROTARY AIRLOCK STOPPED
RA1_313_7_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_7.FTS_ALM
RA1_313_7_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_7.IM
RA1_313_7_MS | KILN1_BH | RA1_313_7 MODULE 7 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_7_MS | RA1_313_7 MODULE 7 ROTARY AIRLOCK MOTION SWITCH
RA1_313_7_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_7.MSF_ALM
RA1_313_7_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | RA1_313_7.MSFBYP
RA1_313_7_PBS | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_7.PBS
RA1_313_7_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_7.PBT
RA1_313_7_RUN | KILN1_BH | RA1_313_7 MODULE 7 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_7_RUN | RA1_313_7 MODULE 7 ROTARY AIRLOCK RUN
RA1_313_8_AUTO | KILN1_BH | RA1_313_8 MODULE 8 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_8_AUTO | RA1_313_8 MODULE 8 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_8_AUX | KILN1_BH | RA1_313_8 MODULE 8 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_8_AUX | KILN1 BH MOD 8 ROTARY AIRLOCK STOPPED
RA1_313_8_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_8.FTS_ALM
RA1_313_8_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_8.IM
RA1_313_8_MS | KILN1_BH | RA1_313_8 MODULE 8 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_8_MS | RA1_313_8 MODULE 8 ROTARY AIRLOCK MOTION SWITCH
RA1_313_8_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_8.MSF_ALM
RA1_313_8_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | RA1_313_8.MSFBYP
RA1_313_8_PBS | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_8.PBS
RA1_313_8_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_8.PBT
RA1_313_8_RUN | KILN1_BH | RA1_313_8 MODULE 8 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_8_RUN | RA1_313_8 MODULE 8 ROTARY AIRLOCK RUN
RA1_313_9_AUTO | KILN1_BH | RA1_313_9 MODULE 9 ROTARY AIRLOCK IN AUTO POSITION | None | KILN1_BH_READ | RA1_313_9_AUTO | RA1_313_9 MODULE 9 ROTARY AIRLOCK IN AUTO POSITION
RA1_313_9_AUX | KILN1_BH | RA1_313_9 MODULE 9 ROTARY AIRLOCK RUNNING | Off | KILN1_BH_READ | RA1_313_9_AUX | KILN1 BH MOD 9 ROTARY AIRLOCK STOPPED
RA1_313_9_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_9.FTS_ALM
RA1_313_9_IM | KILN1_BH |  | None | KILN1_BH_READ | RA1_313_9.IM
RA1_313_9_MS | KILN1_BH | RA1_313_9 MODULE 9 ROTARY AIRLOCK MOTION SWITCH | None | KILN1_BH_READ | RA1_313_9_MS | RA1_313_9 MODULE 9 ROTARY AIRLOCK MOTION SWITCH
RA1_313_9_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | RA1_313_9.MSF_ALM
RA1_313_9_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | RA1_313_9.MSFBYP
RA1_313_9_PBS | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_9.PBS
RA1_313_9_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | RA1_313_9.PBT
RA1_313_9_RUN | KILN1_BH | RA1_313_9 MODULE 9 ROTARY AIRLOCK RUN | None | KILN1_BH_READ | RA1_313_9_RUN | RA1_313_9 MODULE 9 ROTARY AIRLOCK RUN
SC1_316A_AUTO | KILN1_BH |  | None | KILN1_BH_READ | SC1_316A_AUTO
SC1_316A_AUX | KILN1_BH |  | None | KILN1_BH_READ | KILN1_PLC5_MSGX.1
SC1_316A_FTS_ALM | KILN1_BH |  | None | KILN1_BH_ALARM | SC1_316A.FTS_ALM
SC1_316A_IM | KILN1_BH |  | None | KILN1_BH_READ | SC1_316A.IM
SC1_316A_MS | KILN1_BH |  | None | KILN1_BH_READ | SC1_316A_MS
SC1_316A_MSF_ALM | KILN1_BH |  | None | KILN1_BH_ALARM | SC1_316A.MSF_ALM
SC1_316A_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | SC1_316A.MSFBYP
SC1_316A_PBS | KILN1_BH | SC1_316A KILN DUST SCREW CONVEYOR | None | KILN1_BH_WRITE | SC1_316A.PBS
SC1_316A_PBT | KILN1_BH |  | None | KILN1_BH_WRITE | SC1_316A.PBT
SC1_316A_RUN | KILN1_BH |  | None | KILN1_BH_READ | SC1_316A_RUN
SC1_316B | KILN1_BH |  | None | KILN1_BH_READ | SC1_316B
SC1_316B_AUTO | KILN1_BH |  | None | KILN1_BH_READ | SC1_316B_AUTO
SC1_316B_AUX | KILN1_BH |  | Off | KILN1_BH_READ | SC1_316B_AUX | KILN1 BH SC 316B STOPPED
SC1_316B_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316B.FTS_ALM | KILN1 BH SC316B FTS ALARM
SC1_316B_IM | KILN1_BH |  | None | KILN1_BH_READ | SC1_316B.IM
SC1_316B_MS | KILN1_BH |  | None | KILN1_BH_READ | SC1_316B_MS
SC1_316B_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316B.MSF_ALM | KILN1 BH SC1316B MSF ALARM
SC1_316B_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | SC1_316B.MSFBYP
SC1_316B_PBS | KILN1_BH | SC1_316B KILN 1 DUST SCREW CONVEYOR | None | KILN1_BH_WRITE | SC1_316B.PBS
SC1_316B_PBT | KILN1_BH |  | None | KILN1_BH_WRITE | SC1_316B.PBT
SC1_316B_RUN | KILN1_BH |  | None | KILN1_BH_READ | SC1_316B_RUN
SC1_316C_AUTO | KILN1_BH |  | None | KILN1_BH_READ | SC1_316C_AUTO
SC1_316C_AUX | KILN1_BH |  | Off | KILN1_BH_READ | SC1_316C_AUX | KILN1 BH SC 316C STOPPED
SC1_316C_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316C.FTS_ALM | KILN1 BH SC316C FTS ALARM
SC1_316C_IM | KILN1_BH |  | None | KILN1_BH_READ | SC1_316C.IM
SC1_316C_MS | KILN1_BH |  | None | KILN1_BH_READ | SC1_316C_MS
SC1_316C_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316C.MSF_ALM | KILN1 BH SC316C MSF ALARM
SC1_316C_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | SC1_316C.MSFBYP
SC1_316C_PBS | KILN1_BH | SC1_316C KILN 1DUST SCREW CONVEYOR | None | KILN1_BH_WRITE | SC1_316C.PBS
SC1_316C_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | SC1_316C.PBT
SC1_316C_RUN | KILN1_BH |  | None | KILN1_BH_READ | SC1_316C_RUN
SC1_316D_AUTO | KILN1_BH |  | None | KILN1_BH_READ | SC1_316D_AUTO
SC1_316D_AUX | KILN1_BH |  | Off | KILN1_BH_READ | SC1_316D_AUX | KILN1 BH SC 316D STOPPED
SC1_316D_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316D.FTS_ALM | KILN1 BH SC316D FAILED TO START
SC1_316D_IM | KILN1_BH |  | None | KILN1_BH_READ | SC1_316D.IM
SC1_316D_MS | KILN1_BH |  | None | KILN1_BH_READ | SC1_316D_MS
SC1_316D_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316D.MSF_ALM | KILN1 BH SC_316D MSF ALARM
SC1_316D_MSF_BYP | KILN1_BH |  | None | KILN1_BH_WRITE | SC1_316D.MSFBYP
SC1_316D_PBS | KILN1_BH | SC1_316D KILN 1 DUST SCREW CONVEYOR | None | KILN1_BH_WRITE | SC1_316D.PBS | SC1_316D KILN 1 DUST SCREW CONVEYOR
SC1_316D_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | SC1_316D.PBT
SC1_316D_RUN | KILN1_BH |  | None | KILN1_BH_READ | SC1_316D_RUN
SC1_316E_AUTO | KILN1_BH |  | None | KILN1_BH_READ | SC1_316E_AUTO
SC1_316E_AUX | KILN1_BH |  | Off | KILN1_BH_READ | SC1_316E_AUX | KILN1 BH SC 316E STOPPED
SC1_316E_FTS_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316E.FTS_ALM
SC1_316E_IM | KILN1_BH |  | None | KILN1_BH_READ | SC1_316E.IM
SC1_316E_MS | KILN1_BH |  | None | KILN1_BH_READ | SC1_316E_MS
SC1_316E_MSF_ALM | KILN1_BH |  | On | KILN1_BH_ALARM | SC1_316E.MSF_ALM
SC1_316E_MSF_BYP | KILN1_BH |  | On | KILN1_BH_WRITE | SC1_316E.MSFBYP
SC1_316E_PBS | KILN1_BH | SC1 316E KILN 1 DUST SCREW CONVEYOR | Off | KILN1_BH_WRITE | SC1_316E.PBS | SC1 316E KILN 1 DUST SCREW CONVEYOR
SC1_316E_PBT | KILN1_BH |  | Off | KILN1_BH_WRITE | SC1_316E.PBT
SC1_316E_RUN | KILN1_BH |  | None | KILN1_BH_READ | SC1_316E_RUN
TE1_313_1 | KILN1_BH | TE1_313_1 MODULE 1 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_1 | 2
TE1_313_10 | KILN1_BH | TE1_313_10 MODULE 10 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_10 | 2
TE1_313_11_HIGH | KILN1_BH | KILN 1 BAGHOUSE INLET TEMP. HIGH | On | KILN1_BH_ALARM | TE1_313_11_HIGH | KILN 1 BAGHOUSE INLET TEMP. HIGH
TE1_313_11_HIHIGH | KILN1_BH | KILN1 BAGHOUSE INLET TEMP. HIGH HIGH | On | KILN1_BH_ALARM | TE1_313_11_HIHIGH | KILN1 BAGHOUSE INLET TEMP. HIGH HIGH
TE1_313_11_INLET_A | KILN1_BH | TE1_313_11 KILN 1 BAGHOUSE INLET A TEMP. | °F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_11_INLET_A | 2
TE1_313_12_HIGH | KILN1_BH | KILN 1 BAGHOUSE BACKUP INLET TEMP HIGH | On | KILN1_BH_ALARM | TE1_313_12_HIGH | KILN 1 BAGHOUSE BACKUP INLET TEMP HIGH
TE1_313_12_HIHIGH | KILN1_BH | KILN 1 BAGHOUSE BACKUP INLET TEMP HIGH HIGH | On | KILN1_BH_ALARM | TE1_313_12_HIHIGH | KILN 1 BAGHOUSE BACKUP INLET TEMP HIGH HIGH
TE1_313_12_INLET_B | KILN1_BH | TE1_313_12 KILN 1 BAGHOUSE INLET B TEMP | °F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_12_INLET_B | 2
TE1_313_13_EXHAUST | KILN1_BH | TE1_313_13 KILN 1 BAGHOUSE EXHAUST TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_13_EXHAUST | 2
TE1_313_2 | KILN1_BH | TE1_313_2 MODULE 2 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_2 | 2
TE1_313_3 | KILN1_BH | TE1_313_3 MODULE 3 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_3 | 2
TE1_313_4 | KILN1_BH | TE1_313_4 MODULE 4 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_4 | 2
TE1_313_5 | KILN1_BH | TE1_313_5 MODULE 5 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_5 | 2
TE1_313_6 | KILN1_BH | TE1_313_6 MODULE 6 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_6 | 2
TE1_313_7 | KILN1_BH | TE1_313_7 MODULE 7 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_7 | 2
TE1_313_8 | KILN1_BH | TE1_313_8 MODULE 8 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_8 | 2
TE1_313_9 | KILN1_BH | TE1_313_9 MODULE 9 TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_9 | 2
TE1_313_PID_AVE_PV | KILN1_BH |  | DEG F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_313_PID_AVE_PV | 2
TE1_313_PIDTEMPSP | KILN1_BH | TE1_313 PID INLET TEMP. SETPOINT BAGHOUSE BLEED AI | DEG. F | 500 | 2 | 0 | 0 | KILN1_BH_WRITE | TE1_313_PIDTEMPSP | 2
TE1_314_1 | KILN1_BH | TE1_314_1 KILN 1 MOTOR BEARING TEMP. FAR SIDE | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_1 | 2
TE1_314_10 | KILN1_BH | TE1_314_10 KILN 1 ID FAN MOTOR WINDING TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_10 | 2
TE1_314_2 | KILN1_BH | TE1_314_2 KILN 1 MOTOR BEARING TEMP. FAN SIDE | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_2 | 2
TE1_314_3 | KILN1_BH | TE1_314_3 KILN 1 ID FAN BEARING TEMP. MOTOR SIDE | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_3 | 2
TE1_314_4 | KILN1_BH | TE1_314_4 KILN 1 ID FAN BEARING TEMP. FAR SIDE | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_4 | 2
TE1_314_5 | KILN1_BH | TE1_314_5 KILN 1 ID FAN MOTOR WINDING TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_5 | 2
TE1_314_6 | KILN1_BH | TE1_314_6 KILN 1 ID FAN MOTOR WINDING TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_6 | 2
TE1_314_7 | KILN1_BH | TE1_314_7 KILN 1 ID FAN MOTOR WINDING TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_7 | 2
TE1_314_8 | KILN1_BH | TE1_314_8 KILN 1 ID FAN MOTOR WINDING TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_8 | 2
TE1_314_9 | KILN1_BH | TE1_314_9 KILN 1 ID FAN MOTOR WINDING TEMP. | F | 1000 | 0 | 0 | 0 | KILN1_BH_READ | TE1_314_9 | 2
VE1_314_1 | KILN1_BH | VE1_314_1 KILN 1 ID FAN MOTOR VIB. SENSOR END HORI | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_1 | 2
VE1_314_2 | KILN1_BH | VE1_314_2 KILN 1 ID FAN MOTOR VIB. SENSOR FAR END | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_2 | 2
VE1_314_3 | KILN1_BH | VE1_314_3 KILN 1 ID FAN MOTOR VIB. SENSOR END HORI | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_3 | 2
VE1_314_4 | KILN1_BH | VE1_314_4 KILN 1 ID FAN MOTOR VIB. SENSOR END VERT | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_4 | 2
VE1_314_5 | KILN1_BH | VE1_313_5 KILN 1 ID FAN MOTOR VIB. SENSOR SIDE HOR | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_5 | 2
VE1_314_6 | KILN1_BH | VE1_314_6 KILN 1 ID FAN MOTOR VIB. SENSOR SIDE VER | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_6 | 2
VE1_314_7 | KILN1_BH | VE1_314_7 KILN 1 ID FAN MOTOR VIB. SENSOR FAR SIDE | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_7 | 2
VE1_314_8 | KILN1_BH | VE1_314_8 KILN 1 ID FAN MOTOR VIB. SENSOR FAR SIDE | IPS | 1 | 0 | 0 | 0 | KILN1_BH_READ | VE1_314_8 | 2
WP361_2_OFF | KILN1_BH |  | None | KILN1_BH_ALARM | Local_Timer(1).DN | FN 1-314 SPEED SET TO ZERO
ADEQ_K2FUELTOT_HOUR | Kiln2 | KILN 2 TOTAL TONS FUEL PER HOUR | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:155 | KILN 1 TONS LIMESTONE PER HOUR
ADEQ_K2LIMETOT_HOUR | Kiln2 | KILN 2 TOTAL TONS LIME PER HOUR | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:153 | KILN 1 TONS LIMESTONE PER HOUR
ADEQ_K2STR | Kiln2 | KILN 2 STROKES/HR | STROKES/HR | 250 | 0 | 0 | 0 | PLC_FLTREAD | F9:207 | KILN 2 STROKES/HR
ADEQ_K2STR_HOUR | Kiln2 | KILN 2 STROKES/HR - HOURLY READING | STROKES/HR | 300 | 0 | 0 | 0 | PLC_FLTREAD | F9:224 | KILN 2 STROKES/HR - HOURLY READING
ADEQ_K2TONFUELLSPHR | Kiln2 | KILN 2 TONS COAL/COKE AND LIMESTONE PER HOUR | TONS/HR | 150 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:212 | KILN 2 TONS COAL/COKE AND LIMESTONE PER HOUR
ADEQ_K2TONFUELLSPHR_HOUR | Kiln2 | KILN 2 TONS FUEL AND LIMESTONE PER HOUR - HOURLY | TONS/HR | 150 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:229 | KILN 2 TONS FUEL AND LIMESTONE PER HOUR - HOURLY
ADEQ_K2TONFUELPHR | Kiln2 | KILN 2 TONS COAL/COKE PER HOUR | TONS/HR | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:211 | KILN 2 TONS COAL/COKE PER HOUR
ADEQ_K2TONFUELPHR_HOUR | Kiln2 | KILN 2 TONS COAL/COKE PER HOUR - HOURLY READING | TONS/HR | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:228 | KILN 2 TONS COAL/COKE PER HOUR - HOURLY READING
ADEQ_K2TONLSPHR | Kiln2 | KILN 2 TONS LIMESTONE PER HOUR | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:210 | KILN 2 TONS LIMESTONE PER HOUR
ADEQ_K2TONLSPHR_HOUR | Kiln2 | KILN 2 TONS LIMESTONE PER HOUR - HOURLY READING | TONS/HR | 125 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:227 | KILN 2 TONS LIMESTONE PER HOUR - HOURLY READING
ADEQ_K2TONLSPSTR | Kiln2 | KILN 2 TONS LIMESTONE PER STROKE | TON/STROKE | 1 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:209 | KILN 2 TONS LIMESTONE PER STROKE
ADEQ_K2TONLSPSTR_HOUR | Kiln2 | KILN 2 TONS LIMESTONE PER STROKE - HOURLY READING | TON/STROKE | 1 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:226 | KILN 2 TONS LIMESTONE PER STROKE - HOURLY READING
ADEQ_K2TOTSTR | Kiln2 | KILN 2 TOTAL STROKES | TOT | 10000 | 10 | 0 | 0 | PLC_FLTREAD | F9:208 | KILN 2 TOTAL STROKES
ADEQ_K2TOTSTR_DAY | Kiln2 | KILN 2 TOTAL STROKES - DAILY | STROKES | 9999 | 1 | 0 | 0 | PLC_FLTREAD | F9:123 | KILN 2 TOTAL STROKES - DAILY
ADEQ_K2TOTSTR_HOUR | Kiln2 | KILN 2 TOTAL STROKES - HOURLY READING | STROKES | 10000 | 1 | 0 | 0 | PLC_FLTREAD | F9:225 | KILN 2 TOTAL STROKES - HOURLY READING
ADEQ_K2TOTTONLS | Kiln2 | KILN 2 TOTAL TONS LIMESTONE | TONS | 2500 | 1 | 0 | 0 | PLC_FLTREAD | F9:213 | KILN 2 TOTAL TONS LIMESTONE
ADEQ_K2TOTTONLS_DAY | Kiln2 | KILN 2 TOTAL TON LIMESTONE - DAILY | STROKES | 3000 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:124 | KILN 2 TOTAL TON LIMESTONE - DAILY
ADEQ_K2TOTTONLS_HOUR | Kiln2 | KILN 2 TOTAL TONS LIMESTONE - HOURLY READING | TONS | 2500 | 1 | 0 | 0 | PLC_FLTREAD | F9:230 | KILN 2 TOTAL TONS LIMESTONE - HOURLY READING
BDP_K2LIME | Kiln2 | KILN 2 LIME Best Demonstrated Performance | TON | 1200 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:77 | KILN 2 LIME TOTALIZER
BE2317_BYP | Kiln2 | BE 2-317 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/427 | BE 2-317 MOTION SWITCH BYPASSED
BE2317_IM | Kiln2 | BE 2-317 INTERLOCKS MET | None | PLC_DISCREAD | B3/411 | BE 2-317 INTERLOCKS MET
BE2317_JOGIN | Kiln2 | BE 2-317 JOG PLUG INSERTED | None | PLC_DISCREAD | I:55/07
BE2317_PBS | Kiln2 | BE 2-317 PC START | None | PLC_DISCWRITE | B100/214 | BE 2-317 PC START
BE2317_PBT | Kiln2 | BE 2-317 PC STOP | None | PLC_DISCWRITE | B100/230 | BE 2-317 PC STOP
BE2317FTS_ALM | Kiln2 | BE 2-317 FAILED TO START | On | PLC_ALARM | B101/327 | BE 2-317 FAILED TO START
BE2317MS_X | Kiln2 | BE 2-317 AUX CONTACT | Off | PLC_DISCREAD | I:57/17 | BE 2-317 STOPPED!!
BE2317MSF_ALM | Kiln2 | BE 2-317 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/328 | BE 2-317 MOTION SWITCH FAILURE
BELT401SSW | Kiln2 | VF 2-311 SELECTOR SWITCH FOR BELT 401 | None | PLC_DISCWRITE | B100/346 | VF 2-311 SELECTOR SWITCH FOR BELT 401
BELT420SSW | Kiln2 | VF 2-311 SELECTOR SWITCH FOR 420 BELT | None | PLC_DISCWRITE | B100/348 | VF 2-311 SELECTOR SWITCH FOR 420 BELT
BH2313_MOD# | Kiln2 | BH 2-313 ACTIVE MODULE # 0=NOT CYCLING | STR/HR | 15 | 0 | 0 | 0 | PLC_INTREAD | N102:28 | BH 2-313 ACTIVE MODULE # 0=NOT CYCLING
BM_2602_LUBE_FAILURE_ALM | Kiln2 | K2 Ball Mill Lube Failure | On | PLC_ALARM | B101/588 | K2 BALL MILL LUBE FAILURE!!!
BM1602_STARTALM | Kiln2 | BM 1 602 START-UP ALARM | None | PLC_ALARM | O:116/3 | BM 1 602 START-UP ALARM
BM2602_BEARINGTEMPHI | Kiln2 | BM 2-602 BEARING TEMP HI | None | PLC_DISCREAD | B101/601 | BM 2-602 BEARING TEMP HI
BM2602_IM | Kiln2 | BM 2-602 INTERLOCKS MET | None | PLC_DISCREAD | B3/391 | BM 2-602 INTERLOCKS MET
BM2602_IT | Kiln2 | BM 2-602 AMPS | A | 75 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:95 | BM 2-602 AMPS
BM2602_LT | Kiln2 | BM 2-602 MILL LEVEL | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:74 | BM 2-602 MILL LEVEL
BM2602_PBS | Kiln2 | BM 2-602 PC START | None | PLC_DISCWRITE | B100/12 | BM 2-602 PC START
BM2602_PBT | Kiln2 | BM 2-602 PC STOP | None | PLC_DISCWRITE | B100/13 | BM 2-602 PC STOP
BM2602_PDT | Kiln2 | BM 2-602 DIFFERENTIAL PRESSURE | "WC | 5 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:93 | BM 2-602 DIFFERENTIAL PRESSURE
BM2602_SSA_HMI | Kiln2 | BM 2-602 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1396
BM2602_STARTALM | Kiln2 | BM 2 602 START-UP ALARM | None | PLC_ALARM | O:15/14 | BM 2 602 START-UP ALARM
BM2602_TT_2 | Kiln2 | BM 2-602 OUTLET TEMP | °F | 1000 | 2 | 0 | 0 | PLC_INTREAD | N55:00 | BM 2-602 OUTLET TEMP
BM2602_TT_3 | Kiln2 | BM 2-602 OUTBOARD BEARING TEMP | F | 500 | 2 | 0 | 0 | PLC_INTREAD | N55:07 | BM 2-602 OUTBOARD BEARING TEMP
BM2602_TT_4 | Kiln2 | BM 2-602 INBOARD BEARING TEMP | F | 500 | 2 | 0 | 0 | PLC_INTREAD | N56:00 | BM 2-602 INBOARD BEARING TEMP
BM2602_TT_5 | Kiln2 | BM 2-602 GEARBOX TEMP | F | 500 | 2 | 0 | 0 | PLC_INTREAD | N56:07 | BM 2-602 GEARBOX TEMP
BM2602_VIB_LT | Kiln2 | BM 2-602 MILL LEVEL VIB | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:177 | BM 2-602 MILL LEVEL
BM2602FTS_ALM | Kiln2 | BM 2-602 FAILED TO START | On | PLC_ALARM | B101/336 | BM 2-602 FAILED TO START
BM2602INBEARINGTEMP_ALM | Kiln2 | BM 2-602 BEARING TEMPERATURE > 140 | On | PLC_ALARM | B101/480 | BM 2-602 BEARING TEMPERATURE > 140
BM2602INLETTEMPHI_ALM | Kiln2 | BM 2-602 INLET TEMPERATURE > 540 F | On | PLC_ALARM | B101/481 | BM 2-602 INLET TEMPERATURE > 540 F
BM2602LUBEFAIL_ALM | Kiln2 | BM 2602 LUBE FAILURE! | None | PLC_ALARM | B101/588 | BM 2602 LUBE FAILURE!
BM2602MS_X | Kiln2 | BM 2-602 AUX FDBK | Off | PLC_DISCREAD | I:17/16 | BM 2-602 STOPPED
BM2602OUTBEARINGTEMP_ALM | Kiln2 | BM 2-602 BEARING TEMPERATURE > 140 | On | PLC_ALARM | B101/600 | BM 2-602 BEARING TEMPERATURE > 140
BM2602OUTLETTEMPHI_ALM | Kiln2 | BM 2-602 OUTLET TEMPERATURE > 180 F | On | PLC_ALARM | B101/482 | BM 2-602 OUTLET TEMPERATURE > 180 F
BM2602TT_1 | Kiln2 | BM 2-602 INLET TEMP | °F | 1000 | 2 | 0 | 0 | PLC_INTREAD | N55:04 | BM 2-602 INLET TEMP
BM2602TT1_PIDSP | Kiln2 | BM INLET TEMP PID SP FOR FV 2-215 | F | 540 | 1 | 0 | 500 | PLC_INTWRITE | N102:62 | BM INLET TEMP PID SP FOR FV 2-215
BM2602TT2_PIDSP | Kiln2 | BM OUTLET TEMP PID SP FOR FV 2-215 | F | 200 | 1 | 0 | 160 | PLC_INTWRITE | N102:61 | BM OUTLET TEMP PID SP FOR FV 2-215
BN8210HL_ALM | Kiln2 | CHAT BIN 210 HIGH LEVEL! | On | PLC_ALARM | I:23/00 | CHAT BIN 210 HIGH LEVEL!
BOTHBELTSSSW | Kiln2 | VF 2-311 SELECTOR SWITCH FOR BOTH BELTS | None | PLC_DISCWRITE | B100/347 | VF 2-311 SELECTOR SWITCH FOR BOTH BELTS
BU2308PT | Kiln2 | KILN 2 BURNER PRESSURE | "H2O | 10 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:94 | KILN 2 BURNER PRESSURE
BV2518_EN | Kiln2 | BV 2-518 ENABLED TO RUN | None | PLC_DISCREAD | B3/508 | BV 2-518 ENABLED TO RUN
BV2518_IM | Kiln2 | BV 2-518 INTERLOCKS MET | None | PLC_DISCREAD | B3/506 | BV 2-518 INTERLOCKS MET
BV2518_PAUSE | Kiln2 | BV 2-518 PAUSE TIMER SETPOINT | SEC | 120 | 1 | 0 | 0 | PLC_INTWRITE | T4:516.PRE | BV 2-518 PAUSE TIMER SETPOINT
BV2518_PBS | Kiln2 | BV 2-518 PC START | None | PLC_DISCWRITE | B100/705 | BV 2-518 PC START
BV2518_PBT | Kiln2 | BV 2-518 PC STOP | None | PLC_DISCWRITE | B100/704 | BV 2-518 PC STOP
BV2518_RUN | Kiln2 | BV 2-518 RUN TIMER SETPOINT | SEC | 120 | 1 | 0 | 0 | PLC_INTWRITE | T4:517.PRE | BV 2-518 RUN TIMER SETPOINT
BV2518_SSA_HMI | Kiln2 | BV 2-518 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1416
BV2518FTS_ALM | Kiln2 | BV 2-518 FAILED TO START | On | PLC_ALARM | B101/334 | BV 2-518 FAILED TO START
BV2518MS_X | Kiln2 | BV 2-518 AUX FDBK | None | PLC_DISCREAD | I:221/02 | BV 2-518 AUX FDBK
C2310_HILVL | Kiln2 | C 2-310 COOLER HIGH LEVEL | None | PLC_DISCREAD | N102:167/1 | C 2-310 COOLER HIGH LEVEL
C2310_LOLVL | Kiln2 | C 2-310 COOLER LOW LEVEL | None | PLC_DISCREAD | N102:168/1 | C 2-310 COOLER LOW LEVEL
C2310HI_ALM | Kiln2 | C 2-310 HIGH LEVEL TOO LONG | On | PLC_ALARM | T4:342.DN | C 2-310 HIGH LEVEL TOO LONG
C2310HIGH_ALMSP | Kiln2 | C 2-310 HIGH LEVEL TOO LONG | SEC | 3600 | 0 | 0 | 0 | PLC_INTWRITE | T4:342.PRE | C 2-310 HIGH LEVEL TOO LONG
C2310LO_ALM | Kiln2 | C 2-310 LOW LEVEL TOO LONG | On | PLC_ALARM | T4:343.DN | C 2-310 LOW LEVEL TOO LONG
C2310LOW_ALMSP | Kiln2 | C 2-310 LOW LEVEL TOO LONG | SEC | 7200 | 0 | 0 | 0 | PLC_INTWRITE | T4:343.PRE | C 2-310 LOW LEVEL TOO LONG
CA2320MS_X | Kiln2 | CA 2-323-B AUX FDBK | Off | PLC_DISCREAD | I:205/17 | CA 2-323-B STOPPED
CM2602TT_1_TREND | Kiln2 | KILN 2 COAL MILL INLET TEMPERATURE |  | 800 | 2 | 0 | KILN 2 COAL MILL INLET TEMPERATURE | 0 | 0 | 0
CM2602TT_2_TREND | Kiln2 | KILN 2 COAL MILL OUTLET TEMPERATURE |  | 400 | 2 | 0 | KILN 2 COAL MILL OUTLET TEMPERATURE | 0 | 0 | 0
CO2310FT_2 | Kiln2 | Cooler Air Flow - Pitot tube | "H2O | 3 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:77 | Cooler Air Flow - Pitot tube
CO2310TT_1 | Kiln2 | CO 2-310 DISCHARGE ALARM | F | 2000 | 5 | 0 | 0 | PLC_INTREAD | N55:06 | CO 2-310 DISCHARGE ALARM
CO2310TT_2 | Kiln2 | CO 2-310 PRODUCT DISCHARGE TEMP | °F | 2000 | 5 | 0 | 0 | PLC_INTREAD | N56:01 | CO 2-310 PRODUCT DISCHARGE TEMP
CO2310TT_2_TREND | Kiln2 | KILN 2 COOLER PRODUCT DISCH. TEMPERATURE | DEG F | 1000 | 2 | 0 | KILN 2 COOLER PRODUCT DISCH. TEMPERATURE | 0 | 0 | 0
CO2310TT_2HA_SP | Kiln2 | KILN #2 COOLER PRODUCT TEMP ALARM SETPOINT | F | 850 | 5 | 0 | 0 | PLC_INTWRITE | N7:31 | KILN #2 COOLER PRODUCT TEMP ALARM SETPOINT
CO2310TT_3 | Kiln2 | KILN 2 BELOW GRATE AIR TEMPERATURE | °F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N57:0 | KILN 2 SECONDARY AIR TEMPERATURE
CO2310TT_3_STREND | Kiln2 | KILN #2 SECONDARY AIR STARTUP TEMP RANGE - TRENDS | DEG F | 1000 | 5 | 0 | KILN #2 SECONDARY AIR STARTUP TEMP RANGE - TRENDS | 0 | 0 | 0
CO2310TT_3_TREND | Kiln2 | KILN 2 SECONDARY AIR TEMPERATURE | DEG F | 1800 | 5 | 0 | KILN 2 SECONDARY AIR TEMPERATURE | 0 | 0 | 0
CO2310TT_4 | Kiln2 | KILN 2 COOLER GRATE TEMPERATURE | °F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N57:5 | KILN 2 SECONDARY AIR TEMPERATURE
CO2310TT_E | Kiln2 | KILN 2 EAST COOLER TEMPERATURE | F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N56:06 | KILN 2 EAST COOLER TEMPERATURE
CO2310TT_N | Kiln2 | KILN 2 NORTH COOLER TEMPERATURE | F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N56:03 | KILN 2 NORTH COOLER TEMPERATURE
CO2310TT_S | Kiln2 | KILN 2 SOUTH COOLER TEMPERATURE | F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N56:04 | KILN 2 SOUTH COOLER TEMPERATURE
CO2310TT_W | Kiln2 | KILN 2 WEST COOLER TEMPERATURE | F | 3000 | 5 | 0 | 0 | PLC_INTREAD | N56:05 | KILN 2 WEST COOLER TEMPERATURE
DA2313_SP | Kiln2 | DA 2-313 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:35 | DA 2-313 PC SETPOINT
DA2313_ZT | Kiln2 | DA 2-313 POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F8:21 | DA 2-313 POSITION
DA2313E_CLOSED | Kiln2 | DA 2-313-E IN CLOSED POSITION | None | PLC_DISCREAD | I:206/11 | DA 2-313-E IN CLOSED POSITION
DA2313E_OPEN | Kiln2 | DA 2-313-E IN OPEN POSITION! | On | PLC_DISCREAD | I:206/10 | DA 2-313-E IN OPEN POSITION!
DA2313E_PCCLOSE | Kiln2 | DA 2-313-E PC CLOSE DAMPER | None | PLC_DISCWRITE | B100/487 | DA 2-313-E PC CLOSE DAMPER
DA2313E_PCOPEN | Kiln2 | DA 2-313-E PC OPEN DAMPER | None | PLC_DISCWRITE | B100/486 | DA 2-313-E PC OPEN DAMPER
DA2313EFTC_ALM | Kiln2 | DA 2-313-E FAILED TO CLOSE! | On | PLC_ALARM | B101/142 | DA 2-313-E FAILED TO CLOSE!
DA2313EFTO_ALM | Kiln2 | DA 2-313-E FAILED TO OPEN! | On | PLC_ALARM | B101/141 | DA 2-313-E FAILED TO OPEN!
DA2313ESTUCK_ALM | Kiln2 | DA 2-313-E STUCK! | On | PLC_ALARM | B101/143 | DA 2-313-E STUCK!
DA2313HIPID_SP | Kiln2 | DA 2-313 HI DAMPER PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N98:11 | DA 2-313 HI DAMPER PID SP
DA2313LOWPID_SP | Kiln2 | DA 2-313 LOW PID DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N98:12 | DA 2-313 LOW PID DAMPER SP
DA2313MAN_SP | Kiln2 | DA 2-313 BAGHOUSE BLEED AIR DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_FLTWRITE | F8:41 | DA 2-313 BAGHOUSE BLEED AIR DAMPER SP
DA2313PID_%RUN | Kiln2 | KILN 2 BLEED AIR PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:361 | KILN 2 BLEED AIR PID % RUNTIME - TODAY
DA2313PID_%RUN_YEST | Kiln2 | KILN 2 BLEED AIR PID % RUNTIME - PAST | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F9:363 | KILN 2 BLEED AIR PID % RUNTIME - PAST
DA2313PID_AM | Kiln2 | DA 2-313 BH TEMP PID AUTO/MANUAL | None | PLC_DISCREAD | N98:0/1 | DA 2-313 BH TEMP PID AUTO/MANUAL
DA2313PID_AVAIL | Kiln2 | KILN 2 BLEED AIR PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:360 | KILN 2 BLEED AIR PID AVAIL RUN HOURS - TODAY
DA2313PID_AVAIL_YEST | Kiln2 | KILN 2 BLEED AIR PID AVAIL RUN HOURS - PAST | HRS | 24 | 0 | 0 | 0 | PLC_FLTREAD | F9:362 | KILN 2 BLEED AIR PID AVAIL RUN HOURS - PAST
DA2313PID_CV | Kiln2 | DA 2-313 PID CV (DA 2-313 %) |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N98:24 | DA 2-313 PID CV (DA 2-313 %)
DA2313PID_DB | Kiln2 | DA 2-313 PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N98:9 | DA 2-313 PID DEADBAND
DA2313PID_DR | Kiln2 | DA 2-313 PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N98:5 | DA 2-313 PID DR
DA2313PID_ER | Kiln2 | DA 2-313 PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N98:15 | DA 2-313 PID ERROR
DA2313PID_PG | Kiln2 | DA 2-313 PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N98:3 | DA 2-313 PID PG
DA2313PID_PV | Kiln2 | DA 2-313 PID PV (BH INLET T) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N98:23 | DA 2-313 PID PV (BH INLET T) 0-4095
DA2313PID_RT | Kiln2 | DA 2-313 PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N98:4 | DA 2-313 PID RT
DA2313PID_SP | Kiln2 | DA 2-313 PID SP - SP = BH INLET T |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N98:2 | DA 2-313 PID SP - SP = BH INLET T
DA2313PID_TB | Kiln2 | DA 2-313 PID TB (DA 2-313 %) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N98:25 | DA 2-313 PID TB (DA 2-313 %) 0-4095
DA2313PID_UT | Kiln2 | DA 2-313 PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | N98:13 | DA 2-313 PID UPDATE TIME
DC2313_DP | Kiln2 | DC 2-313 DIFF PRESSURE | "WC | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:20 | DC 2-313 DIFF PRESSURE
DC231310DMPR_TOG | Kiln2 | DC 2-313-10 PC TOGGLE MOD 10 OUTLET DAMPER | None | PLC_DISCWRITE | B100/677 | DC 2-313-10 PC TOGGLE MOD 10 OUTLET DAMPER
DC231310MODIN_CLOSE | Kiln2 | DC 2-313 MOD #10 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:204/11 | DC 2-313 MOD #10 INLET DAMPER CLOSED
DC231310MODIN_OPEN | Kiln2 | DC 2-313 MOD #10 INLET DAMPER OPEN | None | PLC_DISCREAD | I:204/10 | DC 2-313 MOD #10 INLET DAMPER OPEN
DC231310MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #10 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:204/13 | DC 2-313 MOD #10 OUTLET DAMPER CLOSED
DC231310MODOUT_OPEN | Kiln2 | DC 2-313 MOD #10 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:204/12 | DC 2-313 MOD #10 OUTLET DAMPER OPEN
DC23131DMPR_TOG | Kiln2 | DC 2-313-1 PC TOGGLE MOD 1 OUTLET DAMPER | None | PLC_DISCWRITE | B100/668 | DC 2-313-1 PC TOGGLE MOD 1 OUTLET DAMPER
DC23131MODIN_CLOSE | Kiln2 | DC 2-313 MOD #1 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:200/01 | DC 2-313 MOD #1 INLET DAMPER CLOSED
DC23131MODIN_OPEN | Kiln2 | DC 2-313 MOD #1 INLET DAMPER OPEN | None | PLC_DISCREAD | I:200/00 | DC 2-313 MOD #1 INLET DAMPER OPEN
DC23131MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #1 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:200/03 | DC 2-313 MOD #1 OUTLET DAMPER CLOSED
DC23131MODOUT_OPEN | Kiln2 | DC 2-313 MOD #1 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:200/02 | DC 2-313 MOD #1 OUTLET DAMPER OPEN
DC23132DMPR_TOG | Kiln2 | DC 2-313-2 PC TOGGLE MOD 2 OUTLET DAMPER | None | PLC_DISCWRITE | B100/673 | DC 2-313-2 PC TOGGLE MOD 2 OUTLET DAMPER
DC23132MODIN_CLOSE | Kiln2 | DC 2-313 MOD #2 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:200/11 | DC 2-313 MOD #2 INLET DAMPER CLOSED
DC23132MODIN_OPEN | Kiln2 | DC 2-313 MOD #2 INLET DAMPER OPEN | None | PLC_DISCREAD | I:200/10 | DC 2-313 MOD #2 INLET DAMPER OPEN
DC23132MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #2 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:200/13 | DC 2-313 MOD #2 OUTLET DAMPER CLOSED
DC23132MODOUT_OPEN | Kiln2 | DC 2-313 MOD #2 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:200/12 | DC 2-313 MOD #2 OUTLET DAMPER OPEN
DC23133DMPR_TOG | Kiln2 | DC 2-313-3 PC TOGGLE MOD 3 OUTLET DAMPER | None | PLC_DISCWRITE | B100/669 | DC 2-313-3 PC TOGGLE MOD 3 OUTLET DAMPER
DC23133MODIN_CLOSE | Kiln2 | DC 2-313 MOD #3 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:201/01 | DC 2-313 MOD #3 INLET DAMPER CLOSED
DC23133MODIN_OPEN | Kiln2 | DC 2-313 MOD #3 INLET DAMPER OPEN | None | PLC_DISCREAD | I:201/00 | DC 2-313 MOD #3 INLET DAMPER OPEN
DC23133MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #3 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:201/03 | DC 2-313 MOD #3 OUTLET DAMPER CLOSED
DC23133MODOUT_OPEN | Kiln2 | DC 2-313 MOD #3 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:201/02 | DC 2-313 MOD #3 OUTLET DAMPER OPEN
DC23134DMPR_TOG | Kiln2 | DC 2-313-4 PC TOGGLE MOD 4 OUTLET DAMPER | None | PLC_DISCWRITE | B100/674 | DC 2-313-4 PC TOGGLE MOD 4 OUTLET DAMPER
DC23134MODIN_CLOSE | Kiln2 | DC 2-313 MOD #4 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:201/11 | DC 2-313 MOD #4 INLET DAMPER CLOSED
DC23134MODIN_OPEN | Kiln2 | DC 2-313 MOD #4 INLET DAMPER OPEN | None | PLC_DISCREAD | I:201/10 | DC 2-313 MOD #4 INLET DAMPER OPEN
DC23134MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #4 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:201/13 | DC 2-313 MOD #4 OUTLET DAMPER CLOSED
DC23134MODOUT_OPEN | Kiln2 | DC 2-313 MOD #4 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:201/12 | DC 2-313 MOD #4 OUTLET DAMPER OPEN
DC23135DMPR_TOG | Kiln2 | DC 2-313-5 PC TOGGLE MOD 5 OUTLET DAMPER | None | PLC_DISCWRITE | B100/670 | DC 2-313-5 PC TOGGLE MOD 5 OUTLET DAMPER
DC23135MODIN_CLOSE | Kiln2 | DC 2-313 MOD #5 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:202/01 | DC 2-313 MOD #5 INLET DAMPER CLOSED
DC23135MODIN_OPEN | Kiln2 | DC 2-313 MOD #5 INLET DAMPER OPEN | None | PLC_DISCREAD | I:202/00 | DC 2-313 MOD #5 INLET DAMPER OPEN
DC23135MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #5 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:202/03 | DC 2-313 MOD #5 OUTLET DAMPER CLOSED
DC23135MODOUT_OPEN | Kiln2 | DC 2-313 MOD #5 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:202/02 | DC 2-313 MOD #5 OUTLET DAMPER OPEN
DC23136DMPR_TOG | Kiln2 | DC 2-313-6 PC TOGGLE MOD 6 OUTLET DAMPER | None | PLC_DISCWRITE | B100/675 | DC 2-313-6 PC TOGGLE MOD 6 OUTLET DAMPER
DC23136MODIN_CLOSE | Kiln2 | DC 2-313 MOD #6 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:202/11 | DC 2-313 MOD #6 INLET DAMPER CLOSED
DC23136MODIN_OPEN | Kiln2 | DC 2-313 MOD #6 INLET DAMPER OPEN | None | PLC_DISCREAD | I:202/10 | DC 2-313 MOD #6 INLET DAMPER OPEN
DC23136MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #6 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:202/13 | DC 2-313 MOD #6 OUTLET DAMPER CLOSED
DC23136MODOUT_OPEN | Kiln2 | DC 2-313 MOD #6 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:202/12 | DC 2-313 MOD #6 OUTLET DAMPER OPEN
DC23137DMPR_TOG | Kiln2 | DC 2-313-7 PC TOGGLE MOD 7 OUTLET DAMPER | None | PLC_DISCWRITE | B100/671 | DC 2-313-7 PC TOGGLE MOD 7 OUTLET DAMPER
DC23137MODIN_CLOSE | Kiln2 | DC 2-313 MOD #7 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:203/01 | DC 2-313 MOD #7 INLET DAMPER CLOSED
DC23137MODIN_OPEN | Kiln2 | DC 2-313 MOD #7 INLET DAMPER OPEN | None | PLC_DISCREAD | I:203/00 | DC 2-313 MOD #7 INLET DAMPER OPEN
DC23137MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #7 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:203/03 | DC 2-313 MOD #7 OUTLET DAMPER CLOSED
DC23137MODOUT_OPEN | Kiln2 | DC 2-313 MOD #7 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:203/02 | DC 2-313 MOD #7 OUTLET DAMPER OPEN
DC23138DMPR_TOG | Kiln2 | DC 2-313-8 PC TOGGLE MOD 8 OUTLET DAMPER | None | PLC_DISCWRITE | B100/676 | DC 2-313-8 PC TOGGLE MOD 8 OUTLET DAMPER
DC23138MODIN_CLOSE | Kiln2 | DC 2-313 MOD #8 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:203/11 | DC 2-313 MOD #8 INLET DAMPER CLOSED
DC23138MODIN_OPEN | Kiln2 | DC 2-313 MOD #8 INLET DAMPER OPEN | None | PLC_DISCREAD | I:203/10 | DC 2-313 MOD #8 INLET DAMPER OPEN
DC23138MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #8 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:203/13 | DC 2-313 MOD #8 OUTLET DAMPER CLOSED
DC23138MODOUT_OPEN | Kiln2 | DC 2-313 MOD #8 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:203/12 | DC 2-313 MOD #8 OUTLET DAMPER OPEN
DC23139DMPR_TOG | Kiln2 | DC 2-313-9 PC TOGGLE MOD 9 OUTLET DAMPER | None | PLC_DISCWRITE | B100/672 | DC 2-313-9 PC TOGGLE MOD 9 OUTLET DAMPER
DC23139MODIN_CLOSE | Kiln2 | DC 2-313 MOD #9 INLET DAMPER CLOSED | None | PLC_DISCREAD | I:204/01 | DC 2-313 MOD #9 INLET DAMPER CLOSED
DC23139MODIN_OPEN | Kiln2 | DC 2-313 MOD #9 INLET DAMPER OPEN | None | PLC_DISCREAD | I:204/00 | DC 2-313 MOD #9 INLET DAMPER OPEN
DC23139MODOUT_CLOSE | Kiln2 | DC 2-313 MOD #9 OUTLET DAMPER CLOSED | None | PLC_DISCREAD | I:204/03 | DC 2-313 MOD #9 OUTLET DAMPER CLOSED
DC23139MODOUT_OPEN | Kiln2 | DC 2-313 MOD #9 OUTLET DAMPER OPEN | None | PLC_DISCREAD | I:204/02 | DC 2-313 MOD #9 OUTLET DAMPER OPEN
DC2313CLEANINGMODE_TOG | Kiln2 | DC 2-313 BAGHOUSE CLEANING MODE PC TOGGLE | None | PLC_DISCWRITE | B100/679 | DC 2-313 BAGHOUSE CLEANING MODE PC TOGGLE
DC2313DIFF_ALM | Kiln2 | KILN 2 BAGHOUSE HIGH DIFFERENTIAL PRESSURE | On | PLC_ALARM | B101/473 | KILN 2 BAGHOUSE HIGH DIFFERENTIAL PRESSURE
DC2313DP_SP | Kiln2 | DC 2-313 BAGHOUSE DP SP | "WC | 15 | 0.05 | 0 | 0 | PLC_FLTWRITE | F8:40 | DC 2-313 BAGHOUSE DP SP
DC2313IN_TT | Kiln2 | DC 2-313 INLET TEMP | °F | 1000 | 1 | 0 | 0 | PLC_INTREAD | N64:3 | DC 2-313 INLET TEMP
DC2313IN_TT2 | Kiln2 | DC 2-313 BACK-UP INLET TEMP | °F | 1000 | 1 | 0 | 0 | PLC_INTREAD | N64:4 | DC 2-313 BACK-UP INLET TEMP
DC2313INTT_SP | Kiln2 | DC 2-313 INLET TEMP PC PID SETPOINT | °F | 500 | 1 | 0 | 100 | PLC_INTWRITE | N7:27 | DC 2-313 INLET TEMP PC PID SETPOINT
DC2313INTT1_ALM | Kiln2 | KILN 2 BAGHOUSE INLET TEMPERATURE >480 | On | PLC_ALARM | B101/474 | KILN 2 BAGHOUSE INLET TEMPERATURE >480
DC2313INTT2_ALM | Kiln2 | KILN 2 BAGHOUSE INLET TEMPERATURE > 480 | On | PLC_ALARM | B101/475 | KILN 2 BAGHOUSE INLET TEMPERATURE > 480
DC2313INTTHI1_ALM | Kiln2 | KILN 2 BAGHOUSE INLET TEMPERATURE > 498 | On | PLC_ALARM | B101/476 | KILN 2 BAGHOUSE INLET TEMPERATURE > 498
DC2313INTTHI2_ALM | Kiln2 | KILN 2 BAGHOUSE INLET TEMPERATURE > 498 | On | PLC_ALARM | B101/477 | KILN 2 BAGHOUSE INLET TEMPERATURE > 498
DC2313INTTHIHI1_ALM | Kiln2 | KILN 2 BAGHOUSE INLET TEMPERATURE > 515 | On | PLC_ALARM | B101/582 | KILN 2 BAGHOUSE INLET TEMPERATURE > 515
DC2313INTTHIHI2_ALM | Kiln2 | KILN 2 BAGHOUSE INLET TEMPERATURE > 515 | On | PLC_ALARM | B101/583 | KILN 2 BAGHOUSE INLET TEMPERATURE > 515
DC2313MODE_TOG | Kiln2 | DC 2-313 BAGHOUSE MODULE CLEANING MODE | None | PLC_DISCWRITE | B100/680 | DC 2-313 BAGHOUSE MODULE CLEANING MODE
DC2313OUT_TT | Kiln2 | DC 2-313 OUTLET TEMP | DEG F | 1000 | 1 | 0 | 0 | PLC_INTREAD | N64:5 | DC 2-313 OUTLET TEMP
DC2313POP_RESET | Kiln2 | DC 2-313 POPPETS RESET TO OPEN | On | PLC_DISCWRITE | B100/529 | DC 2-313 POPPETS RESET TO OPEN
DC2313POP1_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #1 POPPET ALARM | On | PLC_ALARM | B101/280 | DC 2-313 BAGHOUSE MOD #1 POPPET ALARM
DC2313POP10_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #10 POPPET ALARM | On | PLC_ALARM | B101/289 | DC 2-313 BAGHOUSE MOD #10 POPPET ALARM
DC2313POP2_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #2 POPPET ALARM | On | PLC_ALARM | B101/281 | DC 2-313 BAGHOUSE MOD #2 POPPET ALARM
DC2313POP3_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #3 POPPET ALARM | On | PLC_ALARM | B101/282 | DC 2-313 BAGHOUSE MOD #3 POPPET ALARM
DC2313POP4_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #4 POPPET ALARM | On | PLC_ALARM | B101/283 | DC 2-313 BAGHOUSE MOD #4 POPPET ALARM
DC2313POP5_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #5 POPPET ALARM | On | PLC_ALARM | B101/284 | DC 2-313 BAGHOUSE MOD #5 POPPET ALARM
DC2313POP6_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #6 POPPET ALARM | On | PLC_ALARM | B101/285 | DC 2-313 BAGHOUSE MOD #6 POPPET ALARM
DC2313POP7_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #7 POPPET ALARM | On | PLC_ALARM | B101/286 | DC 2-313 BAGHOUSE MOD #7 POPPET ALARM
DC2313POP8_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #8 POPPET ALARM | On | PLC_ALARM | B101/287 | DC 2-313 BAGHOUSE MOD #8 POPPET ALARM
DC2313POP9_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #9 POPPET ALARM | On | PLC_ALARM | B101/288 | DC 2-313 BAGHOUSE MOD #9 POPPET ALARM
DC2313SEQ1_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #1 SEQUENCER ALARM | On | PLC_ALARM | B101/106 | DC 2-313 BAGHOUSE MOD #1 SEQUENCER ALARM
DC2313SEQ10_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #10 SEQUENCER ALARM | On | PLC_ALARM | B101/115 | DC 2-313 BAGHOUSE MOD #10 SEQUENCER ALARM
DC2313SEQ2_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #2 SEQUENCER ALARM | On | PLC_ALARM | B101/107 | DC 2-313 BAGHOUSE MOD #2 SEQUENCER ALARM
DC2313SEQ3_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #3 SEQUENCER ALARM | On | PLC_ALARM | B101/108 | DC 2-313 BAGHOUSE MOD #3 SEQUENCER ALARM
DC2313SEQ4_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #4 SEQUENCER ALARM | On | PLC_ALARM | B101/109 | DC 2-313 BAGHOUSE MOD #4 SEQUENCER ALARM
DC2313SEQ5_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #5 SEQUENCER ALARM | On | PLC_ALARM | B101/110 | DC 2-313 BAGHOUSE MOD #5 SEQUENCER ALARM
DC2313SEQ6_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #6 SEQUENCER ALARM | On | PLC_ALARM | B101/111 | DC 2-313 BAGHOUSE MOD #6 SEQUENCER ALARM
DC2313SEQ7_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #7 SEQUENCER ALARM | On | PLC_ALARM | B101/112 | DC 2-313 BAGHOUSE MOD #7 SEQUENCER ALARM
DC2313SEQ8_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #8 SEQUENCER ALARM | On | PLC_ALARM | B101/113 | DC 2-313 BAGHOUSE MOD #8 SEQUENCER ALARM
DC2313SEQ9_ALM | Kiln2 | DC 2-313 BAGHOUSE MOD #9 SEQUENCER ALARM | On | PLC_ALARM | B101/114 | DC 2-313 BAGHOUSE MOD #9 SEQUENCER ALARM
DC2313TIME_SP | Kiln2 | DC 2-313 TIME CYCLE PC SETPOINT | HRS | 25 | 1 | 0 | 0 | PLC_INTWRITE | C5:10.PRE | DC 2-313 TIME CYCLE PC SETPOINT
DC2319_PDT | Kiln2 | KILN 2 PRIMARY DUST COLLECTOR DP | "WC | 5 | 0.25 | 0 | 0 | PLC_FLTREAD | F9:435 | KILN 2 PRIMARY DUST COLLECTOR DP
DC2319_PT | Kiln2 | DC 2-319 EXIT STATIC PRESSURE | "WC | 50 | 0.25 | 0 | 0 | PLC_FLTREAD | F9:87 | DC 2-319 EXIT STATIC PRESSURE
DC2319EXIT_TT | Kiln2 | DC 2-319 EXIT TEMPERATURE | DEG F | 1000 | 1 | 0 | 0 | PLC_INTREAD | N59:4 | DC 2-319 EXIT TEMPERATURE
DC2319EXITTTHI_ALM | Kiln2 | DC 2-319 EXIT TEMPERATURE > 550 F | On | PLC_ALARM | B101/478 | DC 2-319 EXIT TEMPERATURE > 550 F
DM1_313_PCSP | Kiln2 | DM 1-313 PC SETPOINT | % | 100 | 1 | 0 | 0 | KILN1_BH_WRITE | DM1_313_PCSP | DA 2-313 PC SETPOINT
DM1_313_PID_UPD | Kiln2 | DM 1-313 PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | DM1_313_PID.UPD | DA 2-313 PID UPDATE TIME
ESTTOT_K2LIME | Kiln2 | ESTIMATED KILN 2 LIME TOTALIZER AT STROKE RATE | TON | 1500 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:36 | KILN 1 LIME TOTALIZER
FH2309_DOOR | Kiln2 | FH 2-309 INDICATE HOOD DOOR OPEN/CLOSED FOR PID | None | PLC_DISCWRITE | B100/48 | FH 2-309 INDICATE HOOD DOOR OPEN/CLOSED FOR PID
FH2309DOOR_VIS | Kiln2 | FH 2-309 OPEN/CLOSE DOOR BUTTON VISIBILITY CONTROL | None | PLC_DISCREAD | B3/313 | FH 2-309 OPEN/CLOSE DOOR BUTTON VISIBILITY CONTROL
FN2210_AUTO | Kiln2 | FN 2-210 IN AUTO POSITION | None | PLC_DISCREAD | I:231/12 | FN 2-210 IN AUTO POSITION
FN2210_IM | Kiln2 | FN 2-210 INTERLOCKS MET | None | PLC_DISCREAD | B3/720 | FN 2-210 INTERLOCKS MET
FN2210_PBS | Kiln2 | FN 2-210 PC START | None | PLC_DISCWRITE | B100/496 | FN 2-210 PC START
FN2210_PBT | Kiln2 | FN 2-210 PC STOP | None | PLC_DISCWRITE | B100/497 | FN 2-210 PC STOP
FN2210_SSA_HMI | Kiln2 | FN 2-210 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1426
FN2210FTS_ALM | Kiln2 | FN 2-210 FAILED TO START! | On | PLC_ALARM | B101/164 | FN 2-210 FAILED TO START!
FN2210MS_X | Kiln2 | FN 2-210 AUX FDBK | Off | PLC_DISCREAD | I:231/13 | FN 2-210 STOPPED!
FN2215_IM | Kiln2 | FN 2-215 INTERLOCKS MET | None | PLC_DISCREAD | B3/387 | FN 2-215 INTERLOCKS MET
FN2215_PBS | Kiln2 | FN 2-215 PC START | None | PLC_DISCWRITE | B100/334 | FN 2-215 PC START
FN2215_PBT | Kiln2 | FN 2-215 PC STOP | None | PLC_DISCWRITE | B100/335 | FN 2-215 PC STOP
FN2215_SSA_HMI | Kiln2 | FN 2-215 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1466
FN2215FTS_ALM | Kiln2 | FN 2-215 BECK COOLING FAN FAILED TO START | On | PLC_ALARM | B101/273 | FN 2-215 BECK COOLING FAN FAILED TO START
FN2215MS_X | Kiln2 | FN 2-215 BECK COOLING FAN AUX FDBK | Off | PLC_DISCREAD | I:16/10 | FN 2-215 STOPPED
FN2308A_IM | Kiln2 | FN 2-308-A INTERLOCKS MET | None | PLC_DISCREAD | B3/371 | FN 2-308-A INTERLOCKS MET
FN2308A_PBS | Kiln2 | FN 2-308-A PC START | None | PLC_DISCWRITE | B100/24 | FN 2-308-A PC START
FN2308A_PBT | Kiln2 | FN 2-308-A PC STOP | None | PLC_DISCWRITE | B100/25 | FN 2-308-A PC STOP
FN2308A_SSA_HMI | Kiln2 | FN 2-308A Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1381
FN2308A1_IM | Kiln2 | FN 2-308-A1 Interlocks Met | None | PLC_DISCREAD | B3/1193
FN2308A1_OVERLOADS | Kiln2 | FN 2-308-A1 Overloads OK (NC) | None | PLC_DISCREAD | I:60/06
FN2308A1_PBS | Kiln2 | FN 2-308-A1 PC Start | None | PLC_DISCWRITE | B100/571
FN2308A1_PBT | Kiln2 | FN 2-308-A1 PC Stop | None | PLC_DISCWRITE | B100/570
FN2308A1_SSA_HMI | Kiln2 | FN 2-308-A1 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1371
FN2308A1FTS_ALM | Kiln2 | FN 2-308-A1 Failed To Start! | On | PLC_ALARM | B101/571 | FN 2-308-A1 Failed To Start!
FN2308A1MS_X | Kiln2 | FN 2-308-A1 Running | Off | PLC_DISCREAD | I:60/07 | FN 2-308-A1 Off!!
FN2308AFTS_ALM | Kiln2 | FN 2-308-A FAILED TO START | On | PLC_ALARM | B101/277 | FN 2-308-A FAILED TO START
FN2308AMS_X | Kiln2 | FN 2-308-A AUX FDBK | Off | PLC_DISCREAD | I:16/04 | FN 2-308-A STOPPED
FN2308B1_IM | Kiln2 | FN 2-308-B1 Interlocks Met | None | PLC_DISCREAD | B3/1195
FN2308B1_OVERLOADS | Kiln2 | FN 2-308-B1 Overloads OK (NC) | None | PLC_DISCREAD | I:60/16
FN2308B1_PBS | Kiln2 | FN 2-308-B1 PC Start | None | PLC_DISCREAD | B100/612
FN2308B1_PBT | Kiln2 | FN 2-308-B1 PC Stop | None | PLC_DISCREAD | B100/611
FN2308B1_SSA_HMI | Kiln2 | FN 2-308-B1 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1376
FN2308B1FTS_ALM | Kiln2 | FN 2-308-B1 Failed To Start! | On | PLC_ALARM | B101/572 | FN 2-308-B1 Failed To Start!
FN2308B1MS_X | Kiln2 | FN 2-308-B1 Running | Off | PLC_DISCREAD | I:60/17 | FN 2-308-B1 Off!!
FN2312_IM | Kiln2 | FN 2-312 INTERLOCKS MET | None | PLC_DISCREAD | B3/373 | FN 2-312 INTERLOCKS MET
FN2312_IT | Kiln2 | FN 2-312 AMPS | A | 250 | 0.5 | 0 | 0 | PLC_FLTREAD | F84:9 | FN 2-312 AMPS
FN2312_IT_AH | Kiln2 | KN2 COOLER FAN CURRENT HIGH ALARM | On | PLC_ALARM | B3/1242 | KN2 COOLER FAN CURRENT HIGH ALARM
FN2312_PBS | Kiln2 | FN 2-312 PC START | None | PLC_DISCWRITE | B100/08 | FN 2-312 PC START
FN2312_PBT | Kiln2 | FN 2-312 PC STOP | None | PLC_DISCWRITE | B100/09 | FN 2-312 PC STOP
FN2312_PDT | Kiln2 | FN 2-312 D/P | "WC | 3 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:91 | FN 2-312 D/P
FN2312_PT | Kiln2 | FN 2-312 PRESSURE | "WC | 20 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:92 | FN 2-312 PRESSURE
FN2312_SSA_HMI | Kiln2 | FN 2-312 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1421
FN2312FTS_ALM | Kiln2 | FN 2-312 FAILED TO START | On | PLC_ALARM | B101/279 | FN 2-312 FAILED TO START
FN2312MS_X | Kiln2 | FN 2-312 AUX FDBK | Off | PLC_DISCREAD | B100:55/2 | FN 2-312 STOPPED
FN2314_DRIVE_FLT | Kiln2 | FN 2-314 DRIVE FAULT-- RESET DRIVE | On | PLC_DISCREAD | B100:51/3 | FN 2-314 DRIVE FAULT-- RESET DRIVE
FN2314_DRIVE_READY | Kiln2 | FN 2-314 VFD Ready | None | PLC_DISCREAD | B100:49/0 | FN 2-314 Current High High Alarm
FN2314_DRIVE_RPM | Kiln2 | FN 2-314 RPM | RPM | 1200 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:37 | FN 2-314 AMPS
FN2314_DRIVE_WRN | Kiln2 | FN 2-314 DRIVE WARNING-- CHECK DRIVE | On | PLC_DISCREAD | B100:51/2 | FN 2-314 DRIVE WARNING-- CHECK DRIVE
FN2314_IM | Kiln2 | FN 2-314 INTERLOCKS MET | None | PLC_DISCREAD | B3/369 | FN 2-314 INTERLOCKS MET
FN2314_IT_AH | Kiln2 | FN 2-314 Current High Alarm | On | PLC_DISCREAD | B101/267 | FN 2-314 Current High Alarm
FN2314_IT_AHH | Kiln2 | FN 2-314 Current High High Alarm | On | PLC_DISCREAD | B101/266 | FN 2-314 Current High High Alarm
FN2314_PBS | Kiln2 | FN 2-314 PC START | None | PLC_DISCWRITE | B100/344 | FN 2-314 PC START
FN2314_PBT | Kiln2 | FN 2-314 PC STOP | None | PLC_DISCWRITE | B100/345 | FN 2-314 PC STOP
FN2314_SPD_IND | Kiln2 | FN 2-314 Speed Ref Indication | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:82 | FN 2-314 AMPS
FN2314_SSA_HMI | Kiln2 | FN 2-314 Auto Man swith in HMI 0=Auto 1=Man | None | PLC_DISCWRITE | B3/1364 | FN 2-314 Auto Man swith in HMI 0=Auto 1=Man
FN2314_TLOCK | Kiln2 | FN 2-314 ID Fan Motor and Bearing Temp interlocks | Off | PLC_DISCREAD | B3/1367 | FN 2-314 ID Fan Motor and Bearing Temp interlocks
FN2314_VT1 | Kiln2 | FN 2-314 Motor-Outboard-Top Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:134
FN2314_VT2 | Kiln2 | FN 2-314 Motor-Outboard-Side Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:135
FN2314_VT3 | Kiln2 | FN 2-314 Motor-Inboard-Top Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:136
FN2314_VT4 | Kiln2 | FN 2-314 Motor-Inboard-Side Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:137
FN2314_VT5 | Kiln2 | FN 2-314 Fan-Inboard-Top Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:138
FN2314_VT6 | Kiln2 | FN 2-314 Fan-Inboard-Side Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:139
FN2314_VT7 | Kiln2 | FN 2-314 Fan-Outboard-Top Vibration | ips | 1 | 0.005 | 0 | 0 | PLC_FLTREAD | F9:140
FN2314FTS_ALM | Kiln2 | FN 2-314 FAILED TO START | On | PLC_ALARM | B101/310 | FN 2-314 FAILED TO START
FN2314IT | Kiln2 | FN 2-314 AMPS | A | 350 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:24 | FN 2-314 AMPS
FN2314MOTWIND1_TT | Kiln2 | FN 2-314 MOTOR WINDING #1 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:395 | FN 2-314 MOTOR WINDING #1 TEMP
FN2314MOTWIND1TT_ALM | Kiln2 | FN 2-314 MOTOR WINDING 1 TEMP HIGH | On | PLC_ALARM | B101/512 | FN 2-314 MOTOR WINDING 1 TEMP HIGH
FN2314MOTWIND1TTHH_ALM | Kiln2 | FN 2-314 MOT WINDING #1 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/518 | FN 2-314 MOT WINDING #1 TEMP HIHI - SHUTDOWN 3 MIN
FN2314MOTWIND1TTSD_ALM | Kiln2 | FN 2-314 MOTOR WINDING #1 SHUTDOWN FAN | On | PLC_ALARM | B101/524 | FN 2-314 MOTOR WINDING #1 SHUTDOWN FAN
FN2314MOTWIND2_TT | Kiln2 | FN 2-314 MOTOR WINDING #2 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:396 | FN 2-314 MOTOR WINDING #2 TEMP
FN2314MOTWIND2TT_ALM | Kiln2 | FN 2-314 MOTOR WINDING 2 TEMP HIGH | On | PLC_ALARM | B101/513 | FN 2-314 MOTOR WINDING 2 TEMP HIGH
FN2314MOTWIND2TTHH_ALM | Kiln2 | FN 2-314 MOT WINDING #2 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/519 | FN 2-314 MOT WINDING #2 TEMP HIHI - SHUTDOWN 3 MIN
FN2314MOTWIND2TTSD_ALM | Kiln2 | FN 2-314 MOTOR WINDING #2 SHUTDOWN FAN | On | PLC_ALARM | B101/525 | FN 2-314 MOTOR WINDING #2 SHUTDOWN FAN
FN2314MOTWIND3_TT | Kiln2 | FN 2-314 MOTOR WINDING #3 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:397 | FN 2-314 MOTOR WINDING #3 TEMP
FN2314MOTWIND3TT_ALM | Kiln2 | FN 2-314 MOTOR WINDING 3 TEMP HIGH | On | PLC_ALARM | B101/514 | FN 2-314 MOTOR WINDING 3 TEMP HIGH
FN2314MOTWIND3TTHH_ALM | Kiln2 | FN 2-314 MOT WINDING #3 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/520 | FN 2-314 MOT WINDING #3 TEMP HIHI - SHUTDOWN 3 MIN
FN2314MOTWIND3TTSD_ALM | Kiln2 | FN 2-314 MOTOR WINDING #3 SHUTDOWN FAN | On | PLC_ALARM | B101/526 | FN 2-314 MOTOR WINDING #3 SHUTDOWN FAN
FN2314MOTWIND4_TT | Kiln2 | FN 2-314 MOTOR WINDING #4 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:398 | FN 2-314 MOTOR WINDING #4 TEMP
FN2314MOTWIND4TT_ALM | Kiln2 | FN 2-314 MOTOR WINDING 4 TEMP HIGH | On | PLC_ALARM | B101/515 | FN 2-314 MOTOR WINDING 4 TEMP HIGH
FN2314MOTWIND4TTHH_ALM | Kiln2 | FN 2-314 MOT WINDING #4 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/521 | FN 2-314 MOT WINDING #4 TEMP HIHI - SHUTDOWN 3 MIN
FN2314MOTWIND4TTSD_ALM | Kiln2 | FN 2-314 MOTOR WINDING #4 SHUTDOWN FAN | On | PLC_ALARM | B101/527 | FN 2-314 MOTOR WINDING #4 SHUTDOWN FAN
FN2314MOTWIND5_TT | Kiln2 | FN 2-314 MOTOR WINDING #5 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:399 | FN 2-314 MOTOR WINDING #5 TEMP
FN2314MOTWIND5TT_ALM | Kiln2 | FN 2-314 MOTOR WINDING 5 TEMP HIGH | On | PLC_ALARM | B101/516 | FN 2-314 MOTOR WINDING 5 TEMP HIGH
FN2314MOTWIND5TTHH_ALM | Kiln2 | FN 2-314 MOT WINDING #5 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/522 | FN 2-314 MOT WINDING #5 TEMP HIHI - SHUTDOWN 3 MIN
FN2314MOTWIND5TTSD_ALM | Kiln2 | FN 2-314 MOTOR WINDING #5 SHUTDOWN FAN | On | PLC_ALARM | B101/528 | FN 2-314 MOTOR WINDING #5 SHUTDOWN FAN
FN2314MOTWIND6_TT | Kiln2 | FN 2-314 MOTOR WINDING #6 TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:400 | FN 2-314 MOTOR WINDING #6 TEMP
FN2314MOTWIND6TT_ALM | Kiln2 | FN 2-314 MOTOR WINDING 6 TEMP HIGH | On | PLC_ALARM | B101/517 | FN 2-314 MOTOR WINDING 6 TEMP HIGH
FN2314MOTWIND6TTHH_ALM | Kiln2 | FN 2-314 MOT WINDING #6 TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/523 | FN 2-314 MOT WINDING #6 TEMP HIHI - SHUTDOWN 3 MIN
FN2314MOTWIND6TTSD_ALM | Kiln2 | FN 2-314 MOTOR WINDING #6 SHUTDOWN FAN | On | PLC_ALARM | B101/529 | FN 2-314 MOTOR WINDING #6 SHUTDOWN FAN
FN2314MS_X | Kiln2 | FN 2-314 AUX FDBK | Off | PLC_DISCREAD | B100:51/1 | FN 2-314 STOPPED
FN2314NFANBEAR_TT | Kiln2 | FN 2-314 NORTH FAN BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:391 | FN 2-314 NORTH FAN BEARING TEMP
FN2314NFANBEARTT_ALM | Kiln2 | FN 2-314 NORTH FAN BEARING TEMP HIGH | On | PLC_ALARM | B101/500 | FN 2-314 NORTH FAN BEARING TEMP HIGH TAKE CORRECTIVE ACTION!
FN2314NFANBEARTTHH_ALM | Kiln2 | FN 2-314 N. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/502 | FN 2-314 N. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN2314NFANBEARTTSD_ALM | Kiln2 | FN 2-314 NORTH FAN BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/504 | FN 2-314 NORTH FAN BEARING SHUTDOWN FAN
FN2314NMOTBEAR_TT | Kiln2 | FN 2-314 NORTH MOTOR BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:394 | FN 2-314 NORTH MOTOR BEARING TEMP
FN2314NMOTBEARTT_ALM | Kiln2 | FN 2-314 NORTH MOTOR BEARING TEMP HIGH | On | PLC_ALARM | B101/506 | FN 2-314 NORTH MOTOR BEARING TEMP HIGH TAKE CORRECTIVE ACTION!
FN2314NMOTBEARTTHH_ALM | Kiln2 | FN 2-314 N. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/508 | FN 2-314 N. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN2314NMOTBEARTTSD_ALM | Kiln2 | FN 2-314 NORTH MOT BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/510 | FN 2-314 NORTH MOT BEARING SHUTDOWN FAN
FN2314SFANBEAR_TT | Kiln2 | FN 2-314 SOUTH FAN BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:392 | FN 2-314 SOUTH FAN BEARING TEMP
FN2314SFANBEARTT_ALM | Kiln2 | FN 2-314 SOUTH FAN BEARING TEMP HIGH | On | PLC_ALARM | B101/501 | FN 2-314 SOUTH FAN BEARING TEMP HIGH TAKE CORRECTIVE ACTION!
FN2314SFANBEARTTHH_ALM | Kiln2 | FN 2-314 S. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/503 | FN 2-314 S. FAN BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN2314SFANBEARTTSD_ALM | Kiln2 | FN 2-314 SOUTH FAN BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/505 | FN 2-314 SOUTH FAN BEARING SHUTDOWN FAN
FN2314SMOTBEAR_TT | Kiln2 | FN 2-314 SOUTH MOTOR BEARING TEMP | DEG F | 428 | 1 | 0 | 32 | PLC_FLTREAD | F9:393 | FN 2-314 SOUTH MOTOR BEARING TEMP
FN2314SMOTBEARTT_ALM | Kiln2 | FN 2-314 SOUTH MOTOR BEARING TEMP HIGH | On | PLC_ALARM | B101/507 | FN 2-314 SOUTH MOTOR BEARING TEMP HIGH TAKE CORRECTIVE ACTION!
FN2314SMOTBEARTTHH_ALM | Kiln2 | FN 2-314 S. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN | On | PLC_ALARM | B101/509 | FN 2-314 S. MOT BEARING TEMP HIHI - SHUTDOWN 3 MIN
FN2314SMOTBEARTTSD_ALM | Kiln2 | FN 2-314 SOUTH MOTOR BEARING SHUTDOWN FAN | On | PLC_ALARM | B101/511 | FN 2-314 SOUTH MOTOR BEARING SHUTDOWN FAN
FN2315_SPD_SP | Kiln2 | FN 2-314 Speed Ref setpoint | % | 100 | 0.5 | 0 | 0 | PLC_FLTWRITE | F9:59 | FN 2-314 AMPS
FN2321_DCBYP | Kiln2 | FN 2-321 DUST COLLECTOR BYPASSED | On | PLC_DISCWRITE | B100/451 | FN 2-321 DUST COLLECTOR BYPASSED
FN2321_IM | Kiln2 | FN 2-321 INTERLOCKS MET | None | PLC_DISCREAD | B3/413 | FN 2-321 INTERLOCKS MET
FN2321_PBS | Kiln2 | FN 2-321 PC START | None | PLC_DISCWRITE | B100/216 | FN 2-321 PC START
FN2321_PBT | Kiln2 | FN 2-321 PC STOP | None | PLC_DISCWRITE | B100/232 | FN 2-321 PC STOP
FN2321FTS_ALM | Kiln2 | FN 2-321 FAILED TO START | On | PLC_ALARM | B101/330 | FN 2-321 FAILED TO START
FN2321MS_X | Kiln2 | FN 2-321 AUX CONTACT | Off | PLC_DISCREAD | I:56/0 | FN 2-321 STOPPED
FN2326_IM | Kiln2 | FN 2-326 INTERLOCKS MET | None | PLC_DISCREAD | B3/359 | FN 2-326 INTERLOCKS MET
FN2326_PBS | Kiln2 | FN 2-326 PC START | None | PLC_DISCWRITE | B100/328 | FN 2-326 PC START
FN2326_PBT | Kiln2 | FN 2-326 PC STOP | None | PLC_DISCWRITE | B100/329 | FN 2-326 PC STOP
FN2326_SSA_HMI | Kiln2 | FN 2-326 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1431
FN2326FTS_ALM | Kiln2 | FN 2-326 FAILED TO START | On | PLC_ALARM | B101/331 | FN 2-326 FAILED TO START
FN2326MS_X | Kiln2 | FN 2-326 AUX FDBK | Off | PLC_DISCREAD | I:14/12 | FN 2-326 STOPPED
FN2605_AUTO | Kiln2 | FN 2-605 IN AUTO | None | PLC_DISCREAD | I:016/01 | FN 2-605 IN AUTO
FN2605_HZ | Kiln2 | FN 2-605 VFD HERTZ | HZ | 60 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:438 | FN 2-605 VFD HERTZ
FN2605_IM | Kiln2 | FN 2-605 INTERLOCKS MET | None | PLC_DISCREAD | B3/383 | FN 2-605 INTERLOCKS MET
FN2605_PBS | Kiln2 | FN 2-605 PC START | None | PLC_DISCWRITE | B100/10 | FN 2-605 PC START
FN2605_PBT | Kiln2 | FN 2-605 PC STOP | None | PLC_DISCWRITE | B100/11 | FN 2-605 PC STOP
FN2605_PCVFD% | Kiln2 | FN 2-605 PC VFD % SP | % | 100 | 0.05 | 0 | 0 | PLC_FLTWRITE | F71:13 | FN 2-605 PC VFD % SP
FN2605_SSA_HMI | Kiln2 | FN 2-605 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1391
FN2605_VFDATSPD | Kiln2 | FN 2-605 VFD AT SPEED | None | PLC_DISCREAD | B3/978 | FN 2-605 VFD AT SPEED
FN2605_VFDCTRL | Kiln2 | FN 2-605 CONTROL VFD=1 A/F=0 | None | PLC_DISCWRITE | B100/485 | FN 2-605 CONTROL VFD=1 A/F=0
FN2605_VFDFLT | Kiln2 | FN 2-605 VFD FAULTED | On | PLC_ALARM | B101/150 | FN 2-605 VFD FAULTED
FN2605_VFDIM | Kiln2 | FN 2-605 VFD ENABLED | None | PLC_DISCREAD | O:222/15 | FN 2-605 VFD ENABLED
FN2605_VFDIT | Kiln2 | FN 2-605 VFD AMPS | A | 200 | 1 | 0 | 0 | PLC_FLTREAD | F9:439 | FN 2-605 VFD AMPS
FN2605_VFDPBS | Kiln2 | FN 2-605 VFD PC START | None | PLC_DISCWRITE | B100/73 | FN 2-605 VFD PC START
FN2605_VFDPBT | Kiln2 | FN 2-605 PC STOP VFD | None | PLC_DISCWRITE | B100/71 | FN 2-605 PC STOP VFD
FN2605_VFDRES | Kiln2 | FN 2-605 RESET VFD FAULT | None | PLC_DISCWRITE | B100/480 | FN 2-605 RESET VFD FAULT
FN2605FTS_ALM | Kiln2 | FN 2-605 FAILED TO START | On | PLC_ALARM | B101/339 | FN 2-605 FAILED TO START
FN2605IT | Kiln2 | FN 2-605 AMPS | A | 200 | 1 | 0 | 0 | PLC_FLTREAD | F9:80 | FN 2-605 AMPS
FN2605ITAMP_ALM | Kiln2 | FN 2-605 HIGH AMPS | On | PLC_ALARM | B101/483 | FN 2-605 HIGH AMPS
FN2605MOTTEMP_ALM | Kiln2 | FN 2-605 HIGH MOTOR TEMP | Off | PLC_ALARM | I:014/7 | FN 2-605 HIGH MOTOR TEMP
FN2605MS_X | Kiln2 | FN 2-605 AUX FDBK | Off | PLC_DISCREAD | I:17/15 | FN 2-605 STOPPED
FN2605TT | Kiln2 | FN 2-605 INLET TEMP | °F | 900 | 1 | 0 | 0 | PLC_INTREAD | N57:04 | FN 2-605 INLET TEMP
FN2605TT_TREND | Kiln2 | KILN 2 COAL MILL FAN INLET TEMPERATURE |  | 800 | 5 | 0 | KILN 2 COAL MILL FAN INLET TEMPERATURE | 0 | 0 | 0
FN2605VFD_COOLEN | Kiln2 | FN 2-605 PC Enable Cooldown | None | PLC_DISCWRITE | B100/532
FN2605VFD_COOLPER | Kiln2 | FN 2-605 Allow Cooldown Cycle Permissive | None | PLC_DISCREAD | B3/1207
FN2605VFDMS_X | Kiln2 | FN 2-605 VFD RUNNING | Off | PLC_DISCREAD | O:222/16 | FN 2-605 VFD STOPPED
FN2614_IM | Kiln2 | FN 2-614 INTERLOCKS MET | None | USCNEL202 | NEL_KN2_FN2614.FLT | FN 2-614 INTERLOCKS MET
FN2614_PBS | Kiln2 | FN 2-614 PC START | None | PLC_DISCWRITE | B100/22 | FN 2-614 PC START
FN2614_PBT | Kiln2 | FN 2-614 PC STOP | None | PLC_DISCWRITE | B100/23 | FN 2-614 PC STOP
FN2614_RESET | Kiln2 | Reset VFD Fault | None | USCNEL202 | NEL_KN2_FN2614.FLT_RST | PH 2-305 START STROKE RAMP UP
FN2614_SSA_HMI | Kiln2 | FN 2-614 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1386
FN2614FTS_ALM | Kiln2 | FN 2-614 VFD FAULTED | On | USCNEL202 | NEL_KN2_FN2614.FLT | FN 2-614 FAILED TO START
FN2614MS_X | Kiln2 | FN 2-614 AUX FDBK | Off | USCNEL202 | NEL_KN2_FN2614.AUX | FN 2-614 STOPPED
FV2211_OPEN95 | Kiln2 | FV 2-211 OPEN 95% | None | PLC_DISCREAD | B3/734 | FV 2-211 OPEN 95%
FV2211_PBS | Kiln2 | FV 2-211 OPEN | None | PLC_DISCWRITE | B100/478 | FV 2-211 OPEN
FV2211_PBT | Kiln2 | FV 2-211 CLOSE | None | PLC_DISCWRITE | B100/479 | FV 2-211 CLOSE
FV2211_SP | Kiln2 | FV 2-211 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:0 | FV 2-211 PC SETPOINT
FV2211_ZT | Kiln2 | FV 2-211 DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:44 | FV 2-211 DAMPER POSITION
FV2211OPEN95_ALM | Kiln2 | FV 2-211 OPEN LESS THAN 95% | None | PLC_ALARM | B3/734 | FV 2-211 OPEN LESS THAN 95%
FV2215_AM | Kiln2 | FV 2-215 PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100/82 | FV 2-215 PID AUTO MANUAL 1=AUTO 0=MANUAL
FV2215_APC | Kiln2 | FV 2-215 PID APC MANUAL 1=APC 0=MANUAL | None | PLC_DISCWRITE | B100/628 | FV 2-215 PID AUTO MANUAL 1=AUTO 0=MANUAL
FV2215_CV | Kiln2 | FV 2-215 CONTROL VARIABLE = FV2215_SP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N87:24 | FV 2-215 CONTROL VARIABLE = FV2215_SP
FV2215_ER | Kiln2 | FV 2-215 PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N87:15 | FV 2-215 PID ERROR
FV2215_PCSP | Kiln2 | FV 2-215 POSITION PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:41 | FV 2-215 POSITION PC SETPOINT
FV2215_PIDSP | Kiln2 | FV 2-215 PID SP - SP = BM OUTLET/INLET TEMP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N87:2 | FV 2-215 PID SP - SP = BM OUTLET/INLET TEMP
FV2215_PV | Kiln2 | FV 2-215 PROCESS VARIABLE =TEMPERATURE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N87:23 | FV 2-215 PROCESS VARIABLE =TEMPERATURE
FV2215_SP | Kiln2 | FV 2-215 POSITION SETPOINT | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:254 | FV 2-215 POSITION SETPOINT
FV2215_TB | Kiln2 | FV 2-215 TIEBACK VARIABLE = FV2215_ZT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N87:25 | FV 2-215 TIEBACK VARIABLE = FV2215_ZT
FV2215_ZT | Kiln2 | FV 2-215 COAL MILL TEMPERING TEE POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:64 | FV 2-215 COAL MILL TEMPERING TEE POSITION
FV2215HIPID_SP | Kiln2 | FV 2-215 HI DAMPER PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:60 | FV 2-215 HI DAMPER PID SP
FV2215LOWPID_SP | Kiln2 | FV 2-215 LOW PID DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:59 | FV 2-215 LOW PID DAMPER SP
FV2215PID_%RUN | Kiln2 | KILN 2 BM TEMPERING TEE PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:370 | KILN 2 BM TEMPERING TEE PID % RUNTIME - TODAY
FV2215PID_%RUN_YEST | Kiln2 | KILN 2 BM TEMPERING TEE PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:372 | KILN 2 BM TEMPERING TEE PID % RUNTIME - PAST
FV2215PID_AVAIL | Kiln2 | KILN 2 BM TEMPERING TEE PID AVAIL RUN HOURS- TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:369 | KILN 2 BM TEMPERING TEE PID AVAIL RUN HOURS- TODAY
FV2215PID_AVAIL_YEST | Kiln2 | KILN 2 BM TEMPERING TEE PID AVAIL RUN HOURS- PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:371 | KILN 2 BM TEMPERING TEE PID AVAIL RUN HOURS- PAST
FV2215PID_DB | Kiln2 | FV 2-215 PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N87:9 | FV 2-215 PID DEADBAND
FV2215PID_DR | Kiln2 | FV 2-215 PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N87:5 | FV 2-215 PID DR
FV2215PID_PG | Kiln2 | FV 2-215 PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N87:3 | FV 2-215 PID PG
FV2215PID_RT | Kiln2 | FV 2-215 PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N87:4 | FV 2-215 PID RT
FV2215PID_UT | Kiln2 | FV 2-215 PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | T4:362.PRE | FV 2-215 PID UPDATE TIME
FV2216_PCSP | Kiln2 | FV 2-216 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:32 | FV 2-216 PC SETPOINT
FV2216_SP | Kiln2 | FV 2-216 ACTUAL SETPOINT AUTO OR MANUAL | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:12 | FV 2-216 ACTUAL SETPOINT AUTO OR MANUAL
FV2216_ZT | Kiln2 | FV 2-216 DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:47 | FV 2-216 DAMPER POSITION
FV2216PID_%RUN | Kiln2 | KILN 2 OXYGEN PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:357 | KILN 2 OXYGEN PID % RUNTIME - TODAY
FV2216PID_%RUN_YEST | Kiln2 | KILN 2 OXYGEN PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:359 | KILN 2 OXYGEN PID % RUNTIME - PAST
FV2216PID_AVAIL | Kiln2 | KILN 2 OXYGEN PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:356 | KILN 2 OXYGEN PID AVAIL RUN HOURS - TODAY
FV2216PID_AVAIL_YEST | Kiln2 | KILN 2 OXYGEN PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:358 | KILN 2 OXYGEN PID AVAIL RUN HOURS - PAST
FV2220_SP | Kiln2 | FV 2-220 PC SERPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:29 | FV 2-220 PC SERPOINT
FV2220_ZT | Kiln2 | FV 2-220 DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:46 | FV 2-220 DAMPER POSITION
FV2228_PCSP | Kiln2 | FV 2-228 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:33 | FV 2-228 PC SETPOINT
FV2228_SP | Kiln2 | FV 2-228 ACTUAL SETPOINT AUTO OR MANUAL | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:11 | FV 2-228 ACTUAL SETPOINT AUTO OR MANUAL
FV2228_ZT | Kiln2 | FV 2-228 DAMPER POSITION | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:45 | FV 2-228 DAMPER POSITION
FV2228HIPID_SP | Kiln2 | FV 2-228 HI DAMPER PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N77:11 | FV 2-228 HI DAMPER PID SP
FV2228LOWPID_SP | Kiln2 | FV 2-228 LOW PID DAMPER SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N77:12 | FV 2-228 LOW PID DAMPER SP
FV2228PID_%RUN | Kiln2 | KILN 2 HOOD DRAFT PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:353 | KILN 2 HOOD DRAFT PID % RUNTIME - TODAY
FV2228PID_%RUN_YEST | Kiln2 | KILN 2 HOOD DRAFT PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:355 | KILN 2 HOOD DRAFT PID % RUNTIME - PAST
FV2228PID_AVAIL | Kiln2 | KILN 2 HOOD DRAFT PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:352 | KILN 2 HOOD DRAFT PID AVAIL RUN HOURS - TODAY
FV2228PID_AVAIL_YEST | Kiln2 | KILN 2 HOOD DRAFT PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:354 | KILN 2 HOOD DRAFT PID AVAIL RUN HOURS - PAST
FV2272_SP | Kiln2 | FV 2272 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:23 | FV 2272 PC SETPOINT
FV2272_TT | Kiln2 | FV 2-272 TEMPERATURE OF FUEL SYSTEM CROSS AIR | °F | 1000 | 4 | 0 | 0 | PLC_INTREAD | N55:05 | FV 2-272 TEMPERATURE OF FUEL SYSTEM CROSS AIR
FV2272_ZT | Kiln2 | FV 2-272 DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:39 | FV 2-272 DAMPER POSITION
FV2273_SP | Kiln2 | FV 2-273 PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:11 | FV 2-273 PC SETPOINT
FV2273_ZT | Kiln2 | FV 2-273 BM BYPASS DAMPER POSITION | % | 100 | 1 | 0 | 0 | PLC_FLTREAD | F9:38 | FV 2-273 BM BYPASS DAMPER POSITION
FV2310E_PCSP | Kiln2 | FV 2-310-E PC SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:8 | FV 2-310-E PC SP
FV2310E_ZT | Kiln2 | FV 2-310-E DAMPER POSITION | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:43 | FV 2-310-E DAMPER POSITION
FV2310N_PCSP | Kiln2 | FV 2-310-N PC SETPOINT | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:6 | FV 2-310-N PC SETPOINT
FV2310N_ZT | Kiln2 | FV 2-310-N DAMPER POSITION | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:40 | FV 2-310-N DAMPER POSITION
FV2310S_PCSP | Kiln2 | FV 2-310-S PC SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:7 | FV 2-310-S PC SP
FV2310S_ZT | Kiln2 | FV 2-310-S DAMPER POSITION | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:41 | FV 2-310-S DAMPER POSITION
FV2310W_PCSP | Kiln2 | FV 2-310-W PC SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:9 | FV 2-310-W PC SP
FV2310W_ZT | Kiln2 | FV 2-310 W DAMPER POSITION | % | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:42 | FV 2-310 W DAMPER POSITION
IV2211&2215_PBS | Kiln2 | IV 2-211 & IV 2-215 PC OPEN | None | PLC_DISCWRITE | B100/340 | IV 2-211 & IV 2-215 PC OPEN
IV2211&2215_PBT | Kiln2 | IV 2-211 & 2-215 PC CLOSE | None | PLC_DISCWRITE | B100/341 | IV 2-211 & 2-215 PC CLOSE
IV2211_CLOSED | Kiln2 | IV 2-211 CLOSED | On | PLC_DISCREAD | I:17/04 | KILN 2 ISOLATION VALVE 2-211 CLOSED
IV2211_OPEN | Kiln2 | IV 2-211 OPEN | None | PLC_DISCREAD | I:17/03 | IV 2-211 OPEN
IV2215_CLOSED | Kiln2 | IV 2-215 CLOSED | On | PLC_DISCREAD | I:17/06 | KILN 2 ISOLATION VALVE 2-215 CLOSED
IV2215_OPEN | Kiln2 | IV 2-215 OPEN | None | PLC_DISCREAD | I:17/05 | IV 2-215 OPEN
K1_FUEL_GRATES_PLUGGED | Kiln2 | Kiln 1 Fuel Grates Plugged | On | PLC_ALARM | B101/598 | KILN 1 FUEL GRATES PLUGGED!!!
K2_BLASTER_LOW_PRESSURE | Kiln2 | K2 Air Blaster Low Air Pressure Alarm | On | PLC_ALARM | B101/586 | K2 BLASTERS LOW AIR PRESSURE
K2_CANNON_FIRE_DELAY | Kiln2 | Kiln 2 Cannon Fire Delay Timer Preset | secs | 100 | 1 | 0 | 0 | PLC_INTREAD | N99:14
K2_FUEL_GRATES_PLUGGED | Kiln2 | Kiln 2 Fuel Grates Plugged | On | PLC_ALARM | I:17/10 | KILN 2 FUEL GRATES PLUGGED!!!
K2_LIMECO2 | Kiln2 | KILN 2 LIME CO2 RUNNING VALUE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F69:50 | KILN 2 LIME CO2 RUNNING VALUE
K2_LIMECO2_1 | Kiln2 | KILN 2 LIME CO2 6 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:52 | KILN 2 LIME CO2 6 AM
K2_LIMECO2_1_YEST | Kiln2 | KILN 2 LIME CO2 6 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:752 | KILN 2 LIME CO2 6 AM
K2_LIMECO2_10 | Kiln2 | KILN 2 LIME CO2 10:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:61 | KILN 2 LIME CO2 10:30 AM
K2_LIMECO2_10_YEST | Kiln2 | KILN 2 LIME CO2 10:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:761 | KILN 2 LIME CO2 10:30 AM
K2_LIMECO2_11 | Kiln2 | KILN 2 LIME CO2 11:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:62 | KILN 2 LIME CO2 11:00 AM
K2_LIMECO2_11_YEST | Kiln2 | KILN 2 LIME CO2 11:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:762 | KILN 2 LIME CO2 11:00 AM
K2_LIMECO2_12 | Kiln2 | KILN 2 LIME CO2 11:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:63 | KILN 2 LIME CO2 11:30 AM
K2_LIMECO2_12_YEST | Kiln2 | KILN 2 LIME CO2 11:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:763 | KILN 2 LIME CO2 11:30 AM
K2_LIMECO2_13 | Kiln2 | KILN 2 LIME CO2 12:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:64 | KILN 2 LIME CO2 12:00 PM
K2_LIMECO2_13_YEST | Kiln2 | KILN 2 LIME CO2 12:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:764 | KILN 2 LIME CO2 12:00 PM
K2_LIMECO2_14 | Kiln2 | KILN 2 LIME CO2 12:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:65 | KILN 2 LIME CO2 12:30 PM
K2_LIMECO2_14_YEST | Kiln2 | KILN 2 LIME CO2 12:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:765 | KILN 2 LIME CO2 12:30 PM
K2_LIMECO2_15 | Kiln2 | KILN 2 LIME CO2 1:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:66 | KILN 2 LIME CO2 1:00 PM
K2_LIMECO2_15_YEST | Kiln2 | KILN 2 LIME CO2 1:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:766 | KILN 2 LIME CO2 1:00 PM
K2_LIMECO2_16 | Kiln2 | KILN 2 LIME CO2 1:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:67 | KILN 2 LIME CO2 1:30 PM
K2_LIMECO2_16_YEST | Kiln2 | KILN 2 LIME CO2 1:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:767 | KILN 2 LIME CO2 1:30 PM
K2_LIMECO2_17 | Kiln2 | KILN 2 LIME CO2 2:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:68 | KILN 2 LIME CO2 2:00 PM
K2_LIMECO2_17_YEST | Kiln2 | KILN 2 LIME CO2 2:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:768 | KILN 2 LIME CO2 2:00 PM
K2_LIMECO2_18 | Kiln2 | KILN 2 LIME CO2 2:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:69 | KILN 2 LIME CO2 2:30 PM
K2_LIMECO2_18_YEST | Kiln2 | KILN 2 LIME CO2 2:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:769 | KILN 2 LIME CO2 2:30 PM
K2_LIMECO2_19 | Kiln2 | KILN 2 LIME CO2 3:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:70 | KILN 2 LIME CO2 3:00 PM
K2_LIMECO2_19_YEST | Kiln2 | KILN 2 LIME CO2 3:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:770 | KILN 2 LIME CO2 3:00 PM
K2_LIMECO2_2 | Kiln2 | KILN 2 LIME CO2 6:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:53 | KILN 2 LIME CO2 6:30 AM
K2_LIMECO2_2_YEST | Kiln2 | KILN 2 LIME CO2 6:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:753 | KILN 2 LIME CO2 6:30 AM
K2_LIMECO2_20 | Kiln2 | KILN 2 LIME CO2 3:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:71 | KILN 2 LIME CO2 3:30 PM
K2_LIMECO2_20_YEST | Kiln2 | KILN 2 LIME CO2 3:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F69:771 | KILN 2 LIME CO2 3:30 PM
K2_LIMECO2_21 | Kiln2 | KILN 2 LIME CO2 4:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:72 | KILN 2 LIME CO2 4:00 PM
K2_LIMECO2_21_YEST | Kiln2 | KILN 2 LIME CO2 4:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:772 | KILN 2 LIME CO2 4:00 PM
K2_LIMECO2_22 | Kiln2 | KILN 2 LIME CO2 4:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:73 | KILN 2 LIME CO2 4:30 PM
K2_LIMECO2_22_YEST | Kiln2 | KILN 2 LIME CO2 4:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:773 | KILN 2 LIME CO2 4:30 PM
K2_LIMECO2_23 | Kiln2 | KILN 2 LIME CO2 5:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:74 | KILN 2 LIME CO2 5:00 PM
K2_LIMECO2_23_YEST | Kiln2 | KILN 2 LIME CO2 5:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:774 | KILN 2 LIME CO2 5:00 PM
K2_LIMECO2_24 | Kiln2 | KILN 2 LIME CO2 5:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:75 | KILN 2 LIME CO2 5:30 PM
K2_LIMECO2_24_YEST | Kiln2 | KILN 2 LIME CO2 5:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:775 | KILN 2 LIME CO2 5:30 PM
K2_LIMECO2_25 | Kiln2 | KILN 2 LIME CO2 6:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:76 | KILN 2 LIME CO2 6:00 PM
K2_LIMECO2_25_YEST | Kiln2 | KILN 2 LIME CO2 6:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:776 | KILN 2 LIME CO2 6:00 PM
K2_LIMECO2_26 | Kiln2 | KILN 2 LIME CO2 6:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:77 | KILN 2 LIME CO2 6:30 PM
K2_LIMECO2_26_YEST | Kiln2 | KILN 2 LIME CO2 6:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:777 | KILN 2 LIME CO2 6:30 PM
K2_LIMECO2_27 | Kiln2 | KILN 2 LIME CO2 7:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:78 | KILN 2 LIME CO2 7:00 PM
K2_LIMECO2_27_YEST | Kiln2 | KILN 2 LIME CO2 7:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:778 | KILN 2 LIME CO2 7:00 PM
K2_LIMECO2_28 | Kiln2 | KILN 2 LIME CO2 7:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:79 | KILN 2 LIME CO2 7:30 PM
K2_LIMECO2_28_YEST | Kiln2 | KILN 2 LIME CO2 7:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:779 | KILN 2 LIME CO2 7:30 PM
K2_LIMECO2_29 | Kiln2 | KILN 2 LIME CO2 8:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:80 | KILN 2 LIME CO2 8:00 PM
K2_LIMECO2_29_YEST | Kiln2 | KILN 2 LIME CO2 8:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:780 | KILN 2 LIME CO2 8:00 PM
K2_LIMECO2_3 | Kiln2 | KILN 2 LIME CO2 7:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:54 | KILN 2 LIME CO2 7:00 AM
K2_LIMECO2_3_YEST | Kiln2 | KILN 2 LIME CO2 7:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:754 | KILN 2 LIME CO2 7:00 AM
K2_LIMECO2_30 | Kiln2 | KILN 2 LIME CO2 8:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:81 | KILN 2 LIME CO2 8:30 PM
K2_LIMECO2_30_YEST | Kiln2 | KILN 2 LIME CO2 8:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:781 | KILN 2 LIME CO2 8:30 PM
K2_LIMECO2_31 | Kiln2 | KILN 2 LIME CO2 9:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:82 | KILN 2 LIME CO2 9:00 PM
K2_LIMECO2_31_YEST | Kiln2 | KILN 2 LIME CO2 9:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:782 | KILN 2 LIME CO2 9:00 PM
K2_LIMECO2_32 | Kiln2 | KILN 2 LIME CO2 9:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:83 | KILN 2 LIME CO2 9:30 PM
K2_LIMECO2_32_YEST | Kiln2 | KILN 2 LIME CO2 9:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:783 | KILN 2 LIME CO2 9:30 PM
K2_LIMECO2_33 | Kiln2 | KILN 2 LIME CO2 10:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:84 | KILN 2 LIME CO2 10:00 PM
K2_LIMECO2_33_YEST | Kiln2 | KILN 2 LIME CO2 10:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:784 | KILN 2 LIME CO2 10:00 PM
K2_LIMECO2_34 | Kiln2 | KILN 2 LIME CO2 10:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:85 | KILN 2 LIME CO2 10:30 PM
K2_LIMECO2_34_YEST | Kiln2 | KILN 2 LIME CO2 10:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:785 | KILN 2 LIME CO2 10:30 PM
K2_LIMECO2_35 | Kiln2 | KILN 2 LIME CO2 11:00 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:86 | KILN 2 LIME CO2 11:00 PM
K2_LIMECO2_35_YEST | Kiln2 | KILN 2 LIME CO2 11:00 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:786 | KILN 2 LIME CO2 11:00 PM
K2_LIMECO2_36 | Kiln2 | KILN 2 LIME CO2 11:30 PM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:87 | KILN 2 LIME CO2 11:30 PM
K2_LIMECO2_36_YEST | Kiln2 | KILN 2 LIME CO2 11:30 PM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:787 | KILN 2 LIME CO2 11:30 PM
K2_LIMECO2_37 | Kiln2 | KILN 2 LIME CO2 12:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:88 | KILN 2 LIME CO2 12:00 AM
K2_LIMECO2_37_YEST | Kiln2 | KILN 2 LIME CO2 12:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:788 | KILN 2 LIME CO2 12:00 AM
K2_LIMECO2_38 | Kiln2 | KILN 2 LIME CO2 12:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:89 | KILN 2 LIME CO2 12:30 AM
K2_LIMECO2_38_YEST | Kiln2 | KILN 2 LIME CO2 12:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:789 | KILN 2 LIME CO2 12:30 AM
K2_LIMECO2_39 | Kiln2 | KILN 2 LIME CO2 1:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:90 | KILN 2 LIME CO2 1:00 AM
K2_LIMECO2_39_YEST | Kiln2 | KILN 2 LIME CO2 1:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:790 | KILN 2 LIME CO2 1:00 AM
K2_LIMECO2_4 | Kiln2 | KILN 2 LIME CO2 7:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:55 | KILN 2 LIME CO2 7:30 AM
K2_LIMECO2_4_YEST | Kiln2 | KILN 2 LIME CO2 7:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:755 | KILN 2 LIME CO2 7:30 AM
K2_LIMECO2_40 | Kiln2 | KILN 2 LIME CO2 1:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:91 | KILN 2 LIME CO2 1:30 AM
K2_LIMECO2_40_YEST | Kiln2 | KILN 2 LIME CO2 1:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:791 | KILN 2 LIME CO2 1:30 AM
K2_LIMECO2_41 | Kiln2 | KILN 2 LIME CO2 2:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:92 | KILN 2 LIME CO2 2:00 AM
K2_LIMECO2_41_YEST | Kiln2 | KILN 2 LIME CO2 2:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:792 | KILN 2 LIME CO2 2:00 AM
K2_LIMECO2_42 | Kiln2 | KILN 2 LIME CO2 2:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:93 | KILN 2 LIME CO2 2:30 AM
K2_LIMECO2_42_YEST | Kiln2 | KILN 2 LIME CO2 2:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:793 | KILN 2 LIME CO2 2:30 AM
K2_LIMECO2_43 | Kiln2 | KILN 2 LIME CO2 3:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:94 | KILN 2 LIME CO2 3:00 AM
K2_LIMECO2_43_YEST | Kiln2 | KILN 2 LIME CO2 3:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:794 | KILN 2 LIME CO2 3:00 AM
K2_LIMECO2_44 | Kiln2 | KILN 2 LIME CO2 3:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:95 | KILN 2 LIME CO2 3:30 AM
K2_LIMECO2_44_YEST | Kiln2 | KILN 2 LIME CO2 3:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:795 | KILN 2 LIME CO2 3:30 AM
K2_LIMECO2_45 | Kiln2 | KILN 2 LIME CO2 4:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:96 | KILN 2 LIME CO2 4:00 AM
K2_LIMECO2_45_YEST | Kiln2 | KILN 2 LIME CO2 4:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:796 | KILN 2 LIME CO2 4:00 AM
K2_LIMECO2_46 | Kiln2 | KILN 2 LIME CO2 4:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:97 | KILN 2 LIME CO2 4:30 AM
K2_LIMECO2_46_YEST | Kiln2 | KILN 2 LIME CO2 4:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:797 | KILN 2 LIME CO2 4:30 AM
K2_LIMECO2_47 | Kiln2 | KILN 2 LIME CO2 5:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:98 | KILN 2 LIME CO2 5:00 AM
K2_LIMECO2_47_YEST | Kiln2 | KILN 2 LIME CO2 5:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:798 | KILN 2 LIME CO2 5:00 AM
K2_LIMECO2_48 | Kiln2 | KILN 2 LIME CO2 5:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:99 | KILN 2 LIME CO2 5:30 AM
K2_LIMECO2_48_YEST | Kiln2 | KILN 2 LIME CO2 5:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:799 | KILN 2 LIME CO2 5:30 AM
K2_LIMECO2_5 | Kiln2 | KILN 2 LIME CO2 8:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:56 | KILN 2 LIME CO2 8:00 AM
K2_LIMECO2_5_YEST | Kiln2 | KILN 2 LIME CO2 8:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:756 | KILN 2 LIME CO2 8:00 AM
K2_LIMECO2_6 | Kiln2 | KILN 2 LIME CO2 8:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:57 | KILN 2 LIME CO2 8:30 AM
K2_LIMECO2_6_YEST | Kiln2 | KILN 2 LIME CO2 8:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:757 | KILN 2 LIME CO2 8:30 AM
K2_LIMECO2_7 | Kiln2 | KILN 2 LIME CO2 9:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:58 | KILN 2 LIME CO2 9:00 AM
K2_LIMECO2_7_YEST | Kiln2 | KILN 2 LIME CO2 9:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:758 | KILN 2 LIME CO2 9:00 AM
K2_LIMECO2_8 | Kiln2 | KILN 2 LIME CO2 9:30 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:59 | KILN 2 LIME CO2 9:30 AM
K2_LIMECO2_8_YEST | Kiln2 | KILN 2 LIME CO2 9:30 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:759 | KILN 2 LIME CO2 9:30 AM
K2_LIMECO2_9 | Kiln2 | KILN 2 LIME CO2 10:00 AM | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTWRITE | F69:60 | KILN 2 LIME CO2 10:00 AM
K2_LIMECO2_9_YEST | Kiln2 | KILN 2 LIME CO2 10:00 AM YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:760 | KILN 2 LIME CO2 10:00 AM
K2_LIMECO2_DAVG | Kiln2 | KILN 2 LIME CO2 DAY SHIFT AVERAGE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:426 | KILN 2 LIME CO2 DAY SHIFT AVERAGE
K2_LIMECO2_GAVG | Kiln2 | KILN 2 LIME CO2 GRAVE SHIFT AVERAGE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:427 | KILN 2 LIME CO2 GRAVE SHIFT AVERAGE
K2_LIMECO2_LIMIT | Kiln2 | KILN 2 LIME CO2 0.5 HR SAMPLE LIMIT | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F69:51 | KILN 2 LIME CO2 0.5 HR SAMPLE LIMIT
K2_LIMECO2_TAVG | Kiln2 | KILN 2 LIME CO2 AVERAGE | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:428 | KILN 2 LIME CO2 AVERAGE
K2_LIMECO2_YEST | Kiln2 | KILN 2 LIME CO2 RUNNING VALUE YESTERDAY | % CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:750 | KILN 2 LIME CO2 RUNNING VALUE
K2_LIMERES | Kiln2 | KILN 2 LIME RESIDUE - RUNNING VALUE | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:551 | KILN 2 LIME RESIDUE - RUNNING VALUE
K2_LIMERES_1 | Kiln2 | KILN 2 LIME RESIDUE - 6AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:552 | KILN 2 LIME RESIDUE - 6AM
K2_LIMERES_1_YEST | Kiln2 | KILN 2 LIME RESIDUE - 6AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:652 | KILN 2 LIME RESIDUE - 6AM
K2_LIMERES_10 | Kiln2 | KILN 2 LIME RESIDUE - 10.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:561 | KILN 2 LIME RESIDUE - 10.5AM
K2_LIMERES_10_YEST | Kiln2 | KILN 2 LIME RESIDUE - 10.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:661 | KILN 2 LIME RESIDUE - 10.5AM
K2_LIMERES_11 | Kiln2 | KILN 2 LIME RESIDUE - 11AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:562 | KILN 2 LIME RESIDUE - 11AM
K2_LIMERES_11_YEST | Kiln2 | KILN 2 LIME RESIDUE - 11AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:662 | KILN 2 LIME RESIDUE - 11AM
K2_LIMERES_12 | Kiln2 | KILN 2 LIME RESIDUE - 11.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:563 | KILN 2 LIME RESIDUE - 11.5AM
K2_LIMERES_12_YEST | Kiln2 | KILN 2 LIME RESIDUE - 11.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:663 | KILN 2 LIME RESIDUE - 11.5AM
K2_LIMERES_13 | Kiln2 | KILN 2 LIME RESIDUE - 12PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:564 | KILN 2 LIME RESIDUE - 12PM
K2_LIMERES_13_YEST | Kiln2 | KILN 2 LIME RESIDUE - 12PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:664 | KILN 2 LIME RESIDUE - 12PM
K2_LIMERES_14 | Kiln2 | KILN 2 LIME RESIDUE - 12.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:565 | KILN 2 LIME RESIDUE - 12.5PM
K2_LIMERES_14_YEST | Kiln2 | KILN 2 LIME RESIDUE - 12.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:665 | KILN 2 LIME RESIDUE - 12.5PM
K2_LIMERES_15 | Kiln2 | KILN 2 LIME RESIDUE - 1PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:566 | KILN 2 LIME RESIDUE - 1PM
K2_LIMERES_15_YEST | Kiln2 | KILN 2 LIME RESIDUE - 1PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:666 | KILN 2 LIME RESIDUE - 1PM
K2_LIMERES_16 | Kiln2 | KILN 2 LIME RESIDUE - 1.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:567 | KILN 2 LIME RESIDUE - 1.5PM
K2_LIMERES_16_YEST | Kiln2 | KILN 2 LIME RESIDUE - 1.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:667 | KILN 2 LIME RESIDUE - 1.5PM
K2_LIMERES_17 | Kiln2 | KILN 2 LIME RESIDUE - 2PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:568 | KILN 2 LIME RESIDUE - 2PM
K2_LIMERES_17_YEST | Kiln2 | KILN 2 LIME RESIDUE - 2PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:668 | KILN 2 LIME RESIDUE - 2PM
K2_LIMERES_18 | Kiln2 | KILN 2 LIME RESIDUE - 2.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:569 | KILN 2 LIME RESIDUE - 2.5PM
K2_LIMERES_18_YEST | Kiln2 | KILN 2 LIME RESIDUE - 2.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:669 | KILN 2 LIME RESIDUE - 2.5PM
K2_LIMERES_19 | Kiln2 | KILN 2 LIME RESIDUE - 3PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:570 | KILN 2 LIME RESIDUE - 3PM
K2_LIMERES_19_YEST | Kiln2 | KILN 2 LIME RESIDUE - 3PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:670 | KILN 2 LIME RESIDUE - 3PM
K2_LIMERES_2 | Kiln2 | KILN 2 LIME RESIDUE - 6.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:553 | KILN 2 LIME RESIDUE - 6.5AM
K2_LIMERES_2_YEST | Kiln2 | KILN 2 LIME RESIDUE - 6.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:653 | KILN 2 LIME RESIDUE - 6.5AM
K2_LIMERES_20 | Kiln2 | KILN 2 LIME RESIDUE - 3.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:571 | KILN 2 LIME RESIDUE - 3.5PM
K2_LIMERES_20_YEST | Kiln2 | KILN 2 LIME RESIDUE - 3.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:671 | KILN 2 LIME RESIDUE - 3.5PM
K2_LIMERES_21 | Kiln2 | KILN 2 LIME RESIDUE - 4PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:572 | KILN 2 LIME RESIDUE - 4PM
K2_LIMERES_21_YEST | Kiln2 | KILN 2 LIME RESIDUE - 4PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:672 | KILN 2 LIME RESIDUE - 4PM
K2_LIMERES_22 | Kiln2 | KILN 2 LIME RESIDUE - 4.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:573 | KILN 2 LIME RESIDUE - 4.5PM
K2_LIMERES_22_YEST | Kiln2 | KILN 2 LIME RESIDUE - 4.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:673 | KILN 2 LIME RESIDUE - 4.5PM
K2_LIMERES_23 | Kiln2 | KILN 2 LIME RESIDUE - 5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:574 | KILN 2 LIME RESIDUE - 5PM
K2_LIMERES_23_YEST | Kiln2 | KILN 2 LIME RESIDUE - 5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:674 | KILN 2 LIME RESIDUE - 5PM
K2_LIMERES_24 | Kiln2 | KILN 2 LIME RESIDUE - 5.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:575 | KILN 2 LIME RESIDUE - 5.5PM
K2_LIMERES_24_YEST | Kiln2 | KILN 2 LIME RESIDUE - 5.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:675 | KILN 2 LIME RESIDUE - 5.5PM
K2_LIMERES_25 | Kiln2 | KILN 2 LIME RESIDUE - 6PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:576 | KILN 2 LIME RESIDUE - 6PM
K2_LIMERES_25_YEST | Kiln2 | KILN 2 LIME RESIDUE - 6PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:676 | KILN 2 LIME RESIDUE - 6PM
K2_LIMERES_26 | Kiln2 | KILN 2 LIME RESIDUE - 6.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:577 | KILN 2 LIME RESIDUE - 6.5PM
K2_LIMERES_26_YEST | Kiln2 | KILN 2 LIME RESIDUE - 6.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:677 | KILN 2 LIME RESIDUE - 6.5PM
K2_LIMERES_27 | Kiln2 | KILN 2 LIME RESIDUE - 7PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:578 | KILN 2 LIME RESIDUE - 7PM
K2_LIMERES_27_YEST | Kiln2 | KILN 2 LIME RESIDUE - 7PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:678 | KILN 2 LIME RESIDUE - 7PM
K2_LIMERES_28 | Kiln2 | KILN 2 LIME RESIDUE - 7.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:579 | KILN 2 LIME RESIDUE - 7.5PM
K2_LIMERES_28_YEST | Kiln2 | KILN 2 LIME RESIDUE - 7.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:679 | KILN 2 LIME RESIDUE - 7.5PM
K2_LIMERES_29 | Kiln2 | KILN 2 LIME RESIDUE - 8PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:580 | KILN 2 LIME RESIDUE - 8PM
K2_LIMERES_29_YEST | Kiln2 | KILN 2 LIME RESIDUE - 8PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:680 | KILN 2 LIME RESIDUE - 8PM
K2_LIMERES_3 | Kiln2 | KILN 2 LIME RESIDUE - 7AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:554 | KILN 2 LIME RESIDUE - 7AM
K2_LIMERES_3_YEST | Kiln2 | KILN 2 LIME RESIDUE - 7AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:654 | KILN 2 LIME RESIDUE - 7AM
K2_LIMERES_30 | Kiln2 | KILN 2 LIME RESIDUE - 8.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:581 | KILN 2 LIME RESIDUE - 8.5PM
K2_LIMERES_30_YEST | Kiln2 | KILN 2 LIME RESIDUE - 8.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:681 | KILN 2 LIME RESIDUE - 8.5PM
K2_LIMERES_31 | Kiln2 | KILN 2 LIME RESIDUE - 9PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:582 | KILN 2 LIME RESIDUE - 9PM
K2_LIMERES_31_YEST | Kiln2 | KILN 2 LIME RESIDUE - 9PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:682 | KILN 2 LIME RESIDUE - 9PM
K2_LIMERES_32 | Kiln2 | KILN 2 LIME RESIDUE - 9.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:583 | KILN 2 LIME RESIDUE - 9.5PM
K2_LIMERES_32_YEST | Kiln2 | KILN 2 LIME RESIDUE - 9.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:683 | KILN 2 LIME RESIDUE - 9.5PM
K2_LIMERES_33 | Kiln2 | KILN 2 LIME RESIDUE - 10PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:584 | KILN 2 LIME RESIDUE - 10PM
K2_LIMERES_33_YEST | Kiln2 | KILN 2 LIME RESIDUE - 10PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:684 | KILN 2 LIME RESIDUE - 10PM
K2_LIMERES_34 | Kiln2 | KILN 2 LIME RESIDUE - 10.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:585 | KILN 2 LIME RESIDUE - 10.5PM
K2_LIMERES_34_YEST | Kiln2 | KILN 2 LIME RESIDUE - 10.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:685 | KILN 2 LIME RESIDUE - 10.5PM
K2_LIMERES_35 | Kiln2 | KILN 2 LIME RESIDUE - 11PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:586 | KILN 2 LIME RESIDUE - 11PM
K2_LIMERES_35_YEST | Kiln2 | KILN 2 LIME RESIDUE - 11PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:686 | KILN 2 LIME RESIDUE - 11PM
K2_LIMERES_36 | Kiln2 | KILN 2 LIME RESIDUE - 11.5PM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:587 | KILN 2 LIME RESIDUE - 11.5PM
K2_LIMERES_36_YEST | Kiln2 | KILN 2 LIME RESIDUE - 11.5PM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:687 | KILN 2 LIME RESIDUE - 11.5PM
K2_LIMERES_37 | Kiln2 | KILN 2 LIME RESIDUE - 12AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:588 | KILN 2 LIME RESIDUE - 12AM
K2_LIMERES_37_YEST | Kiln2 | KILN 2 LIME RESIDUE - 12AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:688 | KILN 2 LIME RESIDUE - 12AM
K2_LIMERES_38 | Kiln2 | KILN 2 LIME RESIDUE - 12.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:589 | KILN 2 LIME RESIDUE - 12.5AM
K2_LIMERES_38_YEST | Kiln2 | KILN 2 LIME RESIDUE - 12.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:689 | KILN 2 LIME RESIDUE - 12.5AM
K2_LIMERES_39 | Kiln2 | KILN 2 LIME RESIDUE - 1AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:590 | KILN 2 LIME RESIDUE - 1AM
K2_LIMERES_39_YEST | Kiln2 | KILN 2 LIME RESIDUE - 1AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:690 | KILN 2 LIME RESIDUE - 1AM
K2_LIMERES_4 | Kiln2 | KILN 2 LIME RESIDUE - 7.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:555 | KILN 2 LIME RESIDUE - 7.5AM
K2_LIMERES_4_YEST | Kiln2 | KILN 2 LIME RESIDUE - 7.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:655 | KILN 2 LIME RESIDUE - 7.5AM
K2_LIMERES_40 | Kiln2 | KILN 2 LIME RESIDUE - 1.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:591 | KILN 2 LIME RESIDUE - 1.5AM
K2_LIMERES_40_YEST | Kiln2 | KILN 2 LIME RESIDUE - 1.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:691 | KILN 2 LIME RESIDUE - 1.5AM
K2_LIMERES_41 | Kiln2 | KILN 2 LIME RESIDUE - 2AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:592 | KILN 2 LIME RESIDUE - 2AM
K2_LIMERES_41_YEST | Kiln2 | KILN 2 LIME RESIDUE - 2AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:692 | KILN 2 LIME RESIDUE - 2AM
K2_LIMERES_42 | Kiln2 | KILN 2 LIME RESIDUE - 2.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:593 | KILN 2 LIME RESIDUE - 2.5AM
K2_LIMERES_42_YEST | Kiln2 | KILN 2 LIME RESIDUE - 2.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:693 | KILN 2 LIME RESIDUE - 2.5AM
K2_LIMERES_43 | Kiln2 | KILN 2 LIME RESIDUE - 3AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:594 | KILN 2 LIME RESIDUE - 3AM
K2_LIMERES_43_YEST | Kiln2 | KILN 2 LIME RESIDUE - 3AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:694 | KILN 2 LIME RESIDUE - 3AM
K2_LIMERES_44 | Kiln2 | KILN 2 LIME RESIDUE - 3.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:595 | KILN 2 LIME RESIDUE - 3.5AM
K2_LIMERES_44_YEST | Kiln2 | KILN 2 LIME RESIDUE - 3.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:695 | KILN 2 LIME RESIDUE - 3.5AM
K2_LIMERES_45 | Kiln2 | KILN 2 LIME RESIDUE - 4AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:596 | KILN 2 LIME RESIDUE - 4AM
K2_LIMERES_45_YEST | Kiln2 | KILN 2 LIME RESIDUE - 4AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:696 | KILN 2 LIME RESIDUE - 4AM
K2_LIMERES_46 | Kiln2 | KILN 2 LIME RESIDUE - 4.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:597 | KILN 2 LIME RESIDUE - 4.5AM
K2_LIMERES_46_YEST | Kiln2 | KILN 2 LIME RESIDUE - 4.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:697 | KILN 2 LIME RESIDUE - 4.5AM
K2_LIMERES_47 | Kiln2 | KILN 2 LIME RESIDUE - 5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:598 | KILN 2 LIME RESIDUE - 5AM
K2_LIMERES_47_YEST | Kiln2 | KILN 2 LIME RESIDUE - 5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:698 | KILN 2 LIME RESIDUE - 5AM
K2_LIMERES_48 | Kiln2 | KILN 2 LIME RESIDUE - 5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:599 | KILN 2 LIME RESIDUE - 5AM
K2_LIMERES_48_YEST | Kiln2 | KILN 2 LIME RESIDUE - 5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:699 | KILN 2 LIME RESIDUE - 5AM
K2_LIMERES_5 | Kiln2 | KILN 2 LIME RESIDUE - 8AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:556 | KILN 2 LIME RESIDUE - 8AM
K2_LIMERES_5_YEST | Kiln2 | KILN 2 LIME RESIDUE - 8AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:656 | KILN 2 LIME RESIDUE - 8AM
K2_LIMERES_6 | Kiln2 | KILN 2 LIME RESIDUE - 8.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:557 | KILN 2 LIME RESIDUE - 8.5AM
K2_LIMERES_6_YEST | Kiln2 | KILN 2 LIME RESIDUE - 8.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:657 | KILN 2 LIME RESIDUE - 8.5AM
K2_LIMERES_7 | Kiln2 | KILN 2 LIME RESIDUE - 9AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:558 | KILN 2 LIME RESIDUE - 9AM
K2_LIMERES_7_YEST | Kiln2 | KILN 2 LIME RESIDUE - 9AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:658 | KILN 2 LIME RESIDUE - 9AM
K2_LIMERES_8 | Kiln2 | KILN 2 LIME RESIDUE - 9.5AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:559 | KILN 2 LIME RESIDUE - 9.5AM
K2_LIMERES_8_YEST | Kiln2 | KILN 2 LIME RESIDUE - 9.5AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:659 | KILN 2 LIME RESIDUE - 9.5AM
K2_LIMERES_9 | Kiln2 | KILN 2 LIME RESIDUE - 10AM | g | 25 | 0.01 | 0 | 0 | PLC_FLTWRITE | F9:560 | KILN 2 LIME RESIDUE - 10AM
K2_LIMERES_9_YEST | Kiln2 | KILN 2 LIME RESIDUE - 10AM YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:660 | KILN 2 LIME RESIDUE - 10AM
K2_LIMERES_YEST | Kiln2 | KILN 2 LIME RESIDUE - RUNNING VALUE YESTERDAY | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:652 | KILN 2 LIME RESIDUE - RUNNING VALUE
K2_O2_PID_MAXO | Kiln2 | K2 O2 PID Maximum Output Clamp | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N78:11
K2_O2_PID_MINO | Kiln2 | K2 O2 PID Minimum Clamp | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N78:12
K2_RES_LIMIT | Kiln2 | KILN 2 LIME RESIDUE 0.5 HR SAMPLE LIMIT | g | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:550 | KILN 2 LIME RESIDUE 0.5 HR SAMPLE LIMIT
K2_SPCCO2_ANS | Kiln2 | Answer Kiln 2 Leco CO2 SPC Alarm | None | 0
K2_SPCKE_ANS | Kiln2 | Answer Kiln 2 Kiln Exit Temp SPC Alarm | None | 0
K2_SPCO2_ANS | Kiln2 | Answer Kiln 2 O2 SPC Alarm | None | 0
K2BLAST_AM | Kiln2 | KILN 2 AIR BLASTERS AUTO MANUAL | None | PLC_DISCWRITE | B100/617
K2BLAST_INT | Kiln2 | K2 AIR CANNON SEQUENCE INTERVAL |  | 28800 | 0 | 0 | 1800 | PLC_INTWRITE | T4:754.PRE
K2BLAST_INTCTN | Kiln2 | K2 AIR CANNON SEQUENCE INTERVAL TIME |  | 32000 | 0 | 0 | 0 | PLC_INTREAD | n7:167
K2BLAST_NUM | Kiln2 | K2 AIR CANNON SEQUENCE NEXT CANNON |  | 100 | 0 | 0 | 0 | PLC_INTREAD | n7:166
K2BLAST_SEQCTN | Kiln2 | K2 AIR CANNON SEQUENCE TIME |  | 10000 | 0 | 0 | 0 | PLC_INTREAD | N73:3
K2BLAST1_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 1 PC BYPASS | None | PLC_DISCREAD | B100/765
K2BLAST1_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 1 PC START | None | PLC_DISCWRITE | B100/752
K2BLAST1_X | Kiln2 | KILN 2 AIR BLASTER CANNON 1 FDBK | None | PLC_DISCREAD | O:042/0
K2BLAST10_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 10 PC BYPASS | None | PLC_DISCREAD | B100/774
K2BLAST10_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 10 PC START | None | PLC_DISCWRITE | B100/761
K2BLAST10_X | Kiln2 | KILN 2 AIR BLASTER CANNON 10 FDBK | None | PLC_DISCREAD | O:042/11
K2BLAST11_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 11 PC START | None | PLC_DISCWRITE | B100/762
K2BLAST12_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 12 PC START | None | PLC_DISCWRITE | B100/763
K2BLAST13_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 13 PC START | None | PLC_DISCWRITE | B100/764
K2BLAST14_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 14 PC START | None | PLC_DISCWRITE | B100/779
K2BLAST2_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 2 PC BYPASS | None | PLC_DISCREAD | B100/766
K2BLAST2_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 2 PC START | None | PLC_DISCWRITE | B100/753
K2BLAST2_X | Kiln2 | KILN 2 AIR BLASTER CANNON 2 FDBK | None | PLC_DISCREAD | O:042/1
K2BLAST3_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 3 PC BYPASS | None | PLC_DISCREAD | B100/767
K2BLAST3_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 3 PC START | None | PLC_DISCWRITE | B100/754
K2BLAST3_X | Kiln2 | KILN 2 AIR BLASTER CANNON 3 FDBK | None | PLC_DISCREAD | O:042/2
K2BLAST4_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 4 PC BYPASS | None | PLC_DISCREAD | B100/768
K2BLAST4_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 4 PC START | None | PLC_DISCWRITE | B100/755
K2BLAST4_X | Kiln2 | KILN 2 AIR BLASTER CANNON 4 FDBK | None | PLC_DISCREAD | O:042/3
K2BLAST5_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 5 PC BYPASS | None | PLC_DISCREAD | B100/769
K2BLAST5_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 5 PC START | None | PLC_DISCWRITE | B100/756
K2BLAST5_X | Kiln2 | KILN 2 AIR BLASTER CANNON 5 FDBK | None | PLC_DISCREAD | O:042/4
K2BLAST6_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 6 PC BYPASS | None | PLC_DISCREAD | B100/770
K2BLAST6_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 6 PC START | None | PLC_DISCWRITE | B100/757
K2BLAST6_X | Kiln2 | KILN 2 AIR BLASTER CANNON 6 FDBK | None | PLC_DISCREAD | O:042/5
K2BLAST7_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 7 PC BYPASS | None | PLC_DISCREAD | B100/771
K2BLAST7_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 7 PC START | None | PLC_DISCWRITE | B100/758
K2BLAST7_X | Kiln2 | KILN 2 AIR BLASTER CANNON 7 FDBK | None | PLC_DISCREAD | O:042/6
K2BLAST8_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 8 PC BYPASS | None | PLC_DISCREAD | B100/772
K2BLAST8_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 8 PC START | None | PLC_DISCWRITE | B100/759
K2BLAST8_X | Kiln2 | KILN 2 AIR BLASTER CANNON 8 FDBK | None | PLC_DISCREAD | O:042/7
K2BLAST9_BYP | Kiln2 | KILN 2 AIR BLASTER CANNON 9 PC BYPASS | None | PLC_DISCREAD | B100/773
K2BLAST9_PCS | Kiln2 | KILN 2 AIR BLASTER CANNON 9 PC START | None | PLC_DISCWRITE | B100/760
K2BLAST9_X | Kiln2 | KILN 2 AIR BLASTER CANNON 9 FDBK | None | PLC_DISCREAD | O:042/10
K2CEMPID_CV | Kiln2 | K2 CEM CONTROL VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N78:24
K2CEMPID_DB | Kiln2 | K2 CEM PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N78:9
K2CEMPID_DR | Kiln2 | K2 CEM PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N78:05
K2CEMPID_ER | Kiln2 | K2 CEM PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N78:15
K2CEMPID_PG | Kiln2 | K2 CEM PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N78:3
K2CEMPID_PIDSP | Kiln2 | K2 CEM PID SP 0 - 4095 |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N78:02
K2CEMPID_PV | Kiln2 | K2 CEM PID PROCESS VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N78:23
K2CEMPID_RT | Kiln2 | K2 CEM PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N78:4
K2CEMPID_TB | Kiln2 | K2 CEM PID TIEBACK VARIABLE |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N78:25
K2CEMPID_UT | Kiln2 | K2 CEM PID UPDATE TIME | SEC | 30000 | 1 | 0 | 0 | PLC_INTREAD | T4:87.PRE
K2CO2CTRLSPC_ALM | Kiln2 | KILN 2 LECO CO2 SPC CONTROL VIOLATION | On | PLC_ALARM | B101/532 | KILN 2 LECO CO2 SPC CONTROL VIOLATION
K2CO2SPC_ACT | Kiln2 | KILN 2 ACTUAL LECO CO2 SPC VIOLATION | % LECO CO2 | 10 | 0.001 | 0 | 0 | PLC_FLTREAD | F9:406 | KILN 2 ACTUAL LECO CO2 SPC VIOLATION
K2CO2SPC_ACTION | Kiln2 | KILN 2 LECO CO2 SPC CORRECTIVE ACTION CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:108 | KILN 2 LECO CO2 SPC CORRECTIVE ACTION CODE
K2CO2SPC_REA | Kiln2 | KILN 2 LECO CO2 SPC REASON CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:107 | KILN 2 LECO CO2 SPC REASON CODE
K2CO2SPC_ULCL | Kiln2 | KILN 1 LECO CO2 SPC UCL/LCL VIOLATION | None | PLC_DISCREAD | B3/749 | KILN 1 LECO CO2 SPC UCL/LCL VIOLATION
K2CO2SPCDAY_ALM | Kiln2 | K2 LECO CO2 SPC VIOLATION DAY
K2CO2SPCHR_ALM | Kiln2 | K2 LECO CO2 SPC VIOLATION TIME
K2DUST_PBS | Kiln2 | KILN 2 DUST SYSTEM PC START | None | PLC_DISCWRITE | B100:42/9 | KILN 2 DUST SYSTEM PC START
K2DUST_PBT | Kiln2 | KILN 2 DUST SYSTEM PC STOP | None | PLC_DISCWRITE | B100/682 | KILN 2 DUST SYSTEM PC STOP
K2DUSTBIN_2318_PLUGGED | Kiln2 | KILN 2 DUST BIN PLUGGED CHUTE | On | PLC_ALARM | I:056/14 | KILN 2 DUST PLUGGED CHUTE
K2DUSTBINHI_ALM | Kiln2 | KILN 2 DUST BIN HIGH LEVEL! | On | PLC_ALARM | I:056/06 | KILN 2 DUST BIN HIGH LEVEL!
K2ETEMPCTRLSPC_ALM | Kiln2 | KILN 2 EXIT TEMP SPC CONTROL VIOLATION | On | PLC_ALARM | B101/531 | KILN 2 EXIT TEMP SPC CONTROL VIOLATION
K2ETEMPSPC_ACT | Kiln2 | KILN 2 ACTUAL EXIT TEMP SPC VIOLATION | F | 2516 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:405 | KILN 2 ACTUAL EXIT TEMP SPC VIOLATION
K2ETEMPSPC_ACTION | Kiln2 | KILN 2 EXIT TEMP SPC CORRECTIVE ACTION CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:106 | KILN 2 EXIT TEMP SPC CORRECTIVE ACTION CODE
K2ETEMPSPC_CL | Kiln2 | KILN 2 EXIT TEMP SPC CONTROL LIMIT | F | 2516 | 0.1 | 0 | 0 | PLC_FLTREAD | F8:89
K2ETEMPSPC_REA | Kiln2 | KILN 2 EXIT TEMP SPC REASON CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:105 | KILN 2 EXIT TEMP SPC REASON CODE
K2ETEMPSPC_ULCL | Kiln2 | KILN 2 EXIT TEMP SPC UCL/LCL VIOLATION | None | PLC_DISCREAD | B3/747 | KILN 2 EXIT TEMP SPC UCL/LCL VIOLATION
K2ETEMPSPCDAY_ALM | Kiln2 | K2 EXIT TEMP SPC VIOLATION DAY
K2ETEMPSPCHR_ALM | Kiln2 | K2 EXIT TEMP SPC VIOLATION TIME
K2EXIT_AM | Kiln2 | KILN 2 EXIT TEMP PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100/98 | KILN 2 EXIT TEMP PID AUTO MANUAL 1=AUTO 0=MANUAL
K2EXIT_CV | Kiln2 | K2 EXIT TEMP PID CONTROL VARIABLE = WF2601_SP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N88:24 | K2 EXIT TEMP PID CONTROL VARIABLE = WF2601_SP
K2EXIT_ER | Kiln2 | KILN 2 EXIT TEMP PID PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | pd114:1.err | KILN 2 EXIT TEMP PID PID ERROR
K2EXIT_PCPIDSP | Kiln2 | K2 EXIT TEMP O2 PID SP TO CONTROL WF 2-601 | °F | 2300 | 1 | 0 | 1700 | PLC_INTWRITE | N102:63 | K2 EXIT TEMP O2 PID SP TO CONTROL WF 2-601
K2EXIT_PID_Valid | Kiln2 | KILN 2 Exit Temp Loop Valid for Operation | None | PLC_DISCREAD | B29/1
K2EXIT_PIDSP | Kiln2 | KILN 2 EXIT TEMP PID SP - SP = K2EXIT_PCPIDSP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N88:2 | KILN 2 EXIT TEMP PID SP - SP = K2EXIT_PCPIDSP
K2EXIT_PV | Kiln2 | K2 EXIT TEMP PID PROCESS VARIABLE =O22309_ACT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N88:23 | K2 EXIT TEMP PID PROCESS VARIABLE =O22309_ACT
K2EXIT_TB | Kiln2 | K2 EXIT TEMP PID TIEBACK VARIABLE = WF2601_WT |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N88:25 | K2 EXIT TEMP PID TIEBACK VARIABLE = WF2601_WT
K2EXITAUTO_SP | Kiln2 | KILN 2 EXIT TEMP PID SETPOINT AUTO SET | None | PLC_DISCWRITE | B100/553
K2EXITAUTOSP_NEW | Kiln2 | KILN 2 EXIT TEMP PID NEW SETPOINT RECOMMENDED | None | PLC_DISCWRITE | B100/554
K2EXITAUTOSP_OK | Kiln2 | KILN 2 EXIT TEMP PID NEW SETPOINT OK | None | PLC_DISCWRITE | B100/555
K2EXITHIPID_SP | Kiln2 | KILN 2 EXIT TEMP HI FEED RATE PID SP | TPH | 15 | 1 | 0 | 1 | PLC_INTWRITE | N102:65 | KILN 2 EXIT TEMP HI FEED RATE PID SP
K2EXITLOWPID_SP | Kiln2 | KILN 2 EXIT TEMP LOW FEED RATE PID SP | TPH | 14 | 1 | 0 | 0 | PLC_INTWRITE | N102:64 | KILN 2 EXIT TEMP LOW FEED RATE PID SP
K2EXITPID_%RUN | Kiln2 | KILN 2 EXIT TEMP PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:374 | KILN 2 EXIT TEMP PID % RUNTIME - TODAY
K2EXITPID_%RUN_YEST | Kiln2 | KILN 2 EXIT TEMP PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:376 | KILN 2 EXIT TEMP PID % RUNTIME - PAST
K2EXITPID_1HRRATE | Kiln2 | KILN 2 EXIT TEMP PID FUEL RATE CHANGE 1 HR |  | 10 | 0 | 0 | -10 | PLC_FLTREAD | f8:147
K2EXITPID_5MINRATE | Kiln2 | KILN 2 EXIT TEMP PID FUEL RATE CHANGE 5 MIN |  | 10 | 0 | 0 | -10 | PLC_FLTREAD | f8:146
K2EXITPID_AVAIL | Kiln2 | KILN 2 EXIT TEMP PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:373 | KILN 2 EXIT TEMP PID AVAIL RUN HOURS - TODAY
K2EXITPID_AVAIL_YEST | Kiln2 | KILN 2 EXIT TEMP PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:375 | KILN 2 EXIT TEMP PID AVAIL RUN HOURS - PAST
K2EXITPID_DB | Kiln2 | KILN 2 EXIT TEMP PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N88:9 | KILN 2 EXIT TEMP PID DEADBAND
K2EXITPID_DR | Kiln2 | KILN 2 EXIT TEMP PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N88:5 | KILN 2 EXIT TEMP PID DR
K2EXITPID_PG | Kiln2 | KILN 2 EXIT TEMP PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N88:3 | KILN 2 EXIT TEMP PID PG
K2EXITPID_RT | Kiln2 | KILN 2 EXIT TEMP PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N88:4 | KILN 2 EXIT TEMP PID RT
K2EXITPID_UT | Kiln2 | KILN 2 EXIT TEMP PID UPDATE TIME | .01 SEC | 32000 | 1 | 0 | 0 | PLC_INTREAD | T4:506.PRE | KILN 2 EXIT TEMP PID UPDATE TIME
K2EXITSP_RECOM | Kiln2 | KILN 2 RECOMMENDED EXIT TEMP PID SP | deg F | 2516 | 1 | 0 | 0 | PLC_FLTREAD | F9:457
K2FUELEFF_CUR | Kiln2 | KILN 2 FUEL EFFICIENCY | MMBTU/TON LIME | 50 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:245 | KILN 2 FUEL EFFICIENCY
K2FUELEFF_DAY | Kiln2 | KILN 2 FUEL EFFICIENCY DAILY FINAL | MMBTU/TON LIME | 50 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:249 | KILN 2 FUEL EFFICIENCY DAILY FINAL
K2HOODPPID_AM | Kiln2 | K2 HOOD DRAFT PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100:2/7
K2HOODPPID_CV | Kiln2 | K2 HOOD DRAFT PID CV (FV 2-216 %) |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N77:24
K2HOODPPID_DB | Kiln2 | K2 HOOD DRAFT PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N77:9
K2HOODPPID_DR | Kiln2 | K2 HOOD DRAFT PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N77:5
K2HOODPPID_ER | Kiln2 | K2 HOOD DRAFT PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N77:15
K2HOODPPID_PG | Kiln2 | K2 HOOD DRAFT PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N77:3
K2HOODPPID_PV | Kiln2 | K2 HOOD DRAFT PID PV (HOOD DRAFT) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N77:23
K2HOODPPID_RT | Kiln2 | K2 HOOD DRAFT PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N77:4
K2HOODPPID_SP | Kiln2 | K2 HOOD DRAFT PID SP - SP = PT2216_PIDSP |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N77:2
K2HOODPPID_TB | Kiln2 | K2 HOOD DRAFT PID TB (FV 2-216 %) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N77:25
K2HOODPPID_UT | Kiln2 | K2 HOOD DRAFT PID UPDATE TIME | MSEC | 10000 | 1 | 0 | 0 | PLC_INTREAD | T4:85.PRE
K2O2_PID_SP | Kiln2 | K2 O2 PID SP | % | 2 | 0 | 0 | 0 | PLC_FLTWRITE | F71:31
K2O2CTRLSPC_ALM | Kiln2 | KILN 2 OXYGEN SPC CONTROL VIOLATION | On | PLC_ALARM | B101/268 | KILN 2 OXYGEN SPC CONTROL VIOLATION
K2O2PID_AM | Kiln2 | KILN 2 O2 PID AUTO MANUAL 1=AUTO 0=MANUAL | None | PLC_DISCWRITE | B100:3/2
K2O2PROBEWATERFLOW_ALM | Kiln2 | KILN 2 O2 PROBE WATER FLOW SWITCH FAILED | On | PLC_ALARM | B101/32 | KILN 2 O2 PROBE WATER FLOW SWITCH FAILED
K2O2SPC_ACT | Kiln2 | KILN 2 ACTUAL OXYGEN SPC VIOLATION | % O2 | 25 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:404 | KILN 2 ACTUAL OXYGEN SPC VIOLATION
K2O2SPC_ACTION | Kiln2 | KILN 2 OXYGEN SPC CORRECTIVE ACTION CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:104 | KILN 2 OXYGEN SPC CORRECTIVE ACTION CODE
K2O2SPC_REA | Kiln2 | KILN 2 OXYGEN SPC REASON CODE |  | 50 | 0 | 0 | 0 | PLC_INTWRITE | N102:103 | KILN 2 OXYGEN SPC REASON CODE
K2O2SPC_ULCL | Kiln2 | KILN 2 OXYGEN SPC UCL/LCL VIOLATION | None | PLC_DISCREAD | B3/745 | KILN 2 OXYGEN SPC UCL/LCL VIOLATION
K2O2SPCDAY_ALM | Kiln2 | K2 O2 SPC VIOLATION DAY
K2O2SPCHR_ALM | Kiln2 | K2 O2 SPC VIOLATION TIME
K2PH2OILLO2LVL_ALM | Kiln2 | KILN 2 PREHEATER 2 LOW OIL LEVEL | On | PLC_ALARM | I:47/13 | KILN 2 PREHEATER 2 LOW OIL LEVEL
K2PH2OILLOLOLVL_ALM | Kiln2 | KILN 2 PREHEATER 2 LOW LOW OIL LEVEL | On | PLC_ALARM | I:47/12 | KILN 2 PREHEATER 2 LOW LOW OIL LEVEL
K2PH2OILPRESS_ALM | Kiln2 | KILN 2 PREHEATER 2 RETURN FILTER PRESSURE SWITCH | On | PLC_ALARM | I:47/14 | KILN 2 PREHEATER 2 RETURN FILTER PRESSURE SWITCH
K2PHOILLOLOLVL_ALM | Kiln2 | PH 2-305 LO LO HYDRAULIC OIL | None | PLC_ALARM | I:47/12 | PH 2-305 LO LO HYDRAULIC OIL
K2RUNTIME_DAY | Kiln2 | KILN 2 RUNTIME DAILY FINAL | HOURS | 24 | 0.05 | 0 | 0 | PLC_FLTREAD | F9:258 | KILN 2 RUNTIME DAILY FINAL
K2SPCCHART_PBS | Kiln2 | KILN 2 RESTART SPC CHARTS | On | PLC_DISCWRITE | B100/99 | KILN 2 SPC CHARTS RESTARTED, UPDATE IN 15 MIN!!
K2SPCUPDATE_ALM | Kiln2 | KILN 2 SPC CHART UPDATE IS OFF | On | PLC_ALARM | B101/148 | KILN 2 SPC CHART UPDATE TURNED OFF BY PLC!!
K2STACKFLOW | Kiln2 | KILN 2 STACK KURZ AIR FLOW | SCFM | 140000 | 0 | 0 | 0 | PLC_FLTREAD | F9:9 | KILN 2 STACK KURZ AIR FLOW
K2STACKTEMP | Kiln2 | KILN 2 STACK KURZ TEMPERATURE | F | 500 | 0 | 0 | 0 | PLC_FLTREAD | F9:8 | KILN 2 STACK KURZ TEMPERATURE
K2T30_0000 | Kiln2 | KILN 2 REACTIVITY T30 AT 0000 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:0
K2T30_0000_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0000 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:0
K2T30_0030 | Kiln2 | KILN 2 REACTIVITY T30 AT 0030 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:1
K2T30_0030_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0030 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:1
K2T30_0100 | Kiln2 | KILN 2 REACTIVITY T30 AT 0100 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:2
K2T30_0100_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0100 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:2
K2T30_0130 | Kiln2 | KILN 2 REACTIVITY T30 AT 0130 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:3
K2T30_0130_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0130 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:3
K2T30_0200 | Kiln2 | KILN 2 REACTIVITY T30 AT 0200 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:4
K2T30_0200_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0200 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:4
K2T30_0230 | Kiln2 | KILN 2 REACTIVITY T30 AT 0230 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:5
K2T30_0230_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0230 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:5
K2T30_0300 | Kiln2 | KILN 2 REACTIVITY T30 AT 0300 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:6
K2T30_0300_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0300 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:6
K2T30_0330 | Kiln2 | KILN 2 REACTIVITY T30 AT 0330 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:7
K2T30_0330_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0330 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:7
K2T30_0400 | Kiln2 | KILN 2 REACTIVITY T30 AT 0400 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:8
K2T30_0400_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0400 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:8
K2T30_0430 | Kiln2 | KILN 2 REACTIVITY T30 AT 0430 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:9
K2T30_0430_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0430 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:9
K2T30_0500 | Kiln2 | KILN 2 REACTIVITY T30 AT 0500 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:10
K2T30_0500_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0500 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:10
K2T30_0530 | Kiln2 | KILN 2 REACTIVITY T30 AT 0530 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:11
K2T30_0530_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0530 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:11
K2T30_0600 | Kiln2 | KILN 2 REACTIVITY T30 AT 0600 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:12
K2T30_0600_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0600 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:12
K2T30_0630 | Kiln2 | KILN 2 REACTIVITY T30 AT 0630 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:13
K2T30_0630_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0630 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:13
K2T30_0700 | Kiln2 | KILN 2 REACTIVITY T30 AT 0700 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:14
K2T30_0700_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0700 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:14
K2T30_0730 | Kiln2 | KILN 2 REACTIVITY T30 AT 0730 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:15
K2T30_0730_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0730 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:15
K2T30_0800 | Kiln2 | KILN 2 REACTIVITY T30 AT 0800 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:16
K2T30_0800_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0800 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:16
K2T30_0830 | Kiln2 | KILN 2 REACTIVITY T30 AT 0830 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:17
K2T30_0830_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0830 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:17
K2T30_0900 | Kiln2 | KILN 2 REACTIVITY T30 AT 0900 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:18
K2T30_0900_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0900 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:18
K2T30_0930 | Kiln2 | KILN 2 REACTIVITY T30 AT 0930 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:19
K2T30_0930_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 0930 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:19
K2T30_1000 | Kiln2 | KILN 2 REACTIVITY T30 AT 1000 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:20
K2T30_1000_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1000 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:20
K2T30_1030 | Kiln2 | KILN 2 REACTIVITY T30 AT 1030 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:21
K2T30_1030_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1030 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:21
K2T30_1100 | Kiln2 | KILN 2 REACTIVITY T30 AT 1100 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:22
K2T30_1100_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1100 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:22
K2T30_1130 | Kiln2 | KILN 2 REACTIVITY T30 AT 1130 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:23
K2T30_1130_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1130 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:23
K2T30_1200 | Kiln2 | KILN 2 REACTIVITY T30 AT 1200 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:24
K2T30_1200_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1200 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:24
K2T30_1230 | Kiln2 | KILN 2 REACTIVITY T30 AT 1230 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:25
K2T30_1230_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1230 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:25
K2T30_1300 | Kiln2 | KILN 2 REACTIVITY T30 AT 1300 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:26
K2T30_1300_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1300 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:26
K2T30_1330 | Kiln2 | KILN 2 REACTIVITY T30 AT 1330 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:27
K2T30_1330_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1330 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:27
K2T30_1400 | Kiln2 | KILN 2 REACTIVITY T30 AT 1400 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:28
K2T30_1400_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1400 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:28
K2T30_1430 | Kiln2 | KILN 2 REACTIVITY T30 AT 1430 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:29
K2T30_1430_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1430 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:29
K2T30_1500 | Kiln2 | KILN 2 REACTIVITY T30 AT 1500 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:30
K2T30_1500_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1500 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:30
K2T30_1530 | Kiln2 | KILN 2 REACTIVITY T30 AT 1530 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:31
K2T30_1530_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1530 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:31
K2T30_1600 | Kiln2 | KILN 2 REACTIVITY T30 AT 1600 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:32
K2T30_1600_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1600 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:32
K2T30_1630 | Kiln2 | KILN 2 REACTIVITY T30 AT 1630 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:33
K2T30_1630_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1630 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:33
K2T30_1700 | Kiln2 | KILN 2 REACTIVITY T30 AT 1700 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:34
K2T30_1700_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1700 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:34
K2T30_1730 | Kiln2 | KILN 2 REACTIVITY T30 AT 1730 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:35
K2T30_1730_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1730 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:35
K2T30_1800 | Kiln2 | KILN 2 REACTIVITY T30 AT 1800 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:36
K2T30_1800_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1800 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:36
K2T30_1830 | Kiln2 | KILN 2 REACTIVITY T30 AT 1830 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:37
K2T30_1830_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1830 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:37
K2T30_1900 | Kiln2 | KILN 2 REACTIVITY T30 AT 1900 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:38
K2T30_1900_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1900 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:38
K2T30_1930 | Kiln2 | KILN 2 REACTIVITY T30 AT 1930 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:39
K2T30_1930_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 1930 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:39
K2T30_2000 | Kiln2 | KILN 2 REACTIVITY T30 AT 2000 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:40
K2T30_2000_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2000 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:40
K2T30_2030 | Kiln2 | KILN 2 REACTIVITY T30 AT 2030 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:41
K2T30_2030_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2030 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:41
K2T30_2100 | Kiln2 | KILN 2 REACTIVITY T30 AT 2100 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:42
K2T30_2100_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2100 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:42
K2T30_2130 | Kiln2 | KILN 2 REACTIVITY T30 AT 2130 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:43
K2T30_2130_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2130 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:43
K2T30_2200 | Kiln2 | KILN 2 REACTIVITY T30 AT 2200 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:44
K2T30_2200_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2200 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:44
K2T30_2230 | Kiln2 | KILN 2 REACTIVITY T30 AT 2230 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:45
K2T30_2230_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2230 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:45
K2T30_2300 | Kiln2 | KILN 2 REACTIVITY T30 AT 2300 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:46
K2T30_2300_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2300 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:46
K2T30_2330 | Kiln2 | KILN 2 REACTIVITY T30 AT 2330 HRS | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:47
K2T30_2330_YEST | Kiln2 | KILN 2 REACTIVITY T30 AT 2330 HRS YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:47
K2T30_DAVG | Kiln2 | KILN 2 REACTIVITY T30 DAY SHIFT AVG | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N21:50
K2T30_DAVG_YEST | Kiln2 | KILN 2 REACTIVITY T30 DAY SHIFT AVG YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:50
K2T30_GAVG | Kiln2 | KILN 2 REACTIVITY T30 GRAVE SHIFT AVG | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N21:52
K2T30_GAVG_YEST | Kiln2 | KILN 2 REACTIVITY T30 GRAVE SHIFT AVG YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:52
K2T30_LAST | Kiln2 | KILN 2 REACTIVITY T30 LAST SAMPLE | DEG F | 90 | 1 | 0 | 0 | PLC_INTWRITE | N21:48
K2T30_LAST_YEST | Kiln2 | KILN 2 REACTIVITY T30 LAST SAMPLE YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:48
K2T30_LOWLIMIT | Kiln2 | KILN 2 REACTIVITY T30 LOW LIMIT | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N21:54
K2T30_TAVG | Kiln2 | KILN 2 REACTIVITY T30 AVERAGE | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N21:53
K2T30_TAVG_YEST | Kiln2 | KILN 2 REACTIVITY T30 AVERAGE YESTERDAY | DEG F | 90 | 1 | 0 | 0 | PLC_INTREAD | N24:53
K2WATERTANK_HIGH | Kiln2 | KILN 2 WATER COOLING TANK HIGH LEVEL | On | PLC_ALARM | I:024/11 | KILN 2 WATER COOLING TANK HIGH LEVEL
K2WATERTANK_LOW | Kiln2 | KILN 2 WATER COOLING TANK LOW LEVEL | On | PLC_ALARM | B101/579 | KILN 2 WATER COOLING TANK LOW LEVEL
K3COHIPID_SP | Kiln2 | KILN 2 EXIT CO HI FEED RATE PID SP | TPH | 15 | 1 | 0 | 1 | PLC_INTWRITE | N95:1 | KILN 2 EXIT TEMP HI FEED RATE PID SP
K3COLOWPID_SP | Kiln2 | KILN 2 EXIT CO LOW FEED RATE PID SP | TPH | 14 | 1 | 0 | 0 | PLC_INTWRITE | N95:0 | KILN 2 EXIT TEMP LOW FEED RATE PID SP
KD2308_OFFSET | Kiln2 | KD 2308-A&B Stroke Offset for Kiln Speed | % | 25 | 1 | 0 | -25 | PLC_INTWRITE | N99:5
KD2308_SSA_HMI | Kiln2 | KD 2-308 KILN 2 KILN Drive Auto Man 0=Auto 1=Auto | None | PLC_DISCWRITE | b3/1368 | KD 2-308 KILN 2 KILN Drive Auto Man 0=Auto 1=Auto
KD2308A_DRVALM | Kiln2 | KD 2-308-A Drive Alarm | Off | PLC_ALARM | I:60/03 | KD 2-308-A Drive Alarm!
KD2308A_DRVFLT_ALM | Kiln2 | KD 2-308-A Drive Fault | On | PLC_ALARM | N103:10/7 | KD 2-308-A Drive Fault!
KD2308A_IM | Kiln2 | KD 2-308-A Interlocks Met | None | USCNEL202 | NEL_KN2_KD2308A.MODE_AUTO
KD2308A_RESHITEMP_ALM | Kiln2 | KD 2-308-A Brake Resistor High Temp Alarm | On | PLC_ALARM | I:60/05 | KD 2-308-A Break Resistor High Temp Alarm!
KD2308A_RPM | Kiln2 | KD 2-308-A Motor RPM | RPM | 2000 | 1 | 0 | 0 | USCNEL202 | NEL_KN2_KD2308A_RPM.IND
KD2308A_TORQUE | Kiln2 | KD 2-308-A Drive % Torque | % | 150 | 0.1 | 0 | 0 | USCNEL202 | NEL_KN2_KD2308A_TQ.IND
KD2308A_TRANSFLT_ALM | Kiln2 | KD 2-308-A Brake Transistor Fault | Off | PLC_ALARM | N103:10/12 | KD 2-308-A Break Transistor Fault!
KD2308A_TRQLMT_ALM | Kiln2 | KD 2-308-A at Torque Limit! | On | USCNEL202 | NEL_KN2_KD2308A_TQ.AH | KD 2-308-A at Torque Limit!
KD2308AB_1DRVSTOP_ALM | Kiln2 | KD 2-308-A&B Only One Drive Running - Shutdown | On | USCNEL202 | NEL_KN2_KD2308_SAFETY_SHUTDOWN_ALARM | KD 2-308-A&B Only One Drive Running - Shutdown!
KD2308AB_KILNSPD | Kiln2 | Kiln #2 Kiln RPM | RPM | 2 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:465
KD2308AB_LUBE_PCENABLE | Kiln2 | KD 2-308-A&B PC Enable Kiln Lube | None | PLC_DISCWRITE | B100/534
KD2308AB_LUBE_STATUS | Kiln2 | KD 2-308-A&B Gear Lube Status | Off | PLC_DISCREAD | O:61/12 | Kiln 2 Gear Lube System Turned Off
KD2308AB_PBS | Kiln2 | KD 2-308-A&B PC Start | None | USCNEL202 | NEL_KN2_KD2308.PBE_HMI
KD2308AB_PBT | Kiln2 | KD 2-308-A&B PC Stop | None | USCNEL202 | NEL_KN2_KD2308.PBS_HMI
KD2308AB_PCSPDREF | Kiln2 | KD 2-308-A&B PC Speed Setpoint | % | 100 | 0.1 | 0 | 0 | USCNEL202 | NEL_KN2_KD2308_ST.SPT
KD2308AB_ROLLTMR | Kiln2 | Kiln #2 Rollback Timer Countdown | sec | 500 | 2 | 0 | 0 | PLC_INTREAD | N102:121
KD2308AB_RPH | Kiln2 | Kiln #2 Kiln RPH | RPH | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:57
KD2308ABMS_TIM | Kiln2 | Kiln #2 Rollback Timer Timing | None | PLC_DISCREAD | t4:733.tt | Kiln #2 Rollback Timer Timing
KD2308AFTS_ALM | Kiln2 | KD 2-308-A Failed to Start | On | USCNEL202 | NEL_KN2_KD2308A.FTS_ALM | KD 2-308-A Failed to Start!
KD2308AMS_X | Kiln2 | KD 2-308-A KILN 2 KILN Drive Running | Off | USCNEL202 | NEL_KN2_KD2308A.AUX | KD 2-308-A Drive Stopped!
KD2308B_DRVALM | Kiln2 | KD 2-308-B Drive Alarm | Off | PLC_ALARM | I:60/13 | KD 2-308-B Drive Alarm!
KD2308B_DRVFLT_ALM | Kiln2 | KD 2-308-B Drive Fault | On | PLC_ALARM | N103:10/9 | KD 2-308-B Drive Fault!
KD2308B_IM | Kiln2 | KD 2-308-B Interlocks Met | None | USCNEL202 | NEL_KN2_KD2308B.MODE_AUTO
KD2308B_RESHITEMP_ALM | Kiln2 | KD 2-308-B Brake Resistor High Temp Alarm | On | PLC_ALARM | I:60/15 | KD 2-308-B Break Resistor High Temp Alarm!
KD2308B_RPM | Kiln2 | KD 2-308-B Motor RPM | RPM | 2000 | 1 | 0 | 0 | USCNEL202 | NEL_KN2_KD2308B_RPM.IND
KD2308B_TORQUE | Kiln2 | KD 2-308-B Drive % Torque | % | 150 | 0.1 | 0 | 0 | USCNEL202 | NEL_KN2_KD2308B_TQ.IND
KD2308B_TRANSFLT_ALM | Kiln2 | KD 2-308-B Brake Transistor Fault | Off | PLC_ALARM | N103:10/12 | KD 2-308-B Break Transistor Fault!
KD2308B_TRQLMT_ALM | Kiln2 | KD 2-308-B at Torque Limit! | On | USCNEL202 | NEL_KN2_KD2308B_TQ.AH | KD 2-308-B at Torque Limit!
KD2308BFTS_ALM | Kiln2 | KD 2-308-B Failed to Start | On | USCNEL202 | NEL_KN2_KD2308B.FTS_ALM | KD 2-308-B Failed to Start!
KD2308BMS_X | Kiln2 | KD 2-308-B Drive Running | Off | USCNEL202 | NEL_KN2_KD2308B.AUX | KD 2-308-B Drive Stopped!
KD2308FS_%RUN | Kiln2 | Kiln 2 Feed to Speed % Runtime - Today | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:365
KD2308FS_%RUN_YEST | Kiln2 | Kiln 2 Feed to Speed Runtime - Yesterday | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:368
KD2308FS_AVAIL | Kiln2 | Kiln 2 Feed to Speed Available Run Hours - Today | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:364
KD2308FS_AVAIL_YEST | Kiln2 | Kiln 2 Feed to Speed Run Hours Avail. - Yesterday | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:366
KD2308FS_TOG | Kiln2 | KD 2-308 Feed to Speed PC Toggle On/Off | None | PLC_DISCWRITE | B100:2/13
KD2308LUBE_ALM | Kiln2 | KD 2-308 Lube Failure | On | PLC_ALARM | I:57/11 | KD 2-308 Lube Failure!
KILN1_BH_TIMEMODE_SP | Kiln2 | KILN1 BH TIME CYCLE PC SETPOINT | HRS | 25 | 1 | 0 | 0 | KILN1_BH_WRITE | KILN1_BH_TIMEMODE.PRE | K1 BH TIME CYCLE PC SETPOINT
KILN2_COALBYWEIGHT | Kiln2 |  | % | 100 | 0 | 0 | 0 | PLC_FLTWRITE | F71:23 | 2
KILN2_COKEBYBTU | Kiln2 | KILN #2 % COKE BY BTU | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:450
KILN2_COKEBYWEIGHT | Kiln2 | KILN 2 % COKE BY WEIGHT | % | 100 | 0.1 | 0 | 0 | PLC_FLTWRITE | F71:20
KILN2_OPAC_RES | Kiln2 | KILN 2 OPACITY RECALIBRATED | On | PLC_DISCWRITE | B67/4 | KILN 2 OPACITY RECALIBRATED
KILN2_SFUELAL2O3 | Kiln2 | KILN #2 SOLID FUEL % Al2O3 | % | 15 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:456
KILN2_SFUELASH | Kiln2 | KILN #2 SOLID FUEL % ASH | % | 50 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:454
KILN2_SFUELBTUTON | Kiln2 | KILN #2 SOLID FUEL MMBTU/TON | MMBTU/ton | 40 | 0.1 | 0 | 5 | PLC_FLTREAD | F9:452
KN1308UE_AM | Kiln2 | KN1308UE IN AUTO/MANUAL 0=AUTO 1=MAN | None | PLC_DISCWRITE | B101/612 | VF 2-311 PID IN AUTO/MANUAL 0=AUTO 1=MAN
KN2308_FTS_RATIO | Kiln2 | KD 2308-A&B FTS Ratio | LST/RPH | 2 | 0 | 0 | 0 | PLC_FLTREAD | F9:484 | KILN 1 PERCENT OXYGEN
KN2308_NOX_IND | Kiln2 | KILN 2 NOx Value | PPM | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:468 | KILN 1 PERCENT OXYGEN
KN2308_NOX_SPT | Kiln2 | KILN 2 NOx SNCR Setpoint | PPM | 1000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:481 | KILN 1 PERCENT OXYGEN
KN2308_UE_IND | Kiln2 | KILN 2 SNCR UREA FLOW RATE | GPM | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:474 | SNCR K2 UE GPM HIGH
KN2308AT_1 | Kiln2 | KILN 2 STACK OPACITY-6 MINUTE AVERAGE |  | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:22 | KILN 2 STACK OPACITY-6 MINUTE AVERAGE
KN2308AT_2 | Kiln2 | KILN 2 STACK OPACITY INSTANTANEOUS |  | 100 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:23 | KILN 2 STACK OPACITY INSTANTANEOUS
KN2308AT_2ROLL | Kiln2 | KILN 2 STACK OPACITY 3-HR ROLLING AVG |  | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:408 | KILN 2 STACK OPACITY 3-HR ROLLING AVG
KN2308AT_5 | Kiln2 | KILN 2 PERCENT OXYGEN | % | 25 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:28 | KILN 2 PERCENT OXYGEN
KN2308AT_5_ALM | Kiln2 | KILN 2 EXTRACTION 02 > 5% FOR 2 MIN | On | PLC_ALARM | B101/147 | KILN 2 EXTRACTION 02 > 5% FOR 2 MIN
KN2308AT_6 | Kiln2 | KILN 2 PERCENT CARBON MONOXIDE | PPM | 50000 | 25 | 0 | 0 | PLC_FLTREAD | F9:29 | KILN 2 PERCENT CARBON MONOXIDE
KN2308AT1_ALM | Kiln2 | KILN 2 STACK OPACITY-6 MINUTE AVERAGE > 15% | On | PLC_ALARM | B101/479 | KILN 2 STACK OPACITY-6 MINUTE AVERAGE > 15%
KN2308AT24ROLL_HOURS | Kiln2 | KILN 2 3-HR ROLLING AVG HIGH FOR XX HOURS | Hours | 8760 | 0 | 0 | 0 | PLC_INTREAD | C5:11.ACC
KN2308AT2ROLL_ALM | Kiln2 | KILN 2 3-HR ROLLING AVERAGE OPACITY > 10% | On | PLC_ALARM | B101/534 | KILN 2 3-HR ROLLING AVERAGE OPACITY > 10%
KN2308AT2ROLL24_ALM | Kiln2 | KILN 2 3-HR ROLLING AVERAGE HIGH FOR OVER 24 HOURS | On | PLC_ALARM | B101/567 | KILN 2 3-HR ROLLING AVERAGE HIGH FOR OVER 24 HOURS!!
KN2308PT | Kiln2 | KILN 2 FEED END DRAFT | "WC | 3 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:89 | KILN 2 FEED END DRAFT
KN2308SHTDWN15_ALM | Kiln2 | TURN KILN 1/4 TURN | On | PLC_ALARM | B101/131 | TURN KILN 1/4 TURN
KN2308SHTDWN30_ALM | Kiln2 | TURN KILN 1/4 TURN | On | PLC_ALARM | B101/132 | TURN KILN 1/4 TURN
KN2308SHTDWNSTOP_ALM | Kiln2 | 4 HRS SINCE BM 2-605 OFF, STOP TURNING KILN | On | PLC_ALARM | B101/130 | 4 HRS SINCE BM 2-605 OFF, STOP TURNING KILN
KN2308TT_1 | Kiln2 | KILN 2 FIRING ZONE | °F | 3000 | 5 | 0 | 0 | PLC_FLTREAD | F9:33 | KILN 2 FIRING ZONE
KN2308TT_1_TREND | Kiln2 | KILN 2 PYROMETER TEMPERATURE | DEG F | 2400 | 5 | 0 | KILN 2 PYROMETER TEMPERATURE | 0 | 0 | 0
KN2308TT_2 | Kiln2 | KILN 2 EXIT GAS TEMPERATURE | °F | 3000 | 1 | 0 | 0 | PLC_INTREAD | N59:07 | KILN 2 EXIT GAS TEMPERATURE
KN2308TT_2_STREND | Kiln2 | KILN #2 EXIT TEMP STARTUP RANGE - TRENDS | DEG F | 1800 | 5 | 0 | KILN #2 EXIT TEMP STARTUP RANGE - TRENDS | 0 | 0 | 0
KN2308TT_2_TREND | Kiln2 | KILN 2 EXIT GAS TEMPERATURE | DEG F | 2400 | 5 | 0 | KILN 2 EXIT GAS TEMPERATURE | 0 | 0 | 0
KN2308TT_DNE | Kiln2 | KILN 2 D.E. N.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:4 | KILN 2 D.E. N.E. TRUNION BRG TEMPERATURE
KN2308TT_DNW | Kiln2 | KILN 2 D.E. N.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:5 | KILN 2 D.E. N.W. TRUNION BRG TEMPERATURE
KN2308TT_DSE | Kiln2 | KILN 2 D.E. S.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:6 | KILN 2 D.E. S.E. TRUNION BRG TEMPERATURE
KN2308TT_DSW | Kiln2 | KILN 2 D.E. S.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:7 | KILN 2 D.E. S.W. TRUNION BRG TEMPERATURE
KN2308TT_FNE | Kiln2 | KILN 2 F.E. N.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:0 | KILN 2 F.E. N.E. TRUNION BRG TEMPERATURE
KN2308TT_FNW | Kiln2 | KILN 2 F.E. N.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:1 | KILN 2 F.E. N.W. TRUNION BRG TEMPERATURE
KN2308TT_FSE | Kiln2 | KILN 2 F.E. S.E. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:2 | KILN 2 F.E. S.E. TRUNION BRG TEMPERATURE
KN2308TT_FSW | Kiln2 | KILN 2 F.E. S.W. TRUNION BRG TEMPERATURE | DEG F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N44:3 | KILN 2 F.E. S.W. TRUNION BRG TEMPERATURE
KN2308TTDNE_HA | Kiln2 | KILN 2 D.E. N.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/116 | KILN 2 D.E. N.E. TRUNION BRG TEMP > 180
KN2308TTDNE_HHA | Kiln2 | KILN 2 D.E. N.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/124 | KILN 2 D.E. N.E. TRUNION BRG TEMP > 220
KN2308TTDNW_HA | Kiln2 | KILN 2 D.E. N.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/117 | KILN 2 D.E. N.W. TRUNION BRG TEMP > 180
KN2308TTDNW_HHA | Kiln2 | KILN 2 D.E. N.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/125 | KILN 2 D.E. N.W. TRUNION BRG TEMP > 220
KN2308TTDSE_HA | Kiln2 | KILN 2 D.E. S.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/118 | KILN 2 D.E. S.E. TRUNION BRG TEMP > 180
KN2308TTDSE_HHA | Kiln2 | KILN 2 D.E. S.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/126 | KILN 2 D.E. S.E. TRUNION BRG TEMP > 220
KN2308TTDSW_HA | Kiln2 | KILN 2 D.E. S.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/119 | KILN 2 D.E. S.W. TRUNION BRG TEMP > 180
KN2308TTDSW_HHA | Kiln2 | KILN 2 D.E. S.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/127 | KILN 2 D.E. S.W. TRUNION BRG TEMP > 220
KN2308TTFNE_HA | Kiln2 | KILN 2 F.E. N.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/112 | KILN 2 F.E. N.E. TRUNION BRG TEMP > 180
KN2308TTFNE_HHA | Kiln2 | KILN 2 F.E. N.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/120 | KILN 2 F.E. N.E. TRUNION BRG TEMP > 220
KN2308TTFNW_HA | Kiln2 | KILN 2 F.E. N.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/113 | KILN 2 F.E. N.W. TRUNION BRG TEMP > 180
KN2308TTFNW_HHA | Kiln2 | KILN 2 F.E. N.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/121 | KILN 2 F.E. N.W. TRUNION BRG TEMP > 220
KN2308TTFSE_HA | Kiln2 | KILN 2 F.E. S.E. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/114 | KILN 2 F.E. S.E. TRUNION BRG TEMP > 180
KN2308TTFSE_HHA | Kiln2 | KILN 2 F.E. S.E. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/122 | KILN 2 F.E. S.E. TRUNION BRG TEMP > 220
KN2308TTFSW_HA | Kiln2 | KILN 2 F.E. S.W. TRUNION BRG TEMP > 180 | On | PLC_ALARM | B3/115 | KILN 2 F.E. S.W. TRUNION BRG TEMP > 180
KN2308TTFSW_HHA | Kiln2 | KILN 2 F.E. S.W. TRUNION BRG TEMP > 220 | On | PLC_ALARM | B3/123 | KILN 2 F.E. S.W. TRUNION BRG TEMP > 220
KN2308UE_AM | Kiln2 | KN2308UE IN AUTO/MANUAL 0=AUTO 1=MAN | None | PLC_DISCWRITE | B100/629 | VF 2-311 PID IN AUTO/MANUAL 0=AUTO 1=MAN
KN2308UE_IM | Kiln2 | KN2308UE Alarm State | None | PLC_DISCREAD | N103:9/0 | KN2308 UE PERMISSIVE
KN2308UE_X | Kiln2 | KN2308UE AUX FDBK | Off | PLC_DISCREAD | N103:9/1 | KN2308 UE STOPPED
NEL_KN2_BC2601B_AUX | Kiln2 | BC2601B KILN 2 COAL BIN #1 AUX FDBK | Off | USCNEL202 | NEL_KN2_BC2601B.AUX | BC2601B STOPPED
NEL_KN2_DG2401_ZT_IND | Kiln2 | Kiln 2 Cooler Diverter Gate % Position FDBK BC401 | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F8:173 | HM 422 AMPS
NEL_KN2_DG2401_ZT_SPT | Kiln2 | Kiln 2 Cooler Diverter Gate % Position to BC401 | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F8:171 | HM 422 AMPS
NEL_KN2_DG2420_ZT_IND | Kiln2 | Kiln 2 Cooler Diverter Gate % Position FDBK PC420 | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F8:172 | HM 422 AMPS
NEL_KN2_DG2420_ZT_SPT | Kiln2 | Kiln 2 Cooler Diverter Gate % Position to PC420 | % | 100 | 0 | 0 | 0 | PLC_FLTREAD | F8:170 | HM 422 AMPS
NEL_KN2_RA2612_AUX | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK AUX FDBK | Off | USCNEL202 | NEL_KN2_RA2612.AUX | RA2612 STOPPED
NEL_KN2_RA2612_FLT | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK FLT | On | USCNEL202 | NEL_KN2_RA2612.FLT | RA2612 FAULTED
NEL_KN2_RA2612_FTS_ALM | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK FTS ALM | On | USCNEL202 | NEL_KN2_RA2612.FTS_ALM | RA2612 FAILED TO START
NEL_KN2_RA2612_IT_IND | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK AMPS | AMPS | 25 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_RA2612_IT.IND
NEL_KN2_RA2612_MLOCK | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK MLOCK | Off | USCNEL202 | NEL_KN2_RA2612.MLOCK | RA2612 MLOCK NOT MET
NEL_KN2_RA2612_OVL_ALM | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK OVL ALM | On | USCNEL202 | NEL_KN2_RA2612.OVL_ALM | RA2612 OVL ALM
NEL_KN2_RA2612_PBE_HMI | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK PBE HMI | None | USCNEL202 | NEL_KN2_RA2612.PBE_HMI | RA2612
NEL_KN2_RA2612_PBS_HMI | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK PBS HMI | None | USCNEL202 | NEL_KN2_RA2612.PBS_HMI | RA2612
NEL_KN2_RA2612_PLOCK | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK PLOCK | Off | USCNEL202 | NEL_KN2_RA2612.PLOCK | RA2612 PLOCK NOT MET
NEL_KN2_RA2612_RDY | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK READY | Off | USCNEL202 | NEL_KN2_RA2612.RDY | RA2612 NOT READY
NEL_KN2_RA2612_SLOCK | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK SLOCK | Off | USCNEL202 | NEL_KN2_RA2612.SLOCK | RA2612 SLOCK NOT MET
NEL_KN2_RA2612_SS_ALM | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK SS ALM | On | USCNEL202 | NEL_KN2_RA2612.SS_ALM | RA2612 MOTION SWITCH ALARM
NEL_KN2_RA2612_SS_BYP | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK SS BYPASS | On | USCNEL202 | NEL_KN2_RA2612.SS_BYP | RA2612 MOTION SWITCH BYPASSED
NEL_KN2_RA2612_SS_BYP_PB | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK SS BYPASS PB | None | USCNEL202 | NEL_KN2_RA2612.SS_BYP_PB | RA2612 MOTION SWITCH BYPASSED
NEL_KN2_RA2612_SSA_HMI | Kiln2 | RA2612 KILN 2 FUEL AIRLOCK SSA HMI | Off | USCNEL202 | NEL_KN2_RA2612.SSA_HMI | RA2612 IN MANUAL
NEL_KN2_SPC_CEM_ALM | Kiln2 | Kiln 2 SPC CO Violation | On | KILN1_BH_ALARM | NEL_KN2_SPC_CEM.ALM | K2 CO SPC VIOLATION. LOG EVENT
NEL_KN2_SPC_QC_ALM | Kiln2 | Kiln 2 SPC Quality Violation | On | KILN1_BH_ALARM | NEL_KN2_SPC_QC.ALM | K2 QUATITY SPC VIOLATION. LOG EVENT
NEL_KN2_SPC_TEMP_ALM | Kiln2 | Kiln 2 SPC Temperature Violation | On | KILN1_BH_ALARM | NEL_KN2_SPC_TEMP.ALM | K2 TEMPERATURE SPC VIOLATION. LOG EVENT
NEL_KN2_WF1601_QT_SPT | Kiln2 | WF1601 KILN1COKE BIN #2 FEED RATE TPH SPT | TPH | 15 | 0 | 0 | 0 | USCNEL101 | NEL_KN2_WF1601_QT.SPT
NEL_KN2_WF2601_AUX | Kiln2 | WF2601 KILN 2 COKE BIN #2 AUX FDBK | Off | USCNEL202 | NEL_KN2_WF2601.AUX | WF2601 STOPPED
NEL_KN2_WF2601_FLT | Kiln2 | WF2601 KILN 2 COKE BIN #2 FAULT | On | USCNEL202 | NEL_KN2_WF2601.FLT | WF2601 FAULTED
NEL_KN2_WF2601_FTS_ALM | Kiln2 | WF2601 KILN 2 COKE BIN #2 FTS ALM | On | USCNEL202 | NEL_KN2_WF2601.FTS_ALM | WF2601 FAILED TO START
NEL_KN2_WF2601_IT_PCT | Kiln2 |  | % Amps | 100 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_IT.PCT
NEL_KN2_WF2601_MLOCK | Kiln2 | WF2601 KILN 2 COKE BIN #2 MLOCK | Off | USCNEL202 | NEL_KN2_WF2601.MLOCK | WF2601 MLOCK NOT MET
NEL_KN2_WF2601_OVL_ALM | Kiln2 | WF2601 KILN 2 COKE BIN #2 OVL ALM | On | USCNEL202 | NEL_KN2_WF2601.OVL_ALM | WF2601 OVL ALM
NEL_KN2_WF2601_PBE_HMI | Kiln2 | WF2601 KILN 2 COKE BIN #2 PBE HMI | None | USCNEL202 | NEL_KN2_WF2601.PBE_HMI | WF2601
NEL_KN2_WF2601_PBS_HMI | Kiln2 | WF2601 KILN 2 COKE BIN #2 PBS HMI | None | USCNEL202 | NEL_KN2_WF2601.PBS_HMI | WF2601
NEL_KN2_WF2601_PLOCK | Kiln2 | WF2601 KILN 2 COKE BIN #2 PLOCK | Off | USCNEL202 | NEL_KN2_WF2601.PLOCK | WF2601 PLOCK NOT MET
NEL_KN2_WF2601_QT_AH | Kiln2 | WF2601 KILN 2 COKE BIN #2 FEED RATE HI ALM | On | USCNEL202 | NEL_KN2_WF2601_QT.AH | WF2601 FEED RATE HI
NEL_KN2_WF2601_QT_AH_SPT | Kiln2 | WF2601 KILN 2 COKE BIN #2 FEED RATE HI ALM SPT | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT.AH_SPT
NEL_KN2_WF2601_QT_AL | Kiln2 | WF2601 KILN 2 COKE BIN #2 FEED RATE LO ALM | On | USCNEL202 | NEL_KN2_WF2601_QT.AL | WF2601 FEED RATE LO
NEL_KN2_WF2601_QT_AL_SPT | Kiln2 | WF2601 KILN 2 COKE BIN #2 FEED RATE LO ALM SPT | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT.AL_SPT
NEL_KN2_WF2601_QT_IND | Kiln2 | WF2601 KILN 2 COKE BIN #2 FEED RATE TPH | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT.IND
NEL_KN2_WF2601_QT_PCT_SPT | Kiln2 | WF 2-601 FEED PERCENT SETPOINT | % | 100 | 0.01 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_QT.PCT_SPT | WF 1-601 FEED RATE SETPOINT
NEL_KN2_WF2601_RDY | Kiln2 | WF2601 KILN 2 COKE BIN #2 READY | Off | USCNEL202 | NEL_KN2_WF2601.RDY | WF2601 NOT READY
NEL_KN2_WF2601_SLOCK | Kiln2 | WF2601 KILN 2 COKE BIN #2 SLOCK | Off | USCNEL202 | NEL_KN2_WF2601.SLOCK | WF2601 SLOCK NOT MET
NEL_KN2_WF2601_SSA_HMI | Kiln2 | WF2601 KILN 2 COKE BIN #2 SSA HMI | Off | USCNEL202 | NEL_KN2_WF2601.SSA_HMI | WF2601 IN MANUAL
NEL_KN2_WF2601_ST_IND | Kiln2 | WF2601 Speed Feedback (percent) | % RPM | 9999 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601_ST.IND
NEL_KN2_WF2601A_AUX | Kiln2 | WF2601A KILN 2 COAL BIN #1 AUX FDBK | Off | USCNEL202 | NEL_KN2_WF2601A.AUX | WF2601A STOPPED
NEL_KN2_WF2601A_FLT | Kiln2 | WF2601A KILN 2 COAL BIN #1 FLT | On | USCNEL202 | NEL_KN2_WF2601A.FLT | WF2601A FAULTED
NEL_KN2_WF2601A_FTS_ALM | Kiln2 | WF2601A KILN 2 COAL BIN #1 FTS ALM | On | USCNEL202 | NEL_KN2_WF2601A.FTS_ALM | WF2601A FAILED TO START
NEL_KN2_WF2601A_IT_IND | Kiln2 | WF2601A KILN 2 COAL BIN #1 AMPS | AMPS | 25 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_IT.IND
NEL_KN2_WF2601A_MLOCK | Kiln2 | WF2601A KILN 2 COAL BIN #1 MLOCK | Off | USCNEL202 | NEL_KN2_WF2601A.MLOCK | WF2601A MLOCK NOT MET
NEL_KN2_WF2601A_OVL_ALM | Kiln2 | WF2601A KILN 2 COAL BIN #1 OVL ALM | On | USCNEL202 | NEL_KN2_WF2601A.OVL_ALM | WF2601A OVL ALM
NEL_KN2_WF2601A_PBE_HMI | Kiln2 | WF2601A KILN 2 COAL BIN #1 PBE HMI | None | USCNEL202 | NEL_KN2_WF2601A.PBE_HMI | WF2601A
NEL_KN2_WF2601A_PBS_HMI | Kiln2 | WF2601A KILN 2 COAL BIN #1 PBS HMI | None | USCNEL202 | NEL_KN2_WF2601A.PBS_HMI | WF2601A
NEL_KN2_WF2601A_PLOCK | Kiln2 | WF2601A KILN 2 COAL BIN #1 PLOCK | Off | USCNEL202 | NEL_KN2_WF2601A.PLOCK | WF2601A PLOCK NOT MET
NEL_KN2_WF2601A_QT_AH | Kiln2 | WF2601A KILN 2 COAL BIN #1 FEED RATE HI ALM | On | USCNEL202 | NEL_KN2_WF2601A_QT.AH | WF2601A FEED RATE HI
NEL_KN2_WF2601A_QT_AH_SPT | Kiln2 | WF2601A KILN 2 COAL BIN #1 FEED RATE HI ALM SPT | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT.AH_SPT
NEL_KN2_WF2601A_QT_AL | Kiln2 | WF2601A KILN 2 COAL BIN #1 FEED RATE LO ALM | On | USCNEL202 | NEL_KN2_WF2601A_QT.AL | WF2601A FEED RATE LO
NEL_KN2_WF2601A_QT_AL_SPT | Kiln2 | WF2601A KILN 2 COAL BIN #1 FEED RATE LO ALM SPT | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT.AL_SPT
NEL_KN2_WF2601A_QT_IND | Kiln2 | WF2601A KILN 2 COAL BIN #1 FEED RATE TPH | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT.IND
NEL_KN2_WF2601A_QT_PCT_SPT | Kiln2 | WF 2-601A FEED PERCENT SETPOINT | % | 100 | 0.01 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT.PCT_SPT | WF 1-601 FEED RATE SETPOINT
NEL_KN2_WF2601A_QT_SPT | Kiln2 | WF2601A KILN 2 COAL BIN #1 FEED RATE TPH SPT | TPH | 10 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT.SPT
NEL_KN2_WF2601A_QT_TOT | Kiln2 | WF2601A KILN 2 COAL BIN #1 TOTALIZER TONS | TPH | 200 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601A_QT.TOT
NEL_KN2_WF2601A_RDY | Kiln2 | WF2601A KILN 2 COAL BIN #1 READY | Off | USCNEL202 | NEL_KN2_WF2601A.RDY | WF2601A NOT READY
NEL_KN2_WF2601A_SLOCK | Kiln2 | WF2601A KILN 2 COAL BIN #1 SLOCK | Off | USCNEL202 | NEL_KN2_WF2601A.SLOCK | WF2601A SLOCK NOT MET
NEL_KN2_WF2601A_SSA_HMI | Kiln2 | WF2601A KILN 2 COAL BIN #1 SSA HMI | Off | USCNEL202 | NEL_KN2_WF2601A.SSA_HMI | WF2601A IN MANUAL
NEL_KN2_WF2601B_AUX | Kiln2 | WF2601B KILN 2 COKE BIN #2 AUX FDBK | Off | USCNEL202 | NEL_KN2_WF2601B.AUX | WF2601 STOPPED
NEL_KN2_WF2601B_FLT | Kiln2 | WF2601B KILN 2 COAL BIN #1 FLT | On | USCNEL202 | NEL_KN2_WF2601B.FLT | WF2601B FAULTED
NEL_KN2_WF2601B_FTS_ALM | Kiln2 | WF2601B KILN 2 COAL BIN #1 FTS ALM | On | USCNEL202 | NEL_KN2_WF2601B.FTS_ALM | WF2601B FAILED TO START
NEL_KN2_WF2601B_IT_IND | Kiln2 | WF2601B KILN 2 COAL BIN #1 SS BYPASS | AMPS | 25 | 0 | 0 | 0 | USCNEL202 | NEL_KN2_WF2601B_IT.IND
NEL_KN2_WF2601B_MLOCK | Kiln2 | WF2601B KILN 2 COAL BIN #1 MLOCK | Off | USCNEL202 | NEL_KN2_WF2601B.MLOCK | WF2601B MLOCK NOT MET
NEL_KN2_WF2601B_OLV_ALM | Kiln2 | WF2601B KILN 2 COAL BIN #1 OLV ALM | On | USCNEL202 | NEL_KN2_WF2601B.OLV_ALM | WF2601B OVL ALM
NEL_KN2_WF2601B_PBE_HMI | Kiln2 | WF2601B KILN 2 COAL BIN #1 PBE HMI | None | USCNEL202 | NEL_KN2_WF2601B.PBE_HMI | WF2601B
NEL_KN2_WF2601B_PBS_HMI | Kiln2 | WF2601B KILN 2 COAL BIN #1 PBS HMI | None | USCNEL202 | NEL_KN2_WF2601B.PBS_HMI | WF2601B
NEL_KN2_WF2601B_PLOCK | Kiln2 | WF2601B KILN 2 COAL BIN #1 PLOCK | Off | USCNEL202 | NEL_KN2_WF2601B.PLOCK | WF2601B PLOCK NOT MET
NEL_KN2_WF2601B_RDY | Kiln2 | WF2601B KILN 2 COAL BIN #1 READY | Off | USCNEL202 | NEL_KN2_WF2601B.RDY | WF2601A NOT READY
NEL_KN2_WF2601B_SLOCK | Kiln2 | WF2601B KILN 2 COAL BIN #1 SLOCK | Off | USCNEL202 | NEL_KN2_WF2601B.SLOCK | WF2601B SLOCK NOT MET
NEL_KN2_WF2601B_SS_ALM | Kiln2 | WF2601B KILN 2 COAL BIN #1 SS ALM | None | USCNEL202 | NEL_KN2_WF2601B.SS_ALM | WF2601B MOTION SWITCH FAILURE
NEL_KN2_WF2601B_SS_BYP | Kiln2 | WF2601B KILN 2 COAL BIN #1 SS BYPASS | On | USCNEL202 | NEL_KN2_WF2601B.SS_BYP | WF2601B SS BYPASSED
NEL_KN2_WF2601B_SS_BYP_PB | Kiln2 | WF2601B KILN 2 COAL BIN #1 SS BYPASS | None | USCNEL202 | NEL_KN2_WF2601B.SS_BYP_PB | WF2601B SS BYPASSED
NEL_KN2_WF2601B_SSA_HMI | Kiln2 | WF2601B KILN 2 COAL BIN #1 SSA HMI | Off | USCNEL202 | NEL_KN2_WF2601B.SSA_HMI | WF2601B IN MANUAL
NEL_PH1_PH1305_ST_PID_SEL_HMI | Kiln2 | Kiln 1 Preheater Strokes APC Selector | None | USCNEL101 | NEL_PH1_PH1305_ST.PID_SEL_HMI | PH 2-305 START STROKE RAMP UP
OV2310%_ACT | Kiln2 | K2 OHMART/VEGA COOLER LEVEL - % FULL | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:175 | K2 OHMART/VEGA COOLER LEVEL - % FULL
OV2310FT_ACT | Kiln2 | K2 OHMART/VEGA COOLER LEVEL - FEET | FT | 10 | 0.1 | 0 | 2 | PLC_FLTREAD | F9:14 | K2 OHMART/VEGA COOLER LEVEL - FEET
PH2305_DSTR | Kiln2 | PH 2-305 STROKE RAMP UP SET POINT | STR/HR | 300 | 1 | 0 | 0 | PLC_INTWRITE | N102:95 | PH 2-305 STROKE RAMP UP SET POINT
PH2305_EN | Kiln2 | PH 2-305 RAMS TURNED OFF | Off | PLC_ALARM | B3/178 | PH 2-305 RAMS TURNED OFF
PH2305_IM | Kiln2 | PH 2-305 INTERLOCKS MET | None | PLC_DISCREAD | B3/179 | PH 2-305 INTERLOCKS MET
PH2305_INTBYP | Kiln2 | PH 2-305 KILN DRIVE BYPASS ON | On | PLC_DISCWRITE | B100/366 | PH 2-305 KILN DRIVE BYPASS ON
PH2305_MAXDBL | Kiln2 | PH 2-305 MAXIMUM RAMS DOUBLE STROKING | None | PLC_DISCWRITE | B3/1107
PH2305_PBS | Kiln2 | PH 2-305 START RAMS | None | PLC_DISCWRITE | B100/90 | PH 2-305 START RAMS
PH2305_PBT | Kiln2 | PH 2-305 STOP | None | PLC_DISCWRITE | B100/91 | PH 2-305 STOP
PH2305_PCDSTR | Kiln2 | PH 2-305 START STROKE RAMP UP | None | PLC_DISCWRITE | B100/517 | PH 2-305 START STROKE RAMP UP
PH2305_PIN | Kiln2 | PH 2-305 ALL RAMS PINNED!! | On | PLC_DISCWRITE | B100/388 | PH 2-305 ALL RAMS PINNED!!
PH2305R1_BYP | Kiln2 | PH 2-305 RAM 1 PC BYPASS ON | On | PLC_DISCWRITE | B100/78 | PH 2-305 RAM 1 PC BYPASS ON
PH2305R1_CLOSED | Kiln2 | KILN 2 PH RAM 1 CLOSED | None | PLC_DISCREAD | I:45/00 | KILN 2 PH RAM 1 CLOSED
PH2305R1_CLOSING | Kiln2 | KILN 2 PH RAM 1 CLOSING | None | PLC_DISCREAD | O:46/02 | KILN 2 PH RAM 1 CLOSING
PH2305R1_DBL | Kiln2 | KILN 2 PH RAM 1 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/268 | KILN 2 PH RAM 1 PC DOUBLE STROKE ON
PH2305R1_OPENING | Kiln2 | KILN 2 PH RAM 1 OPENING | None | PLC_DISCREAD | B3/821 | KILN 2 PH RAM 1 OPENING
PH2305R1_PIN | Kiln2 | PH 2-305 RAM #1 PINNED | On | PLC_DISCWRITE | B100/389 | PH 2-305 RAM #1 PINNED
PH2305R1_SSW | Kiln2 | PH 2-305 RAM 1 FIELD BYPASS ON | Off | PLC_ALARM | I:46/2 | PH 2-305 RAM 1 FIELD BYPASS ON
PH2305R10_BYP | Kiln2 | PH 2-305 RAM 10 PC BYPASS ON | On | PLC_DISCWRITE | B100/259 | PH 2-305 RAM 10 PC BYPASS ON
PH2305R10_CLOSED | Kiln2 | KILN 2 PH RAM 10 CLOSED | None | PLC_DISCREAD | I:45/011 | KILN 2 PH RAM 10 CLOSED
PH2305R10_CLOSING | Kiln2 | KILN 2 PH RAM 10 CLOSING | None | PLC_DISCREAD | O:46/013 | KILN 2 PH RAM 10 CLOSING
PH2305R10_DBL | Kiln2 | KILN 2 PH RAM 10 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/283 | KILN 2 PH RAM 10 PC DOUBLE STROKE ON
PH2305R10_OPENING | Kiln2 | KILN 2 PH RAM 10 OPENING | None | PLC_DISCREAD | B3/830 | KILN 2 PH RAM 10 OPENING
PH2305R10_PIN | Kiln2 | PH 2-305 RAM 10 PINNED | On | PLC_DISCWRITE | B100/422 | PH 2-305 RAM 10 PINNED
PH2305R10_SSW | Kiln2 | PH 2-305 RAM 10 FIELD BYPASS ON | Off | PLC_ALARM | I:46/13 | PH 2-305 RAM 10 FIELD BYPASS ON
PH2305R10CLOSE_ALM | Kiln2 | KILN 2 PH RAM #10 CLOSING ALARM | On | PLC_ALARM | B101:4/14 | KILN 2 PH RAM #10 CLOSING ALARM
PH2305R10OPEN_ALM | Kiln2 | KILN 2 PH RAM #10 OPENING ALARM | On | PLC_ALARM | B101:6/0 | KILN 2 PH RAM #10 OPENING ALARM
PH2305R11_BYP | Kiln2 | PH 2-305 RAM 11 PC BYPASS ON | On | PLC_DISCWRITE | B100/260 | PH 2-305 RAM 11 PC BYPASS ON
PH2305R11_CLOSED | Kiln2 | KILN 2 PH RAM 11 CLOSED | None | PLC_DISCREAD | I:45/12 | KILN 2 PH RAM 11 CLOSED
PH2305R11_CLOSING | Kiln2 | KILN 2 PH RAM 11 CLOSING | None | PLC_DISCREAD | O:46/14 | KILN 2 PH RAM 11 CLOSING
PH2305R11_DBL | Kiln2 | KILN 2 PH RAM 11 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/285 | KILN 2 PH RAM 11 PC DOUBLE STROKE ON
PH2305R11_OPENING | Kiln2 | KILN 2 PH RAM 11 OPENING | None | PLC_DISCREAD | B3/831 | KILN 2 PH RAM 11 OPENING
PH2305R11_PIN | Kiln2 | PH 2-305 RAM 11 PINNED | On | PLC_DISCWRITE | B100/423 | PH 2-305 RAM 11 PINNED
PH2305R11_SSW | Kiln2 | PH 2-305 RAM 11 FIELD BYPASS ON | Off | PLC_ALARM | I:46/14 | PH 2-305 RAM 11 FIELD BYPASS ON
PH2305R11CLOSE_ALM | Kiln2 | KILN 2 PH RAM #11 CLOSING ALARM | On | PLC_ALARM | B101:4/15 | KILN 2 PH RAM #11 CLOSING ALARM
PH2305R11OPEN_ALM | Kiln2 | KILN 2 PH RAM #11 OPENING ALARM | On | PLC_ALARM | B101:6/1 | KILN 2 PH RAM #11 OPENING ALARM
PH2305R12_BYP | Kiln2 | PH 2-305 RAM 12 PC BYPASS ON | On | PLC_DISCWRITE | B100/261 | PH 2-305 RAM 12 PC BYPASS ON
PH2305R12_CLOSED | Kiln2 | KILN 2 PH RAM 12 CLOSED | None | PLC_DISCREAD | I:45/013 | KILN 2 PH RAM 12 CLOSED
PH2305R12_CLOSING | Kiln2 | KILN 2 PH RAM 12 CLOSING | None | PLC_DISCREAD | O:46/015 | KILN 2 PH RAM 12 CLOSING
PH2305R12_DBL | Kiln2 | KILN 2 PH RAM 12 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/275 | KILN 2 PH RAM 12 PC DOUBLE STROKE ON
PH2305R12_OPENING | Kiln2 | KILN 2 PH RAM 12 OPENING | None | PLC_DISCREAD | B3/832 | KILN 2 PH RAM 12 OPENING
PH2305R12_PIN | Kiln2 | PH 2-305 RAM 12 PINNED | On | PLC_DISCWRITE | B100/461 | PH 2-305 RAM 12 PINNED
PH2305R12_SSW | Kiln2 | PH 2-305 RAM 12 FIELD BYPASS ON | Off | PLC_ALARM | I:46/15 | PH 2-305 RAM 12 FIELD BYPASS ON
PH2305R12CLOSE_ALM | Kiln2 | KILN 2 PH RAM #12 CLOSING ALARM | On | PLC_ALARM | B101:5/0 | KILN 2 PH RAM #12 CLOSING ALARM
PH2305R12OPEN_ALM | Kiln2 | KILN 2 PH RAM #12 OPENING ALARM | On | PLC_ALARM | B101:6/2 | KILN 2 PH RAM #12 OPENING ALARM
PH2305R13_BYP | Kiln2 | PH 2-305 RAM 13 PC BYPASS ON | On | PLC_DISCWRITE | B100/262 | PH 2-305 RAM 13 PC BYPASS ON
PH2305R13_CLOSED | Kiln2 | KILN 2 PH RAM 13 CLOSED | None | PLC_DISCREAD | I:45/14 | KILN 2 PH RAM 13 CLOSED
PH2305R13_CLOSING | Kiln2 | KILN 2 PH RAM 13 CLOSING | None | PLC_DISCREAD | O:46/16 | KILN 2 PH RAM 13 CLOSING
PH2305R13_DBL | Kiln2 | KILN 2 PH RAM 13 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/289 | KILN 2 PH RAM 13 PC DOUBLE STROKE ON
PH2305R13_OPENING | Kiln2 | KILN 2 PH RAM 13 OPENING | None | PLC_DISCREAD | B3/833 | KILN 2 PH RAM 13 OPENING
PH2305R13_PIN | Kiln2 | PH 2-305 RAM 13 PINNED | On | PLC_DISCWRITE | B100/463 | PH 2-305 RAM 13 PINNED
PH2305R13_SSW | Kiln2 | PH 2-305 RAM 13 FIELD BYPASS ON | Off | PLC_ALARM | I:46/16 | PH 2-305 RAM 13 FIELD BYPASS ON
PH2305R13CLOSE_ALM | Kiln2 | KILN 2 PH RAM #13 CLOSING ALARM | On | PLC_ALARM | B101:5/1 | KILN 2 PH RAM #13 CLOSING ALARM
PH2305R13OPEN_ALM | Kiln2 | KILN 2 PH RAM #13 OPENING ALARM | On | PLC_ALARM | B101:6/3 | KILN 2 PH RAM #13 OPENING ALARM
PH2305R14_BYP | Kiln2 | PH 2-305 RAM 14 PC BYPASS ON | On | PLC_DISCWRITE | B100/263 | PH 2-305 RAM 14 PC BYPASS ON
PH2305R14_CLOSED | Kiln2 | KILN 2 PH RAM 14 CLOSED | None | PLC_DISCREAD | I:45/015 | KILN 2 PH RAM 14 CLOSED
PH2305R14_CLOSING | Kiln2 | KILN 2 PH RAM 14 CLOSING | None | PLC_DISCREAD | O:46/017 | KILN 2 PH RAM 14 CLOSING
PH2305R14_DBL | Kiln2 | KILN 2 PH RAM 14 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/291 | KILN 2 PH RAM 14 PC DOUBLE STROKE ON
PH2305R14_OPENING | Kiln2 | KILN 2 PH RAM 14 OPENING | None | PLC_DISCREAD | B3/834 | KILN 2 PH RAM 14 OPENING
PH2305R14_PIN | Kiln2 | PH 2-305 RAM 14 PINNED | On | PLC_DISCWRITE | B100/464 | PH 2-305 RAM 14 PINNED
PH2305R14_SSW | Kiln2 | PH 2-305 RAM 14 FIELD BYPASS ON | Off | PLC_ALARM | I:46/17 | PH 2-305 RAM 14 FIELD BYPASS ON
PH2305R14CLOSE_ALM | Kiln2 | KILN 2 PH RAM #14 CLOSING ALARM | On | PLC_ALARM | B101:5/2 | KILN 2 PH RAM #14 CLOSING ALARM
PH2305R14OPEN_ALM | Kiln2 | KILN 2 PH RAM #14 OPENING ALARM | On | PLC_ALARM | B101:6/5 | KILN 2 PH RAM #14 OPENING ALARM
PH2305R15_BYP | Kiln2 | PH 2-305 RAM 15 PC BYPASS ON | On | PLC_DISCWRITE | B100/264 | PH 2-305 RAM 15 PC BYPASS ON
PH2305R15_CLOSED | Kiln2 | KILN 2 PH RAM 15 CLOSED | None | PLC_DISCREAD | I:45/16 | KILN 2 PH RAM 15 CLOSED
PH2305R15_CLOSING | Kiln2 | KILN 2 PH RAM 15 CLOSING | None | PLC_DISCREAD | O:47/00 | KILN 2 PH RAM 15 CLOSING
PH2305R15_DBL | Kiln2 | KILN 2 PH RAM 15 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/293 | KILN 2 PH RAM 15 PC DOUBLE STROKE ON
PH2305R15_OPENING | Kiln2 | KILN 2 PH RAM 15 OPENING | None | PLC_DISCREAD | B3/835 | KILN 2 PH RAM 15 OPENING
PH2305R15_PIN | Kiln2 | PH 2-305 RAM 15 PINNED | On | PLC_DISCWRITE | B100/465 | PH 2-305 RAM 15 PINNED
PH2305R15_SSW | Kiln2 | PH 2-305 RAM 15 FIELD BYPASS ON | Off | PLC_ALARM | I:47/00 | PH 2-305 RAM 15 FIELD BYPASS ON
PH2305R15CLOSE_ALM | Kiln2 | KILN 2 PH RAM #15 CLOSING ALARM | On | PLC_ALARM | B101:5/3 | KILN 2 PH RAM #15 CLOSING ALARM
PH2305R15OPEN_ALM | Kiln2 | KILN 2 PH RAM #15 OPENING ALARM | On | PLC_ALARM | B101:6/6 | KILN 2 PH RAM #15 OPENING ALARM
PH2305R16_BYP | Kiln2 | PH 2-305 RAM 16 PC BYPASS ON | On | PLC_DISCWRITE | B100/265 | PH 2-305 RAM 16 PC BYPASS ON
PH2305R16_CLOSED | Kiln2 | KILN 2 PH RAM 16 CLOSED | None | PLC_DISCREAD | I:45/017 | KILN 2 PH RAM 16 CLOSED
PH2305R16_CLOSING | Kiln2 | KILN 2 PH RAM 16 CLOSING | None | PLC_DISCREAD | O:47/001 | KILN 2 PH RAM 16 CLOSING
PH2305R16_DBL | Kiln2 | KILN 2 PH RAM 16 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/294 | KILN 2 PH RAM 16 PC DOUBLE STROKE ON
PH2305R16_OPENING | Kiln2 | KILN 2 PH RAM 16 OPENING | None | PLC_DISCREAD | B3/836 | KILN 2 PH RAM 16 OPENING
PH2305R16_PIN | Kiln2 | PH 2-305 RAM 16 PINNED | On | PLC_DISCWRITE | B100/466 | PH 2-305 RAM 16 PINNED
PH2305R16_SSW | Kiln2 | PH 2-305 RAM 16 FIELD BYPASS ON | Off | PLC_ALARM | I:47/01 | PH 2-305 RAM 16 FIELD BYPASS ON
PH2305R16CLOSE_ALM | Kiln2 | KILN 2 PH RAM #16 CLOSING ALARM | On | PLC_ALARM | B101:5/4 | KILN 2 PH RAM #16 CLOSING ALARM
PH2305R16OPEN_ALM | Kiln2 | KILN 2 PH RAM #16 OPENING ALARM | On | PLC_ALARM | B101:6/7 | KILN 2 PH RAM #16 OPENING ALARM
PH2305R17_BYP | Kiln2 | PH 2-305 RAM 17 PC BYPASS ON | On | PLC_DISCWRITE | B100/266 | PH 2-305 RAM 17 PC BYPASS ON
PH2305R17_CLOSED | Kiln2 | KILN 2 PH RAM 17 CLOSED | None | PLC_DISCREAD | I:46/00 | KILN 2 PH RAM 17 CLOSED
PH2305R17_CLOSING | Kiln2 | KILN 2 PH RAM 17 CLOSING | None | PLC_DISCREAD | O:47/02 | KILN 2 PH RAM 17 CLOSING
PH2305R17_DBL | Kiln2 | KILN 2 PH RAM 17 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/296 | KILN 2 PH RAM 17 PC DOUBLE STROKE ON
PH2305R17_OPENING | Kiln2 | KILN 2 PH RAM 17 OPENING | None | PLC_DISCREAD | B3/837 | KILN 2 PH RAM 17 OPENING
PH2305R17_PIN | Kiln2 | PH 2-305 RAM 17 PINNED | On | PLC_DISCWRITE | B100/467 | PH 2-305 RAM 17 PINNED
PH2305R17_SSW | Kiln2 | PH 2-305 RAM 17 FIELD BYPASS ON | Off | PLC_ALARM | I:47/02 | PH 2-305 RAM 17 FIELD BYPASS ON
PH2305R17CLOSE_ALM | Kiln2 | KILN 2 PH RAM #17 CLOSING ALARM | On | PLC_ALARM | B101:5/5 | KILN 2 PH RAM #17 CLOSING ALARM
PH2305R17OPEN_ALM | Kiln2 | KILN 2 PH RAM #17 OPENING ALARM | On | PLC_ALARM | B101:6/8 | KILN 2 PH RAM #17 OPENING ALARM
PH2305R18_BYP | Kiln2 | PH 2-305 RAM 18 PC BYPASS ON | On | PLC_DISCWRITE | B100/267 | PH 2-305 RAM 18 PC BYPASS ON
PH2305R18_CLOSED | Kiln2 | KILN 2 PH RAM 18 CLOSED | None | PLC_DISCREAD | I:46/001 | KILN 2 PH RAM 18 CLOSED
PH2305R18_CLOSING | Kiln2 | KILN 2 PH RAM 18 CLOSING | None | PLC_DISCREAD | O:47/003 | KILN 2 PH RAM 18 CLOSING
PH2305R18_DBL | Kiln2 | KILN 2 PH RAM 18 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/298 | KILN 2 PH RAM 18 PC DOUBLE STROKE ON
PH2305R18_OPENING | Kiln2 | KILN 2 PH RAM 18 OPENING | None | PLC_DISCREAD | B3/838 | KILN 2 PH RAM 18 OPENING
PH2305R18_PIN | Kiln2 | PH 2-305 RAM 18 PINNED | On | PLC_DISCWRITE | B100/468 | PH 2-305 RAM 18 PINNED
PH2305R18_SSW | Kiln2 | PH 2-305 RAM 18 FIELD BYPASS ON | Off | PLC_ALARM | I:47/03 | PH 2-305 RAM 18 FIELD BYPASS ON
PH2305R18CLOSE_ALM | Kiln2 | KILN 2 PH RAM #18 CLOSING ALARM | On | PLC_ALARM | B101:5/6 | KILN 2 PH RAM #18 CLOSING ALARM
PH2305R18OPEN_ALM | Kiln2 | KILN 2 PH RAM #18 OPENING ALARM | On | PLC_ALARM | B101:6/9 | KILN 2 PH RAM #18 OPENING ALARM
PH2305R1CLOSE_ALM | Kiln2 | KILN 2 PH RAM #1 CLOSING ALARM | On | PLC_ALARM | B101:4/5 | KILN 2 PH RAM #1 CLOSING ALARM
PH2305R1OPEN_ALM | Kiln2 | KILN 2 PH RAM #1 OPENING ALARM | On | PLC_ALARM | B101:5/7 | KILN 2 PH RAM #1 OPENING ALARM
PH2305R2_BYP | Kiln2 | PH 2-305 RAM 2 PC BYPASS ON | On | PLC_DISCWRITE | B100/246 | PH 2-305 RAM 2 PC BYPASS ON
PH2305R2_CLOSED | Kiln2 | KILN 2 PH RAM 2 CLOSED | None | PLC_DISCREAD | I:45/001 | KILN 2 PH RAM 2 CLOSED
PH2305R2_CLOSING | Kiln2 | KILN 2 PH RAM 2 CLOSING | None | PLC_DISCREAD | O:46/003 | KILN 2 PH RAM 2 CLOSING
PH2305R2_DBL | Kiln2 | KILN 2 PH RAM 2 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/269 | KILN 2 PH RAM 2 PC DOUBLE STROKE ON
PH2305R2_OPENING | Kiln2 | KILN 2 PH RAM 2 OPENING | None | PLC_DISCREAD | B3/822 | KILN 2 PH RAM 2 OPENING
PH2305R2_PIN | Kiln2 | PH 2-305 RAM 2 PINNED | On | PLC_DISCWRITE | B100/400 | PH 2-305 RAM 2 PINNED
PH2305R2_SSW | Kiln2 | PH 2-305 RAM 2 FIELD BYPASS IS ON | Off | PLC_ALARM | I:46/03 | PH 2-305 RAM 2 FIELD BYPASS IS ON
PH2305R2CLOSE_ALM | Kiln2 | KILN 2 PH RAM #2 CLOSING ALARM | On | PLC_ALARM | B101:4/6 | KILN 2 PH RAM #2 CLOSING ALARM
PH2305R2OPEN_ALM | Kiln2 | KILN 2 PH RAM #2 OPENING ALARM | On | PLC_ALARM | B101:5/8 | KILN 2 PH RAM #2 OPENING ALARM
PH2305R3_BYP | Kiln2 | PH 2-305 RAM 3 PC BYPASS ON | On | PLC_DISCWRITE | B100/250 | PH 2-305 RAM 3 PC BYPASS ON
PH2305R3_CLOSED | Kiln2 | KILN 2 PH RAM 3 CLOSED | None | PLC_DISCREAD | I:45/02 | KILN 2 PH RAM 3 CLOSED
PH2305R3_CLOSING | Kiln2 | KILN 2 PH RAM 3 CLOSING | None | PLC_DISCREAD | O:46/04 | KILN 2 PH RAM 3 CLOSING
PH2305R3_DBL | Kiln2 | KILN 2 PH RAM 3 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/270 | KILN 2 PH RAM 3 PC DOUBLE STROKE ON
PH2305R3_OPENING | Kiln2 | KILN 2 PH RAM 3 OPENING | None | PLC_DISCREAD | B3/823 | KILN 2 PH RAM 3 OPENING
PH2305R3_PIN | Kiln2 | PH 2-305 RAM 3 PINNED | On | PLC_DISCWRITE | B100/401 | PH 2-305 RAM 3 PINNED
PH2305R3_SSW | Kiln2 | PH 2-305 RAM 3 FIELD BYPASS ON | Off | PLC_ALARM | I:46/04 | PH 2-305 RAM 3 FIELD BYPASS ON
PH2305R3CLOSE_ALM | Kiln2 | KILN 2 PH RAM #3 CLOSING ALARM | On | PLC_ALARM | B101:4/7 | KILN 2 PH RAM #3 CLOSING ALARM
PH2305R3OPEN_ALM | Kiln2 | KILN 2 PH RAM #3 OPENING ALARM | On | PLC_ALARM | B101:5/9 | KILN 2 PH RAM #3 OPENING ALARM
PH2305R4_BYP | Kiln2 | PH 2-305 RAM 4 PC BYPASS ON | On | PLC_DISCWRITE | B100/251 | PH 2-305 RAM 4 PC BYPASS ON
PH2305R4_CLOSED | Kiln2 | KILN 2 PH RAM 4 CLOSED | None | PLC_DISCREAD | I:45/003 | KILN 2 PH RAM 4 CLOSED
PH2305R4_CLOSING | Kiln2 | KILN 2 PH RAM 4 CLOSING | None | PLC_DISCREAD | O:46/005 | KILN 2 PH RAM 4 CLOSING
PH2305R4_DBL | Kiln2 | KILN 2 PH RAM 4 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/271 | KILN 2 PH RAM 4 PC DOUBLE STROKE ON
PH2305R4_OPENING | Kiln2 | KILN 2 PH RAM 4 OPENING | None | PLC_DISCREAD | B3/824 | KILN 2 PH RAM 4 OPENING
PH2305R4_PIN | Kiln2 | PH 2-305 RAM 4 PINNED | On | PLC_DISCWRITE | B100/402 | PH 2-305 RAM 4 PINNED
PH2305R4_SSW | Kiln2 | PH 2-305 RAM 4 FIELD BYPASS ON | Off | PLC_ALARM | I:46/05 | PH 2-305 RAM 4 FIELD BYPASS ON
PH2305R4CLOSE_ALM | Kiln2 | KILN 2 PH RAM #4 CLOSING ALARM | On | PLC_ALARM | B101:4/8 | KILN 2 PH RAM #4 CLOSING ALARM
PH2305R4OPEN_ALM | Kiln2 | KILN 2 PH RAM #4 OPENING ALARM | On | PLC_ALARM | B101:5/10 | KILN 2 PH RAM #4 OPENING ALARM
PH2305R5_BYP | Kiln2 | PH 2-305 RAM 5 PC BYPASS ON | On | PLC_DISCWRITE | B100/252 | PH 2-305 RAM 5 PC BYPASS ON
PH2305R5_CLOSED | Kiln2 | KILN 2 PH RAM 5 CLOSED | None | PLC_DISCREAD | I:45/04 | KILN 2 PH RAM 5 CLOSED
PH2305R5_CLOSING | Kiln2 | KILN 2 PH RAM 6 CLOSING | None | PLC_DISCREAD | O:46/06 | KILN 2 PH RAM 6 CLOSING
PH2305R5_DBL | Kiln2 | KILN 2 PH RAM 5 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/272 | KILN 2 PH RAM 5 PC DOUBLE STROKE ON
PH2305R5_OPENING | Kiln2 | KILN 2 PH RAM 5 OPENING | None | PLC_DISCREAD | B3/825 | KILN 2 PH RAM 5 OPENING
PH2305R5_PIN | Kiln2 | PH 2-305 RAM 5 PINNED | On | PLC_DISCWRITE | B100/411 | PH 2-305 RAM 5 PINNED
PH2305R5_SSW | Kiln2 | PH 2-305 RAM 5 FIELD BYPASS ON | Off | PLC_ALARM | I:46/06 | PH 2-305 RAM 5 FIELD BYPASS ON
PH2305R5CLOSE_ALM | Kiln2 | KILN 2 PH RAM #5 CLOSING ALARM | On | PLC_ALARM | B101:4/9 | KILN 2 PH RAM #5 CLOSING ALARM
PH2305R5OPEN_ALM | Kiln2 | KILN 2 PH RAM #5 OPENING ALARM | On | PLC_ALARM | B101:5/11 | KILN 2 PH RAM #5 OPENING ALARM
PH2305R6_BYP | Kiln2 | PH 2-305 RAM 6 PC BYPASS ON | On | PLC_DISCWRITE | B100/253 | PH 2-305 RAM 6 PC BYPASS ON
PH2305R6_CLOSED | Kiln2 | KILN 2 PH RAM 6 CLOSED | None | PLC_DISCREAD | I:45/005 | KILN 2 PH RAM 6 CLOSED
PH2305R6_CLOSING | Kiln2 | KILN 2 PH RAM 6 CLOSING | None | PLC_DISCREAD | O:46/007 | KILN 2 PH RAM 6 CLOSING
PH2305R6_DBL | Kiln2 | KILN 2 PH RAM 6 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/273 | KILN 2 PH RAM 6 PC DOUBLE STROKE ON
PH2305R6_OPENING | Kiln2 | KILN 2 PH RAM 6 OPENING | None | PLC_DISCREAD | B3/826 | KILN 2 PH RAM 6 OPENING
PH2305R6_PIN | Kiln2 | PH 2-305 RAM 6 PINNED | On | PLC_DISCWRITE | B100/412 | PH 2-305 RAM 6 PINNED
PH2305R6_SSW | Kiln2 | PH 2-305 RAM 6 FIELD BYPASS ON | Off | PLC_ALARM | I:46/07 | PH 2-305 RAM 6 FIELD BYPASS ON
PH2305R6CLOSE_ALM | Kiln2 | KILN 2 PH RAM #6 CLOSING ALARM | On | PLC_ALARM | B101:4/10 | KILN 2 PH RAM #6 CLOSING ALARM
PH2305R6OPEN_ALM | Kiln2 | KILN 2 PH RAM #6 OPENING ALARM | On | PLC_ALARM | B101:5/12 | KILN 2 PH RAM #6 OPENING ALARM
PH2305R7_BYP | Kiln2 | PH 2-305 RAM 7 PC BYPASS ON | On | PLC_DISCWRITE | B100/254 | PH 2-305 RAM 7 PC BYPASS ON
PH2305R7_CLOSED | Kiln2 | KILN 2 PH RAM 7 CLOSED | None | PLC_DISCREAD | I:45/06 | KILN 2 PH RAM 7 CLOSED
PH2305R7_CLOSING | Kiln2 | KILN 2 PH RAM 7 CLOSING | None | PLC_DISCREAD | O:46/10 | KILN 2 PH RAM 7 CLOSING
PH2305R7_DBL | Kiln2 | KILN 2 PH RAM 7 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/274 | KILN 2 PH RAM 7 PC DOUBLE STROKE ON
PH2305R7_OPENING | Kiln2 | KILN 2 PH RAM 7 OPENING | None | PLC_DISCREAD | B3/827 | KILN 2 PH RAM 7 OPENING
PH2305R7_PIN | Kiln2 | PH 2-305 RAM 7 PINNED | On | PLC_DISCWRITE | B100/413 | PH 2-305 RAM 7 PINNED
PH2305R7_SSW | Kiln2 | PH 2-305 RAM 7 FIELD BYPASS ON | Off | PLC_ALARM | I:46/10 | PH 2-305 RAM 7 FIELD BYPASS ON
PH2305R7CLOSE_ALM | Kiln2 | KILN 2 PH RAM #7 CLOSING ALARM | On | PLC_ALARM | B101:4/11 | KILN 2 PH RAM #7 CLOSING ALARM
PH2305R7OPEN_ALM | Kiln2 | KILN 2 PH RAM #7 OPENING ALARM | On | PLC_ALARM | B101:5/13 | KILN 2 PH RAM #7 OPENING ALARM
PH2305R8_BYP | Kiln2 | PH 2-305 RAM 8 PC BYPASS | On | PLC_DISCWRITE | B100/255 | PH 2-305 RAM 8 PC BYPASS
PH2305R8_CLOSED | Kiln2 | KILN 2 PH RAM 8 CLOSED | None | PLC_DISCREAD | I:45/007 | KILN 2 PH RAM 8 CLOSED
PH2305R8_CLOSING | Kiln2 | KILN 2 PH RAM 8 CLOSING | None | PLC_DISCREAD | O:46/011 | KILN 2 PH RAM 8 CLOSING
PH2305R8_DBL | Kiln2 | KILN 2 PH RAM 8 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/279 | KILN 2 PH RAM 8 PC DOUBLE STROKE ON
PH2305R8_OPENING | Kiln2 | KILN 2 PH RAM 8 OPENING | None | PLC_DISCREAD | B3/828 | KILN 2 PH RAM 8 OPENING
PH2305R8_PIN | Kiln2 | PH 2-305 RAM 8 PINNED | On | PLC_DISCWRITE | B100/414 | PH 2-305 RAM 8 PINNED
PH2305R8_SSW | Kiln2 | PH 2-305 RAM 8 FIELD BYPASS ON | Off | PLC_ALARM | I:46/11 | PH 2-305 RAM 8 FIELD BYPASS ON
PH2305R8CLOSE_ALM | Kiln2 | KILN 2 PH RAM #8 CLOSING ALARM | On | PLC_ALARM | B101:4/12 | KILN 2 PH RAM #8 CLOSING ALARM
PH2305R8OPEN_ALM | Kiln2 | KILN 2 PH RAM #8 OPENING ALARM | On | PLC_ALARM | B101:5/14 | KILN 2 PH RAM #8 OPENING ALARM
PH2305R9_BYP | Kiln2 | PH 2-305 RAM 9 PC BYPASS ON | On | PLC_DISCWRITE | B100/258 | PH 2-305 RAM 9 PC BYPASS ON
PH2305R9_CLOSED | Kiln2 | KILN 2 PH RAM 9 CLOSED | None | PLC_DISCREAD | I:45/10 | KILN 2 PH RAM 9 CLOSED
PH2305R9_CLOSING | Kiln2 | KILN 2 PH RAM 9 CLOSING | None | PLC_DISCREAD | O:46/12 | KILN 2 PH RAM 9 CLOSING
PH2305R9_DBL | Kiln2 | KILN 2 PH RAM 9 PC DOUBLE STROKE ON | On | PLC_DISCWRITE | B100/281 | KILN 2 PH RAM 9 PC DOUBLE STROKE ON
PH2305R9_OPENING | Kiln2 | KILN 2 PH RAM 9 OPENING | None | PLC_DISCREAD | B3/829 | KILN 2 PH RAM 9 OPENING
PH2305R9_PIN | Kiln2 | PH 2-305 RAM 9 PINNED | On | PLC_DISCWRITE | B100/421 | PH 2-305 RAM 9 PINNED
PH2305R9_SSW | Kiln2 | PH 2-305 RAM 9 FIELD BYPASS ON | Off | PLC_ALARM | I:46/12 | PH 2-305 RAM 9 FIELD BYPASS ON
PH2305R9CLOSE_ALM | Kiln2 | KILN 2 PH RAM #9 CLOSING ALARM | On | PLC_ALARM | B101:4/13 | KILN 2 PH RAM #9 CLOSING ALARM
PH2305R9OPEN_ALM | Kiln2 | KILN 2 PH RAM #9 OPENING ALARM | On | PLC_ALARM | B101:5/15 | KILN 2 PH RAM #9 OPENING ALARM
PH2305RAM# | Kiln2 | PH 2305 ACTIVE RAM NUMBER | RAM | 18 | 1 | 0 | 0 | PLC_INTREAD | N7:18 | PH 2305 ACTIVE RAM NUMBER
PH2305STROKE_SP | Kiln2 | PH 2-305 PC SETPOINT STOKE RATE | STR/HR | 300 | 1 | 0 | 0 | PLC_INTWRITE | N102:2 | PH 2-305 PC SETPOINT STOKE RATE
PH2306_APCSTR | Kiln2 | PH 2-305 STROKE APC SET POINT | STR/HR | 300 | 1 | 0 | 0 | PLC_INTWRITE | N102:169 | PH 2-305 STROKE RAMP UP SET POINT
PH2306_TT_AH | Kiln2 | KN2 PREHEATER OUTLET TEMP HIGH | On | PLC_ALARM | B3/1243 | KN2 PREHEATER OUTLET TEMP HIGH
PH2306PT | Kiln2 | PH 2-306 OUTLET DRAFT | "WC | 50 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:88 | PH 2-306 OUTLET DRAFT
PH2306TT_1 | Kiln2 | PH 2-306 INLET TEMP | °F | 2800 | 5 | 0 | 0 | PLC_INTREAD | N59:05 | PH 2-306 INLET TEMP
PH2306TT_1_STREND | Kiln2 | KILN #2 PREHEATER INLET TEMP STARTUP RANGE - TREND | DEG F | 2200 | 5 | 0 | KILN #2 PREHEATER INLET TEMP STARTUP RANGE - TREND | 0 | 0 | 0
PH2306TT_1_TREND | Kiln2 | KILN 2 PREHEATER INLET TEMPERATURE | DEG F | 2400 | 5 | 0 | KILN 2 PREHEATER INLET TEMPERATURE | 0 | 0 | 0
PH2306TT_2 | Kiln2 | PH 2-306 OUTLET TEMP | °F | 1000 | 5 | 0 | 0 | PLC_INTREAD | N59:06 | PH 2-306 OUTLET TEMP
PH2306TT_2_TREND | Kiln2 | KILN 2 PREHEATER OUTLET TEMPERATURE | DEG F | 800 | 5 | 0 | KILN 2 PREHEATER OUTLET TEMPERATURE | 0 | 0 | 0
PH2RA_P1 | Kiln2 | PREHEATER #2 STROKES/HOUR REGISTER | ST/HR | 9999 | 0 | 0 | 0 | PLC_INTREAD | N7:2 | PREHEATER #2 STROKES/HOUR REGISTER
PM2305_PBS | Kiln2 | PM 2-305 -1 & -2 START | None | PLC_DISCWRITE | B100/110 | PM 2-305 -1 & -2 START
PM2305_PBT | Kiln2 | PM 2305-1 & -2 STOP | None | PLC_DISCWRITE | B100/111 | PM 2305-1 & -2 STOP
PM23051_IM | Kiln2 | PM 2-305-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/172 | PM 2-305-1 INTERLOCKS MET
PM23051_SSA_HMI | Kiln2 | PM 2-305-1 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1456
PM23051_SSW | Kiln2 | PM 2-305-1 ENABLED | None | PLC_DISCREAD | I:47/04 | PM 2-305-1 ENABLED
PM23051DEADHEAD_ALM | Kiln2 | PM 2305-1 DEAD HEADED | On | PLC_ALARM | B101/18 | PM 2305-1 DEAD HEADED
PM23051FTS_ALM | Kiln2 | PM 2-305-1 FAILED TO START | On | PLC_ALARM | B101/274 | PM 2-305-1 FAILED TO START
PM23051MS_X | Kiln2 | PM 2-305-1 AUX FDBK | Off | PLC_DISCREAD | I:47/16 | PM 2-305-1 STOPPED
PM23052_IM | Kiln2 | PM 2-305-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/174 | PM 2-305-2 INTERLOCKS MET
PM23052_PT | Kiln2 | PM 2-305-2 PRESSURE | PSIG | 3000 | 5 | 0 | 0 | PLC_FLTREAD | F9:01 | PM 2-305-2 PRESSURE
PM23052_SSA_HMI | Kiln2 | PM 2-305-2 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1461
PM23052_SSW | Kiln2 | PM 2-305-2 ENABLED | None | PLC_DISCREAD | I:47/05 | PM 2-305-2 ENABLED
PM23052DEADHEAD-ALM | Kiln2 | PM 2305-2 DEAD HEADED | On | PLC_ALARM | B101/19 | PM 2305-2 DEAD HEADED
PM23052FTS_ALM | Kiln2 | PM 2-305-2 FAILED TO START | On | PLC_ALARM | B101/275 | PM 2-305-2 FAILED TO START
PM23052MS_X | Kiln2 | PM 2-305-2 AUX FDBK | Off | PLC_DISCREAD | I:47/17 | PM 2-305-2 STOPPED
PM2602_NO_PRESSURE | Kiln2 | PM 2-602-1 and PM 2-602-2 Failed To Pressurize | On | PLC_ALARM | B101/594 | PM 2-602-1&2 FAILED TO PRESSURIZE
PM2602_PRESSURIZED | Kiln2 | PM 2-602-1 and PM 2-602-2 Pressurized | None | PLC_ALARM | I:221/6
PM26021_IM | Kiln2 | PM 2-602-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/393 | PM 2-602-1 INTERLOCKS MET
PM26021_PBS | Kiln2 | PM 2-602-1 PC START | None | PLC_DISCWRITE | B100/26 | PM 2-602-1 PC START
PM26021_PBT | Kiln2 | PM 2-602-1 PC STOP | None | PLC_DISCWRITE | B100/27 | PM 2-602-1 PC STOP
PM26021FTS_ALM | Kiln2 | PM 2-602-1 FAILED TO START | On | PLC_ALARM | B101/337 | PM 2-602-1 FAILED TO START
PM26021MS_X | Kiln2 | PM 2-602-1 AUX FDBK | Off | PLC_DISCREAD | I:16/5 | PM 2-602-1 STOPPED
PM26022_IM | Kiln2 | PM 2-602-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/395 | PM 2-602-2 INTERLOCKS MET
PM26022_PBS | Kiln2 | PM 2-602-2 PC START | None | PLC_DISCWRITE | B100/28 | PM 2-602-2 PC START
PM26022_PBT | Kiln2 | PM 2-602-2 PC STOP | None | PLC_DISCWRITE | B100/29 | PM 2-602-2 PC STOP
PM26022FTS_ALM | Kiln2 | PM 2-602-2 FAILED TO START | On | PLC_ALARM | B101/338 | PM 2-602-2 FAILED TO START
PM26022MS_X | Kiln2 | PM 2-602-2 AUX FDBK | Off | PLC_DISCREAD | I:16/06 | PM 2-602-2 STOPPED
PM4610SEL_K2 | Kiln2 | PM 610 SELECT KILN 2 FOR DIESEL FEED | None | PLC_DISCWRITE | B100/519 | PM 610 SELECT KILN 2 FOR DIESEL FEED
PT2216_ACT | Kiln2 | KILN 2 FIRING HOOD DRAFT (PT 2-216) | "WC | 1 | 0.01 | 0 | -1 | PLC_FLTREAD | F9:78 | KILN 2 FIRING HOOD DRAFT (PT 2-216)
PT2216_PIDSP | Kiln2 | K2 FIRE HOOD DRAFT PID SP TO CONTROL FV 2-216 | "H2O | 0 | 0.01 | 0 | -0.3 | PLC_FLTWRITE | F71:2
RA23131_AUTO | Kiln2 | RA 2-313-1 IN AUTO | None | PLC_DISCREAD | I:205/01 | RA 2-313-1 IN AUTO
RA23131_BYP | Kiln2 | RA 2-313-1 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/428 | RA 2-313-1 MOTION SWITCH BYPASSED
RA23131_IM | Kiln2 | RA 2-313-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/415 | RA 2-313-1 INTERLOCKS MET
RA23131_PBS | Kiln2 | RA 2-313-1 PC START | None | PLC_DISCWRITE | B100/640 | RA 2-313-1 PC START
RA23131_PBT | Kiln2 | RA 2-313-1 PC STOP | None | PLC_DISCWRITE | B100/641 | RA 2-313-1 PC STOP
RA231310_AUTO | Kiln2 | RA 2-313-10 IN AUTO | None | PLC_DISCREAD | I:205/12 | RA 2-313-10 IN AUTO
RA231310_BYP | Kiln2 | RA 2-313-10 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/438 | RA 2-313-10 MOTION SWITCH BYPASSED
RA231310_IM | Kiln2 | RA 2-313-10 INTERLOCKS MET | None | PLC_DISCREAD | B3/433 | RA 2-313-10 INTERLOCKS MET
RA231310_PBS | Kiln2 | RA 2-313-10 PC START | None | PLC_DISCWRITE | B100/658 | RA 2-313-10 PC START
RA231310_PBT | Kiln2 | RA 2-313-10 PC STOP | None | PLC_DISCWRITE | B100/659 | RA 2-313-10 PC STOP
RA231310FTS_ALM | Kiln2 | RA 2-313-10 FAILED TO START | On | PLC_ALARM | B101/308 | RA 2-313-10 FAILED TO START
RA231310MS_X | Kiln2 | RA 2-313-10 AUX CONTACT | Off | PLC_DISCREAD | I:204/16 | RA 2-313-10 STOPPED
RA231310MSF_ALM | Kiln2 | RA 2-313-10 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/309 | RA 2-313-10 MOTION SWITCH FAILURE
RA23131FTS_ALM | Kiln2 | RA 2-313-1 FAILED TO START | On | PLC_ALARM | B101/290 | RA 2-313-1 FAILED TO START
RA23131MS_X | Kiln2 | RA 2-313-1 AUX CONTACT | Off | PLC_DISCREAD | I:200/06 | RA 2-313-1 STOPPED
RA23131MSF_ALM | Kiln2 | RA 2-313-1 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/291 | RA 2-313-1 MOTION SWITCH FAILURE
RA23132_AUTO | Kiln2 | RA 2-313-2 IN AUTO | None | PLC_DISCREAD | I:205/02 | RA 2-313-2 IN AUTO
RA23132_BYP | Kiln2 | RA 2-313-2 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/429 | RA 2-313-2 MOTION SWITCH BYPASSED
RA23132_IM | Kiln2 | RA 2-313-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/417 | RA 2-313-2 INTERLOCKS MET
RA23132_PBS | Kiln2 | RA 2-313-2 PC START | None | PLC_DISCWRITE | B100/642 | RA 2-313-2 PC START
RA23132_PBT | Kiln2 | RA 2-313-2 PC STOP | None | PLC_DISCWRITE | B100/643 | RA 2-313-2 PC STOP
RA23132FTS_ALM | Kiln2 | RA 2-313-2 FAILED TO START | On | PLC_ALARM | B101/292 | RA 2-313-2 FAILED TO START
RA23132MS_X | Kiln2 | RA 2-313-2 AUX CONTACT | Off | PLC_DISCREAD | I:200/16 | RA 2-313-2 STOPPED
RA23132MSF_ALM | Kiln2 | RA 2-313-2 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/293 | RA 2-313-2 MOTION SWITCH FAILURE
RA23133_AUTO | Kiln2 | RA 2-313-3 IN AUTO | None | PLC_DISCREAD | I:205/03 | RA 2-313-3 IN AUTO
RA23133_BYP | Kiln2 | RA 2-313-3 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/430 | RA 2-313-3 MOTION SWITCH BYPASSED
RA23133_IM | Kiln2 | RA 2-313-3 INTERLOCKS MET | None | PLC_DISCREAD | B3/419 | RA 2-313-3 INTERLOCKS MET
RA23133_PBS | Kiln2 | RA 2-313-3 PC START | None | PLC_DISCWRITE | B100/644 | RA 2-313-3 PC START
RA23133_PBT | Kiln2 | RA 2313-3 PC STOP | None | PLC_DISCWRITE | B100/645 | RA 2313-3 PC STOP
RA23133FTS_ALM | Kiln2 | RA 2-313-3 FAILED TO START | On | PLC_ALARM | B101/294 | RA 2-313-3 FAILED TO START
RA23133MS_X | Kiln2 | RA 2-313-3 AUX CONTACT | Off | PLC_DISCREAD | I:201/06 | RA 2-313-3 STOPPED
RA23133MSF_ALM | Kiln2 | RA 2-313-3 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/295 | RA 2-313-3 MOTION SWITCH FAILURE
RA23134_AUTO | Kiln2 | RA 2-313-4 IN AUTO | None | PLC_DISCREAD | I:205/04 | RA 2-313-4 IN AUTO
RA23134_BYP | Kiln2 | RA 2-313-4 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/432 | RA 2-313-4 MOTION SWITCH BYPASSED
RA23134_IM | Kiln2 | RA 2-313-4 INTERLOCKS MET | None | PLC_DISCREAD | B3/421 | RA 2-313-4 INTERLOCKS MET
RA23134_PBS | Kiln2 | RA 2-313-4 PC START | None | PLC_DISCWRITE | B100/646 | RA 2-313-4 PC START
RA23134_PBT | Kiln2 | RA 2-313-4 PC STOP | None | PLC_DISCWRITE | B100/647 | RA 2-313-4 PC STOP
RA23134FTS_ALM | Kiln2 | RA 2-313-4 FAILED TO START | On | PLC_ALARM | B101/296 | RA 2-313-4 FAILED TO START
RA23134MS_X | Kiln2 | RA 2-313-4 AUX CONTACT | Off | PLC_DISCREAD | I:201/16 | RA 2-313-4 STOPPED
RA23134MSF_ALM | Kiln2 | RA 2-313-4 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/297 | RA 2-313-4 MOTION SWITCH FAILURE
RA23135_AUTO | Kiln2 | RA 2-313-5 IN AUTO | None | PLC_DISCREAD | I:205/05 | RA 2-313-5 IN AUTO
RA23135_BYP | Kiln2 | RA 2-313-5 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/433 | RA 2-313-5 MOTION SWITCH BYPASSED
RA23135_IM | Kiln2 | RA 2-313-5 INTERLOCKS MET | None | PLC_DISCREAD | B3/423 | RA 2-313-5 INTERLOCKS MET
RA23135_PBS | Kiln2 | RA 2-313-5 PC START | None | PLC_DISCWRITE | B100/648 | RA 2-313-5 PC START
RA23135_PBT | Kiln2 | RA 2-313-5 PC STOP | None | PLC_DISCWRITE | B100/649 | RA 2-313-5 PC STOP
RA23135FTS_ALM | Kiln2 | RA 2-313-5 FAILED TO START | On | PLC_ALARM | B101/298 | RA 2-313-5 FAILED TO START
RA23135MS_X | Kiln2 | RA 2-313-5 AUX CONTACT | Off | PLC_DISCREAD | I:202/06 | RA 2-313-5 STOPPED
RA23135MSF_ALM | Kiln2 | RA 2-313-5 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/299 | RA 2-313-5 MOTION SWITCH FAILURE
RA23136_AUTO | Kiln2 | RA 2-313-6 IN AUTO | None | PLC_DISCREAD | I:205/06 | RA 2-313-6 IN AUTO
RA23136_BYP | Kiln2 | RA 2-313-6 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/434 | RA 2-313-6 MOTION SWITCH BYPASSED
RA23136_IM | Kiln2 | RA 2-313-6 INTERLOCKS MET | None | PLC_DISCREAD | B3/425 | RA 2-313-6 INTERLOCKS MET
RA23136_PBS | Kiln2 | RA 2-313-6 PC START | None | PLC_DISCWRITE | B100/650 | RA 2-313-6 PC START
RA23136_PBT | Kiln2 | RA 2-313-6 PC STOP | None | PLC_DISCWRITE | B100/651 | RA 2-313-6 PC STOP
RA23136FTS_ALM | Kiln2 | RA 2-313-6 FAILED TO START | On | PLC_ALARM | B101/300 | RA 2-313-6 FAILED TO START
RA23136MS_X | Kiln2 | RA 2-313-6 AUX CONTACT | Off | PLC_DISCREAD | I:202/16 | RA 2-313-6 STOPPED
RA23136MSF_ALM | Kiln2 | RA 2-313-6 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/301 | RA 2-313-6 MOTION SWITCH FAILURE
RA23137_AUTO | Kiln2 | RA 2-313-7 INTERLOCKS MET | None | PLC_DISCREAD | I:205/07 | RA 2-313-7 INTERLOCKS MET
RA23137_BYP | Kiln2 | RA 2-313-7 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/435 | RA 2-313-7 MOTION SWITCH BYPASSED
RA23137_IM | Kiln2 | RA 2-313-7 INTERLOCKS MET | None | PLC_DISCREAD | B3/427 | RA 2-313-7 INTERLOCKS MET
RA23137_PBS | Kiln2 | RA 2-313-7 PC START | None | PLC_DISCWRITE | B100/652 | RA 2-313-7 PC START
RA23137_PBT | Kiln2 | RA 2-313-7 PC STOP | None | PLC_DISCWRITE | B100/653 | RA 2-313-7 PC STOP
RA23137FTS_ALM | Kiln2 | RA 2-313-7 FAILED TO START | On | PLC_ALARM | B101/302 | RA 2-313-7 FAILED TO START
RA23137MS_X | Kiln2 | RA 2-313-7 AUX CONTACT | Off | PLC_DISCREAD | I:203/06 | RA 2-313-7 STOPPED
RA23137MSF_ALM | Kiln2 | RA 2-313-7 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/303 | RA 2-313-7 MOTION SWITCH FAILURE
RA23138_AUTO | Kiln2 | RA 2-313-8 IN AUTO | None | PLC_DISCREAD | I:205/10 | RA 2-313-8 IN AUTO
RA23138_BYP | Kiln2 | RA 2-313-8 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/436 | RA 2-313-8 MOTION SWITCH BYPASSED
RA23138_IM | Kiln2 | RA 2-313-8 INTERLOCKS MET | None | PLC_DISCREAD | B3/429 | RA 2-313-8 INTERLOCKS MET
RA23138_PBS | Kiln2 | RA 2-313-8 PC START | None | PLC_DISCWRITE | B100/654 | RA 2-313-8 PC START
RA23138_PBT | Kiln2 | RA 2-313-8 PC STOP | None | PLC_DISCWRITE | B100/655 | RA 2-313-8 PC STOP
RA23138FTS_ALM | Kiln2 | RA 2-313-8 FAILED TO START | On | PLC_ALARM | B101/304 | RA 2-313-8 FAILED TO START
RA23138MS_X | Kiln2 | RA 2-313-8 AUX CONTACT | Off | PLC_DISCREAD | I:203/16 | RA 2-313-8 STOPPED
RA23138MSF_ALM | Kiln2 | RA 2-313-8 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/305 | RA 2-313-8 MOTION SWITCH FAILURE
RA23139_AUTO | Kiln2 | RA 2-313-9 IN AUTO | None | PLC_DISCREAD | I:205/011 | RA 2-313-9 IN AUTO
RA23139_BYP | Kiln2 | RA 2-313-9 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/437 | RA 2-313-9 MOTION SWITCH BYPASSED
RA23139_IM | Kiln2 | RA 2-313-9 INTERLOCKS MET | None | PLC_DISCREAD | B3/431 | RA 2-313-9 INTERLOCKS MET
RA23139_PBS | Kiln2 | RA 2-313-9 PC START | None | PLC_DISCWRITE | B100/656 | RA 2-313-9 PC START
RA23139_PBT | Kiln2 | RA 2-313-9 PC STOP | None | PLC_DISCWRITE | B100/657 | RA 2-313-9 PC STOP
RA23139FTS_ALM | Kiln2 | RA 2-313-9 FAILED TO START | On | PLC_ALARM | B101/306 | RA 2-313-9 FAILED TO START
RA23139MS_X | Kiln2 | RA 2-313-9 AUX CONTACT | Off | PLC_DISCREAD | I:204/06 | RA 2-313-9 STOPPED
RA23139MSF_ALM | Kiln2 | RA 2-313-9 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/307 | RA 2-313-9 MOTION SWITCH FAILURE
RA2319_IM | Kiln2 | RA 2-319 INTERLOCKS MET | None | PLC_DISCREAD | B3/401 | RA 2-319 INTERLOCKS MET
RA2319_PBS | Kiln2 | RA 2-319 PC START | None | PLC_DISCWRITE | B100/215 | RA 2-319 PC START
RA2319_PBT | Kiln2 | RA 2-319 PC STOP | None | PLC_DISCWRITE | B100/231 | RA 2-319 PC STOP
RA2319FTS_ALM | Kiln2 | RA 2-319 FAILED TO START | On | PLC_ALARM | B101/329 | RA 2-319 FAILED TO START
RA2319MS_X | Kiln2 | RA 2-319 AUX FDBK | Off | PLC_DISCREAD | I:57/2 | RA 2-319 STOPPED
RA2606_IM | Kiln2 | RA 2-606 INTERLOCKS MET | None | PLC_DISCREAD | B3/389 | RA 2-606 INTERLOCKS MET
RA2606_PBS | Kiln2 | RA 2-606 PC START | None | PLC_DISCWRITE | B100/30 | RA 2-606 PC START
RA2606_PBT | Kiln2 | RA 2-606 PC STOP | None | PLC_DISCWRITE | B100/31 | RA 2-606 PC STOP
RA2606_SSA_HMI | Kiln2 | RA 2-606 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1401
RA2606FTS_ALM | Kiln2 | RA 2-606 FAILED TO START | On | PLC_ALARM | B101/340 | RA 2-606 FAILED TO START
RA2606MS_X | Kiln2 | RA 2-606 AUX FDBK | Off | PLC_DISCREAD | I:16/07 | RA 2-606 STOPPED
RA2612_BYP | Kiln2 | RA 2-612 ZERO SPEED BYPASS | On | PLC_DISCWRITE | B100/450 | RA 2-612 ZERO SPEED BYPASS
RA2612_IM | Kiln2 | RA 2-612 INTERLOCKS MET | None | PLC_DISCREAD | B3/397 | RA 2-612 INTERLOCKS MET
RA2612_PBS | Kiln2 | RA 2-612 PC START | None | PLC_DISCWRITE | B100/58 | RA 2-612 PC START
RA2612_PBT | Kiln2 | RA 2-612 PC STOP | None | PLC_DISCWRITE | B100/59 | RA 2-612 PC STOP
RA2612_SSA_HMI | Kiln2 | RA 2-612 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1406
RA2612FTS_ALM | Kiln2 | RA 2-612 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/341 | RA 2-612 MOTION SWITCH FAILURE
RA2612MS_X | Kiln2 | RA 2-612 AUX FDBK | Off | PLC_DISCREAD | I:14/01 | RA 2-612 STOPPED
RA2612MSF_ALM | Kiln2 | RA 2-612 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/342 | RA 2-612 MOTION SWITCH FAILURE
RATE_K2LIME | Kiln2 | KILN 2 LIME PRODUCTION RATE | TPH | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:236 | KILN 2 LIME PRODUCTION RATE
SB2304HILEVEL_TIMER | Kiln2 | SB 2-304 HI LEVEL TIMER | SEC | 32000 | 0 | 0 | 0 | PLC_INTREAD | T4:159.ACC | SB 2-304 HI LEVEL TIMER
SB2304HL_ALM | Kiln2 | KILN 2 STONE BIN HIGH LEVEL! | On | PLC_ALARM | B101:2/4 | KILN 2 STONE BIN HIGH LEVEL!
SB2304HL1HR_ALM | Kiln2 | NO KILN 2 STONE BIN HIGH LEVEL FOR 1 HOUR! | On | PLC_ALARM | B101:2/5 | NO KILN 2 STONE BIN HIGH LEVEL FOR 1 HOUR!
SB2304LL_ALM | Kiln2 | KILN 2 STONE BIN LOW LEVEL ! | On | PLC_ALARM | B101:2/6 | KILN 2 STONE BIN LOW LEVEL !
SC2316_BYP | Kiln2 | SC 2-316 MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/420 | SC 2-316 MOTION SWITCH BYPASSED
SC2316_IM | Kiln2 | SC 2-316 INTERLOCKS MET | None | PLC_DISCREAD | B3/405 | SC 2-316 INTERLOCKS MET
SC2316_PBS | Kiln2 | SC 2-316 PC START | None | PLC_DISCWRITE | B100/210 | SC 2-316 PC START
SC2316_PBT | Kiln2 | SC 2-316 PC STOP | None | PLC_DISCWRITE | B100/226 | SC 2-316 PC STOP
SC2316A_BYP | Kiln2 | SC 2-316-A MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/419 | SC 2-316-A MOTION SWITCH BYPASSED
SC2316A_IM | Kiln2 | SC 2-316-A INTERLOCKS MET | None | PLC_DISCREAD | B3/403 | SC 2-316-A INTERLOCKS MET
SC2316A_PBS | Kiln2 | SC 2-316-A PC START | None | PLC_DISCWRITE | B100/211 | SC 2-316-A PC START
SC2316A_PBT | Kiln2 | SC 2-316-A PC STOP | None | PLC_DISCWRITE | B100/227 | SC 2-316-A PC STOP
SC2316AFTS_ALM | Kiln2 | SC 2-316-A FAILED TO START | On | PLC_ALARM | B101/313 | SC 2-316-A FAILED TO START
SC2316AMS_X | Kiln2 | SC 2-316-A AUX CONTACT | Off | PLC_DISCREAD | I:57/14 | SC 2-316-A STOPPED
SC2316AMSF_ALM | Kiln2 | SC 2-316-A MOTION SWITCH FAILURE | On | PLC_ALARM | B101/314 | SC 2-316-A MOTION SWITCH FAILURE
SC2316B_BYP | Kiln2 | SC 2-316-B MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/425 | SC 2-316-B MOTION SWITCH BYPASSED
SC2316B_IM | Kiln2 | SC 2-316-B INTERLOCKS MET | None | PLC_DISCREAD | B3/407 | SC 2-316-B INTERLOCKS MET
SC2316B_PBS | Kiln2 | SC 2-316-B PC START | None | PLC_DISCWRITE | B100/212 | SC 2-316-B PC START
SC2316B_PBT | Kiln2 | SC 2-316-B PC STOP | None | PLC_DISCWRITE | B100/228 | SC 2-316-B PC STOP
SC2316BFTS_ALM | Kiln2 | SC 2-316-B FAILED TO START | On | PLC_ALARM | B101/315 | SC 2-316-B FAILED TO START
SC2316BMS_X | Kiln2 | SC 2-316-B AUX CONTACT | Off | PLC_DISCREAD | I:57/15 | SC 2-316-B STOPPED
SC2316BMSF_ALM | Kiln2 | SC 2-316-B MOTION SWITCH FAILURE | On | PLC_ALARM | B101/316 | SC 2-316-B MOTION SWITCH FAILURE
SC2316C_BYP | Kiln2 | SC 2-316-C MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/426 | SC 2-316-C MOTION SWITCH BYPASSED
SC2316C_IM | Kiln2 | SC 2-316-C INTERLOCKS MET | None | PLC_DISCREAD | B3/409 | SC 2-316-C INTERLOCKS MET
SC2316C_PBS | Kiln2 | SC 2-316-C PC START | None | PLC_DISCWRITE | B100/213 | SC 2-316-C PC START
SC2316C_PBT | Kiln2 | SC 2-316-C PC STOP | None | PLC_DISCWRITE | B100/229 | SC 2-316-C PC STOP
SC2316CFTS_ALM | Kiln2 | SC 2-316-C FAILED TO START | On | PLC_ALARM | B101/317 | SC 2-316-C FAILED TO START
SC2316CMS_X | Kiln2 | SC 2-316-C AUX CONTACT | Off | PLC_DISCREAD | I:57/16 | SC 2-316-C STOPPED
SC2316CMSF_ALM | Kiln2 | SC 2-316-C MOTION SWITCH FAILURE | On | PLC_ALARM | B101/318 | SC 2-316-C MOTION SWITCH FAILURE
SC2316D_AUTO | Kiln2 | SC 2-316-D | None | PLC_DISCREAD | I:205/16 | SC 2-316-D
SC2316D_BYP | Kiln2 | SC 2-316-D MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/449 | SC 2-316-D MOTION SWITCH BYPASSED
SC2316D_IM | Kiln2 | SC 2-316-D INTERLOCKS MET | None | PLC_DISCREAD | B3/441 | SC 2-316-D INTERLOCKS MET
SC2316D_PBS | Kiln2 | SC 2-316-D PC START | None | PLC_DISCWRITE | B100/666 | SC 2-316-D PC START
SC2316D_PBT | Kiln2 | SC 2-316-D PC STOP | None | PLC_DISCWRITE | B100/667 | SC 2-316-D PC STOP
SC2316DFTS_ALM | Kiln2 | SC 2-316-D FAILED TO START | On | PLC_ALARM | B101/319 | SC 2-316-D FAILED TO START
SC2316DMS_X | Kiln2 | SC 2-316-D AUX CONTACT | Off | PLC_DISCREAD | I:206/07 | SC 2-316-D STOPPED
SC2316DMSF_ALM | Kiln2 | SC 2-316-D MOTION SWITCH FAILURE | On | PLC_ALARM | B101/320 | SC 2-316-D MOTION SWITCH FAILURE
SC2316E_AUTO | Kiln2 | SC 2-316-E IN AUTO | None | PLC_DISCREAD | I:205/15 | SC 2-316-E IN AUTO
SC2316E_BYP | Kiln2 | SC 2-316-E MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/441 | SC 2-316-E MOTION SWITCH BYPASSED
SC2316E_IM | Kiln2 | SC 2-316-E INTERLOCKS MET | None | PLC_DISCREAD | B3/439 | SC 2-316-E INTERLOCKS MET
SC2316E_PBS | Kiln2 | SC 2-316-E PC START | None | PLC_DISCWRITE | B100/664 | SC 2-316-E PC START
SC2316E_PBT | Kiln2 | SC 2-316-E PC STOP | None | PLC_DISCWRITE | B100/665 | SC 2-316-E PC STOP
SC2316EFTS_ALM | Kiln2 | SC 2-316-E FAILED TO START | On | PLC_ALARM | B101/321 | SC 2-316-E FAILED TO START
SC2316EMS_X | Kiln2 | SC 2-316-E AUX CONTACT | Off | PLC_DISCREAD | I:206/06 | SC 2-316-E STOPPED
SC2316EMSF_ALM | Kiln2 | SC 2-316-E MOTION SWITCH FAILURE | On | PLC_ALARM | B101/322 | SC 2-316-E MOTION SWITCH FAILURE
SC2316F_AUTO | Kiln2 | SC 2-316-F IN AUTO | None | PLC_DISCREAD | I:205/14 | SC 2-316-F IN AUTO
SC2316F_BYP | Kiln2 | SC 2-316-F MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/440 | SC 2-316-F MOTION SWITCH BYPASSED
SC2316F_IM | Kiln2 | SC 2-316-F INTERLOCKS MET | None | PLC_DISCREAD | B3/437 | SC 2-316-F INTERLOCKS MET
SC2316F_PBS | Kiln2 | SC 2-316-F PC START | None | PLC_DISCWRITE | B100/662 | SC 2-316-F PC START
SC2316F_PBT | Kiln2 | SC 2-316-F PC STOP | None | PLC_DISCWRITE | B100/663 | SC 2-316-F PC STOP
SC2316FFTS_ALM | Kiln2 | SC 2-316-F FAILED TO START | On | PLC_ALARM | B101/323 | SC 2-316-F FAILED TO START
SC2316FMS_X | Kiln2 | SC 2-316-F AUX CONTACT | Off | PLC_DISCREAD | I:206/05 | SC 2-316-F STOPPED
SC2316FMSF_ALM | Kiln2 | SC 2-316-F MOTION SWITCH FAILURE | On | PLC_ALARM | B101/324 | SC 2-316-F MOTION SWITCH FAILURE
SC2316FTS_ALM | Kiln2 | SC 2-316 FAILED TO START | On | PLC_ALARM | B101/311 | SC 2-316 FAILED TO START
SC2316G_AUTO | Kiln2 | SC 2-316-G IN AUTO | None | PLC_DISCREAD | I:205/13 | SC 2-316-G IN AUTO
SC2316G_BYP | Kiln2 | SC 2-316-G MOTION SWITCH BYPASSED | On | PLC_DISCWRITE | B100/439 | SC 2-316-G MOTION SWITCH BYPASSED
SC2316G_IM | Kiln2 | SC 2-316-G INTERLOCKS MET | None | PLC_DISCREAD | B3/435 | SC 2-316-G INTERLOCKS MET
SC2316G_PBS | Kiln2 | SC 2-316-G PC START | None | PLC_DISCWRITE | B100/660 | SC 2-316-G PC START
SC2316G_PBT | Kiln2 | SC 2-316-G PC STOP | None | PLC_DISCWRITE | B100/661 | SC 2-316-G PC STOP
SC2316GFTS_ALM | Kiln2 | SC 2-316-G FAILED TO START | On | PLC_ALARM | B101/325 | SC 2-316-G FAILED TO START
SC2316GMS_X | Kiln2 | SC 2-316-G AUX CONTACT | Off | PLC_DISCREAD | I:206/04 | SC 2-316-G STOPPED
SC2316GMSF_ALM | Kiln2 | SC 2-316-G MOTION SWITCH FAILURE | On | PLC_ALARM | B101/326 | SC 2-316-G MOTION SWITCH FAILURE
SC2316MS_X | Kiln2 | SC 2-316 AUX CONTACT | Off | PLC_DISCREAD | I:57/13 | SC 2-316 STOPPED
SC2316MSF_ALM | Kiln2 | SC 2-316 MOTION SWITCH FAILURE | On | PLC_ALARM | B101/312 | SC 2-316 MOTION SWITCH FAILURE
TE23051 | Kiln2 | TE 2-305-1 READING PH 2305 RAM 1 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:00 | TE 2-305-1 READING PH 2305 RAM 1
TE230511 | Kiln2 | TE 2-305-11 READING PH 2305 RAM 11 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:05 | TE 2-305-11 READING PH 2305 RAM 11
TE230513 | Kiln2 | TE 2-305-13 READING PH 2305 RAM 13 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:06 | TE 2-305-13 READING PH 2305 RAM 13
TE230515 | Kiln2 | TE 2-305-15 READING PH 2305 RAM 15 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:07 | TE 2-305-15 READING PH 2305 RAM 15
TE230517 | Kiln2 | TE 2-305-17 READING PH 2305 RAM 17 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N60:00 | TE 2-305-17 READING PH 2305 RAM 17
TE23053 | Kiln2 | TE 2-305-3 READING PH 2305 RAM 3 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:01 | TE 2-305-3 READING PH 2305 RAM 3
TE23055 | Kiln2 | TE 2-305-5 READING PH 2305 RAM 5 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:02 | TE 2-305-5 READING PH 2305 RAM 5
TE23057 | Kiln2 | TE 2-305-7 READING PH 2305 RAM 7 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:03 | TE 2-305-7 READING PH 2305 RAM 7
TE23059 | Kiln2 | TE 2-305-9 READING PH 2305 RAM 9 | F | 2516 | 5 | 0 | 0 | PLC_INTREAD | N49:04 | TE 2-305-9 READING PH 2305 RAM 9
TOT_DAY_K2LIME | Kiln2 | KILN 2 TOT TON LIME YESTERDAY | TON | 1200 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:238 | KILN 2 TOT TON LIME YESTERDAY
TOT_DAY_K2LIMERECLAMATION | Kiln2 | KILN 2 TOT TON LIME TO RECLAMATION YESTERDAY | TON | 2100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:417 | KILN 2 TOT TON LIME TO RECLAMATION YESTERDAY
TOT_DAY_K2LIMESILO | Kiln2 | KILN 2 TOT TON LIME TO SILO 3 YESTERDAY | TON | 2100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:418 | KILN 2 TOT TON LIME TO SILO 3 YESTERDAY
TOT_K2LIME | Kiln2 | KILN 2 LIME TOTALIZER | TON | 1200 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:237 | KILN 2 LIME TOTALIZER
VF2311_AUTO | Kiln2 | VF 2-311 SET IN AUTO MODE | None | PLC_DISCWRITE | B100/369 | VF 2-311 SET IN AUTO MODE
VF2311_FS | Kiln2 | VF 2-311 FIELD STOP | None | PLC_DISCREAD | I:105/2 | VF 2-311 FIELD STOP
VF2311_HI | Kiln2 | VF 2-311 HI SPEED (AUTO) | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:1 | VF 2-311 HI SPEED (AUTO)
VF2311_HITEMP | Kiln2 | VF 2-311 HIGH HIGH TEMP SETPOINT (AUTO) | DEG F | 700 | 1 | 0 | 0 | PLC_INTWRITE | N99:4 | VF 2-311 HIGH HIGH TEMP SETPOINT (AUTO)
VF2311_IM | Kiln2 | VF 2-311 INTERLOCKS MET | None | PLC_DISCREAD | B3/249 | VF 2-311 INTERLOCKS MET
VF2311_LOW | Kiln2 | VF 2-311 LOW SPEED SETPOINT (AUTO) | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:2 | VF 2-311 LOW SPEED SETPOINT (AUTO)
VF2311_LOWLOW | Kiln2 | VF 2-311 LOW LOW SPEED SETPOINT (AUTO) | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:3 | VF 2-311 LOW LOW SPEED SETPOINT (AUTO)
VF2311_MANSPD | Kiln2 | VF 2-311 MANUAL SPEED SETPOINT | % SPEED | 100 | 1 | 0 | 0 | PLC_INTWRITE | N99:0 | VF 2-311 MANUAL SPEED SETPOINT
VF2311_PBS | Kiln2 | VF 2-311 PC START | None | PLC_DISCWRITE | B100/36 | VF 2-311 PC START
VF2311_PBT | Kiln2 | VF 2-311 PC STOP | None | PLC_DISCWRITE | B100/37 | VF 2-311 PC STOP
VF2311_PC_AM | Kiln2 | VF 2-311 PC PID AUTO/MANUAL | None | PLC_DISCWRITE | B100:3/14 | VF 2-311 PC PID AUTO/MANUAL
VF2311FTS_ALM | Kiln2 | VF 2-311 FAILED TO START | On | PLC_ALARM | B101/278 | VF 2-311 FAILED TO START
VF2311HITEMP_ALM | Kiln2 | VF 2-311 DISCHARGE PRODUCT HIGH TEMP! | On | PLC_ALARM | B101/33 | VF 2-311 DISCHARGE PRODUCT HIGH TEMP!
VF2311MS_X | Kiln2 | VF 2-311 AUX FDBK | Off | PLC_DISCREAD | I:16/13 | VF 2-311 STOPPED
VF2311PCPID_SP | Kiln2 | VF 2-311 PC PID SP 0-100% | % | 100 | 0.1 | 0 | 0 | PLC_FLTWRITE | F9:25 | VF 2-311 PC PID SP 0-100%
VF2311PID_%RUN | Kiln2 | KILN 2 COOLER LEVEL PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:345 | KILN 2 COOLER LEVEL PID % RUNTIME - TODAY
VF2311PID_%RUN_YEST | Kiln2 | KILN 2 COOLER LEVEL PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:347 | KILN 2 COOLER LEVEL PID % RUNTIME - PAST
VF2311PID_ACT | Kiln2 | VF 2-311 ACTUAL SPEED % | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:32 | VF 2-311 ACTUAL SPEED %
VF2311PID_AM | Kiln2 | VF 2-311 PID IN AUTO/MANUAL 0=AUTO 1=MAN | None | PLC_DISCWRITE | N79:0/1 | VF 2-311 PID IN AUTO/MANUAL 0=AUTO 1=MAN
VF2311PID_AVAIL | Kiln2 | KILN 2 COOLER LEVEL PID AVAIL RUN HOURS - TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:344 | KILN 2 COOLER LEVEL PID AVAIL RUN HOURS - TODAY
VF2311PID_AVAIL_YEST | Kiln2 | KILN 2 COOLER LEVEL PID AVAIL RUN HOURS - PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:346 | KILN 2 COOLER LEVEL PID AVAIL RUN HOURS - PAST
VF2311PID_CV | Kiln2 | VF 2-311 PID CV (VF SPEED) |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N79:24 | VF 2-311 PID CV (VF SPEED)
VF2311PID_DB | Kiln2 | VF 2-311 PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N79:9 | VF 2-311 PID DEADBAND
VF2311PID_DR | Kiln2 | VF 2311 PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N79:5 | VF 2311 PID DR
VF2311PID_ER | Kiln2 | VF 2-311 PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N79:15 | VF 2-311 PID ERROR
VF2311PID_PG | Kiln2 | VF 2-311 PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N79:3 | VF 2-311 PID PG
VF2311PID_PV | Kiln2 | VF 2-311 PID PV (COOLER LVL) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N79:23 | VF 2-311 PID PV (COOLER LVL) 0-4095
VF2311PID_RT | Kiln2 | VF 2-311 PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N79:4 | VF 2-311 PID RT
VF2311PID_SP | Kiln2 | VF 2-311 PID SP 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N79:2 | VF 2-311 PID SP 0-4095
VF2311PID_TB | Kiln2 | VF 2-311 PID TB (VF SPEED) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N79:25 | VF 2-311 PID TB (VF SPEED) 0-4095
VF2311PID_UT | Kiln2 | VF 2-311 PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | T4:222.PRE | VF 2-311 PID UPDATE TIME
VF2311PIDHI_SP | Kiln2 | VF 2-311 PID HI SPD SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:5 | VF 2-311 PID HI SPD SP
VF2311PIDLOW_SP | Kiln2 | VF 2-311 PID LOW SPD SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N102:4 | VF 2-311 PID LOW SPD SP
VF2311SPD_SP | Kiln2 | VF 2311 SPEED SETPOINT | % | 5000 | 0 | 0 | 0 | PLC_INTREAD | N92:24 | VF 2311 SPEED SETPOINT
VF2311TRANS_ALM | Kiln2 | VF 2-311 TRANSPORT FAILURE!! | Off | PLC_ALARM | B101/28 | VF 2-311 TRANSPORT FAILURE!!
WF2601_IM | Kiln2 | WF 2-601 AUX FDBK | None | PLC_DISCREAD | B3/399 | WF 2-601 AUX FDBK
WF2601_OFF6HRS | Kiln2 | WF 2-601 Off For 6 Hours | None | PLC_DISCREAD | T4:707.DN
WF2601_PBS | Kiln2 | WF 2-601 PC START | None | PLC_DISCWRITE | B100/68 | WF 2-601 PC START
WF2601_PBT | Kiln2 | WF 2-601 PC STOP | None | PLC_DISCWRITE | B100/69 | WF 2-601 PC STOP
WF2601_SP | Kiln2 | WF 2-601 WEIGH FEED PC SETPOINT | TPH | 15 | 0.01 | 0 | 0 | PLC_FLTREAD | F71:00 | WF 2-601 WEIGH FEED PC SETPOINT
WF2601_SSA_HMI | Kiln2 | WF 2-601 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1411
WF2601_TOT | Kiln2 | KILN 2 COAL TOTALIZER | TONS | 300 | 1 | 0 | 0 | PLC_INTREAD | C5:5.ACC | KILN 2 COAL TOTALIZER
WF2601_TOT_DAY | Kiln2 | KILN 2 COAL TOTALIZER - DAILY | TONS | 300 | 1 | 0 | 0 | PLC_FLTREAD | F9:18 | KILN 2 COAL TOTALIZER - DAILY
WF2601_WT | Kiln2 | WF 2-601 ACTUAL FEED RATE | TPH | 15 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:75 | WF 2-601 ACTUAL FEED RATE
WF2601ALMSP_MAX | Kiln2 | WF 2-601 MAX FEED RATE ALARM SETPOINT | TPH | 12 | 1 | 0 | 1 | PLC_INTWRITE | N7:35 | WF 2-601 MAX FEED RATE ALARM SETPOINT
WF2601ALMSP_MIN | Kiln2 | WF 2-601 MIN FEED RATE ALARM SETPOINT | TPH | 12 | 1 | 0 | 1 | PLC_INTWRITE | N7:34 | WF 2-601 MIN FEED RATE ALARM SETPOINT
WF2601FTS_ALM | Kiln2 | WF 2-601 FAILED TO START | On | PLC_ALARM | B101/335 | WF 2-601 FAILED TO START
WF2601HIGHFEED_ALM | Kiln2 | WF 2-601 HIGH COAL FEED RATE ALARM | On | PLC_ALARM | B101/024 | WF 2-601 HIGH COAL FEED RATE ALARM
WF2601HIPID_SP | Kiln2 | WF 2-601 HI SPEED PID SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N75:11 | WF 2-601 HI SPEED PID SP
WF2601LOWFEED_ALM | Kiln2 | WF 2-601 LOW COAL FEED RATE ALARM | On | PLC_ALARM | B101/25 | WF 2-601 LOW COAL FEED RATE ALARM
WF2601LOWPID_SP | Kiln2 | WF 2-601 LOW PID SPEED SP | % | 100 | 1 | 0 | 0 | PLC_INTWRITE | N75:12 | WF 2-601 LOW PID SPEED SP
WF2601MS_X | Kiln2 | WF 2-601 AUX CONTACT | Off | PLC_DISCREAD | I:14/17 | WF 2-601 STOPPED
WF2601PID_%RUN | Kiln2 | KILN 2 FUEL BELT PID % RUNTIME - TODAY | % | 100 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:349 | KILN 2 FUEL BELT PID % RUNTIME - TODAY
WF2601PID_%RUN_YEST | Kiln2 | KILN 2 FUEL BELT PID % RUNTIME - PAST | % | 100 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:351 | KILN 2 FUEL BELT PID % RUNTIME - PAST
WF2601PID_AM | Kiln2 | WF 2-601 PID AUTO = 0 MANUAL = 1 | On | PLC_DISCREAD | N75:00/01 | WF 2-601 PID IS IN MANUAL
WF2601PID_AVAIL | Kiln2 | KILN 2 FUEL BELT PID AVAIL RUN HOURS- TODAY | HRS | 24 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:348 | KILN 2 FUEL BELT PID AVAIL RUN HOURS- TODAY
WF2601PID_AVAIL_YEST | Kiln2 | KILN 2 FUEL BELT PID AVAIL RUN HOURS- PAST | HRS | 24 | 0.01 | 0 | 0 | PLC_FLTREAD | F9:350 | KILN 2 FUEL BELT PID AVAIL RUN HOURS- PAST
WF2601PID_CV | Kiln2 | WF 2-601 PID CV (WF 2-601 %) |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N75:24 | WF 2-601 PID CV (WF 2-601 %)
WF2601PID_DB | Kiln2 | WF 2-601 PID DEADBAND |  | 500 | 1 | 0 | 0 | PLC_INTREAD | N75:9 | WF 2-601 PID DEADBAND
WF2601PID_DR | Kiln2 | WF 2-601 PID DR | 0.01 MIN | 1000 | 1 | 0 | 0 | PLC_INTREAD | N75:5 | WF 2-601 PID DR
WF2601PID_ER | Kiln2 | WF 2-601 PID ERROR |  | 4095 | 5 | 0 | -4095 | PLC_INTREAD | N75:15 | WF 2-601 PID ERROR
WF2601PID_PG | Kiln2 | WF 2-601 PID PG | 0.01 | 1000 | 1 | 0 | 0 | PLC_INTREAD | N75:3 | WF 2-601 PID PG
WF2601PID_PV | Kiln2 | WF2-601 PID PV (TPH) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N75:23 | WF2-601 PID PV (TPH) 0-4095
WF2601PID_RT | Kiln2 | WF 2-601 PID RT | 0.01 MIN/REPEAT | 1000 | 1 | 0 | 0 | PLC_INTREAD | N75:4 | WF 2-601 PID RT
WF2601PID_SP | Kiln2 | WF 2-601 PID SP - SP = TON/HR |  | 4095 | 1 | 0 | 0 | PLC_INTREAD | N75:2 | WF 2-601 PID SP - SP = TON/HR
WF2601PID_TB | Kiln2 | WF2-601 PID TB (WF 2-601 %) 0-4095 |  | 4095 | 5 | 0 | 0 | PLC_INTREAD | N75:25 | WF2-601 PID TB (WF 2-601 %) 0-4095
WF2601PID_TOG | Kiln2 | WF 2-601 PID ON/OFF TOGGLE | None | PLC_DISCWRITE | B100/545 | WF 2-601 PID ON/OFF TOGGLE
WF2601PID_UT | Kiln2 | WF 2-601 PID UPDATE TIME | SEC | 1000 | 1 | 0 | 0 | PLC_INTREAD | N75:13 | WF 2-601 PID UPDATE TIME
WF2601WT_TREND | Kiln2 | KILN #2 COAL MILL FEED RATE - TRENDING TAG |  | 15 | 0.1 | 0 | KILN #2 COAL MILL FEED RATE - TRENDING TAG | 0 | 0 | 0
WP_2326_3_MINUTE_WARNING | Kiln2 | WP 2-326-1&2 OFF FOR 3 MINUTES | On | PLC_ALARM | B101:37/3 | WP 2-326-1&2 OFF FOR 3 MINUTES!!! TAKE CORRECTIVE ACTION!!!!
WP_2326_4_MINUTE_WARNING | Kiln2 | WP 2-326-1&2 OFF FOR 4 MINUTES. START PUMPS! | On | PLC_ALARM | B101:37/4 | WP 2-326-1&2 OFF FOR 4 MINUTES!!! TAKE CORRECTIVE ACTION!!!!
WP2326_LAST | Kiln2 | WP 2-326 LAST PUMP RUNNING INDICATION | None | PLC_DISCREAD | B3/288 | WP 2-326 LAST PUMP RUNNING INDICATION
WP23261_IM | Kiln2 | WP 2-326-1 INTERLOCKS MET | None | PLC_DISCREAD | B3/365 | WP 2-326-1 INTERLOCKS MET
WP23261_PBS | Kiln2 | WP 2-326-1 PC START | None | PLC_DISCWRITE | B100/330 | WP 2-326-1 PC START
WP23261_PBT | Kiln2 | WP 2-326-1 PC STOP | None | PLC_DISCWRITE | B100/331 | WP 2-326-1 PC STOP
WP23261_SSA_HMI | Kiln2 | WP 2-326-1 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1436
WP23261FTS_ALM | Kiln2 | WP 2-326-1 FAILED TO START | On | PLC_ALARM | B101/332 | WP 2-326-1 FAILED TO START
WP23261MS_X | Kiln2 | WP 2-326-1 AUX FDBK | Off | PLC_DISCREAD | I:14/13 | WP 2-326-1 STOPPED
WP23262_IM | Kiln2 | WP 2-326-2 INTERLOCKS MET | None | PLC_DISCREAD | B3/367 | WP 2-326-2 INTERLOCKS MET
WP23262_PBS | Kiln2 | WP 2-326-2 PC START | None | PLC_DISCWRITE | B100/332 | WP 2-326-2 PC START
WP23262_PBT | Kiln2 | WP 2-326-2 PC STOP | None | PLC_DISCWRITE | B100/333 | WP 2-326-2 PC STOP
WP23262_SSA_HMI | Kiln2 | WP 2-326-2 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1441
WP23262FTS_ALM | Kiln2 | WP 2-326-2 FAILED TO START | On | PLC_ALARM | B101/333 | WP 2-326-2 FAILED TO START
WP23262MS_X | Kiln2 | WP 2-326-2 AUX FDBK | Off | PLC_DISCREAD | I:14/14 | WP 2-326-2 STOPPED
WP2326OFF5MIN_ALM | Kiln2 | WP 2-326 1 & 2 OFF FOR 5 MIN | On | PLC_DISCREAD | B3/1223 | WP 2-326 1 & 2 OFF FOR 5 MIN
WP3083_SSA_HMI | Kiln2 | WP 3-083 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1451
WP4369_SSA_HMI | Kiln2 | WP 4-369 Auto Man switch 0=Auto 1=Manual | None | PLC_DISCWRITE | B3/1446
YTDK2BLEEDAIRPID_AVAIL | Kiln2 | KILN 2 BLEED AIR AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:824
YTDK2BLEEDAIRPID_RUNTIME | Kiln2 | KILN 2 BLEED AIR RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:825
YTDK2COOLERLVLPID_AVAIL | Kiln2 | KILN 2 COOLER LEVEL PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:812
YTDK2COOLERLVLPID_RUNTIME | Kiln2 | KILN 2 COOLER LEVEL PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:813
YTDK2FTSPID_AVAIL | Kiln2 | KILN 2 FEED TO SPEED PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:818
YTDK2FUELWBPID_AVAIL | Kiln2 | KILN 2 FUEL WB PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:814
YTDK2FUELWBPID_RUNTIME | Kiln2 | KILN 2 FUEL WB PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:815
YTDK2HOODDRAFTPID_AVAIL | Kiln2 | KILN 2 HOODDRAFT PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:816
YTDK2KILNEXITPID_AVAIL | Kiln2 | KILN 2 KILN EXIT PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:820
YTDK2KILNEXITPID_RUNTIME | Kiln2 | KILN 2 KILN EXIT PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:821
YTDK2TEMPTEEPID_AVAIL | Kiln2 | KILN 2 TEMP TEE PID AVAILABLE RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:822
YTDK2TEMPTEEPID_RUNTIME | Kiln2 | KILN 2 TEMP TEE PID RUNTIME YTD |  | 10000 | 0.1 | 0 | 0 | PLC_FLTREAD | F9:823
BC8225_IM | Stone_Feed | BC 225 INTERLOCKS MET | None | PLC_DISCREAD | B3/449 | BC 225 INTERLOCKS MET
BC8225_PBS | Stone_Feed | BC 225 PC START | None | PLC_DISCWRITE | B100/0 | BC 225 PC START
BC8225_PBT | Stone_Feed | BC 225 PC STOP | None | PLC_DISCWRITE | B100/1 | BC 225 PC STOP
BC8225FTS_ALM | Stone_Feed | BC 225 FAILED TO START | On | PLC_ALARM | B101/167 | BC 225 FAILED TO START
BC8225MS_X | Stone_Feed | BC 225 AUX FDBK | Off | PLC_DISCREAD | I:24/15 | BC 225 STOPPED!!
BC8302_BYP | Stone_Feed | BC 8302 STONE FEED SYSTEM ZERO SPD BYPASS ON | None | PLC_DISCWRITE | B100/53 | BC 8302 STONE FEED SYSTEM ZERO SPD BYPASS ON
BC8302_IM | Stone_Feed | BC 302 INTERLOCKS MET | None | PLC_DISCREAD | B3:28/4 | BC 302 INTERLOCKS MET
BC8302_IT | Stone_Feed | BC 302 AMPS | Amp | 60 | 0.5 | 0 | 0 | PLC_FLTREAD | F9:48 | BC 302 AMPS
BC8302_PBS | Stone_Feed | BC 8302 STONE FEED SYSTEM PC START | None | PLC_DISCWRITE | B100/49 | BC 8302 STONE FEED SYSTEM PC START
BC8302_PBT | Stone_Feed | BC 8302 STONE FEED SYSTEM PC STOP | None | PLC_DISCWRITE | B100/47 | BC 8302 STONE FEED SYSTEM PC STOP
BC8302_PLUG | Stone_Feed | BC 8302 CHUTE TO VS 328 PLUGGED! | On | PLC_ALARM | B101/563 | BC 302 CHUTE TO VS 328 IS PLUGGED!
BC8302_PLUGBYP | Stone_Feed | BC 302 PLUGGED CHUTE INDICATOR BYPASS | On | PLC_DISCWRITE | B100/544 | BC 302 PLUGGED CHUTE BINDICATOR BYPASSED!
BC8302AMP_ALM | Stone_Feed | BC 302 HIGH AMPS! | On | PLC_ALARM | B100/100 | BC 302 HIGH AMPS!
BC8302FTS_ALM | Stone_Feed | BC 302 FAILED TO START! | On | PLC_ALARM | B101/174 | BC 302 FAILED TO START!
BC8302MS_X | Stone_Feed | BC 8302 AUX FDBK | Off | PLC_DISCREAD | I:27/03 | BC 302 STOPPED!!
BC8302MSF_ALM | Stone_Feed | BC 302 ZERO SPEED FAILURE! | On | PLC_ALARM | B101/175 | BC 302 ZERO SPEED FAILURE!
BC8303A_BYP | Stone_Feed | BC 303-A ZERO SPD BYPASSED | On | PLC_DISCWRITE | B100/14 | BC 303-A ZERO SPD BYPASSED
BC8303A_IM | Stone_Feed | BC 303-A INTERLOCKS MET | None | PLC_DISCREAD | B3:21/5 | BC 303-A INTERLOCKS MET
BC8303A_PBS | Stone_Feed | BC 8303-A STONE FEED SYSTEM PC START | None | PLC_DISCWRITE | B100/40 | BC 8303-A STONE FEED SYSTEM PC START
BC8303A_PBT | Stone_Feed | BC 8303-A STONE FEED SYSTEM PC STOP | None | PLC_DISCWRITE | B100/38 | BC 8303-A STONE FEED SYSTEM PC STOP
BC8303A_WEIGHSCALE | Stone_Feed | BC 303-A WEIGH SCALE FOR SB 2-304 | TPH | 300 | 0.5 | 0 | 0 | PLC_FLTREAD | F8:101 | BC 303-A WEIGH SCALE FOR SB 2-304
BC8303AFTS_ALM | Stone_Feed | BC 303-A FAILED TO START! | On | PLC_ALARM | B101/176 | BC 303-A FAILED TO START!
BC8303AMS_X | Stone_Feed | BC 8303-A AUX FDBK | Off | PLC_DISCREAD | I:57/07 | BC 303-A STOPPED!
BC8303AMSF_ALM | Stone_Feed | BC 303-A ZERO SPEED FAILURE! | On | PLC_ALARM | B101/177 | BC 303-A ZERO SPEED FAILURE!
BC8329_BYP | Stone_Feed | BC 329 STONE FEED SYSTEM ZERO SPD BYPASS | On | PLC_DISCWRITE | B100/3 | BC 329 STONE FEED SYSTEM ZERO SPD BYPASS
BC8329_IM | Stone_Feed | BC 329 INTERLOCKS MET | None | PLC_DISCREAD | B3:21/11 | BC 329 INTERLOCKS MET
BC8329_PBS | Stone_Feed | BC 8329 PC START | None | PLC_DISCWRITE | B100/43 | BC 8329 PC START
BC8329_PBT | Stone_Feed | BC 8329 PC STOP | None | PLC_DISCWRITE | B100/41 | BC 8329 PC STOP
BC8329_WEIGHSCALE | Stone_Feed | BC 329 WEIGH SCALE | TPH | 300 | 0.5 | 0 | 0 | PLC_FLTREAD | F8:100 | BC 329 WEIGH SCALE
BC8329FTS_ALM | Stone_Feed | BC 329 FAILED TO START! | On | PLC_ALARM | B101/179 | BC 329 FAILED TO START!
BC8329MS_X | Stone_Feed | BC 8328 AUX FDBK | Off | PLC_DISCREAD | I:27/06 | BC 329 STOPPED!!
BC8329MSF_ALM | Stone_Feed | BC 329 ZERO SPEED FAILURE! | On | PLC_ALARM | B101/180 | BC 329 ZERO SPEED FAILURE!
DG8330_MOV | Stone_Feed | DG 330 WILL NOW MOVE WITHOUT TIMER INDICATOR | None | PLC_DISCREAD | B3/223 | DG 330 WILL NOW MOVE WITHOUT TIMER INDICATOR
DG8330AUTO_ON | Stone_Feed | DG 8330 IS IN AUTO TRAVEL MODE | None | PLC_DISCWRITE | B100/80 | DG 8330 IS IN AUTO TRAVEL MODE
DG8330CONTACT_ALM | Stone_Feed | DG 330 DID NOT MAKE CONTACT! | On | PLC_ALARM | B101/183 | DG 330 DID NOT MAKE CONTACT!
DG8330K1STUCK_ALM | Stone_Feed | DG 330 STUCK TO KILN 1! | On | PLC_ALARM | B101/182 | DG 330 STUCK TO KILN 1!
DG8330K2STUCK_ALM | Stone_Feed | DG 330 STUCK TO KILN 2! | On | PLC_ALARM | B101/181 | DG 330 STUCK TO KILN 2!
DG8330KILN1_SET | Stone_Feed | DG 8330 IS SET TO KILN 1 | None | PLC_DISCWRITE | B100/83 | DG 8330 IS SET TO KILN 1
DG8330KILN2_SET | Stone_Feed | DG 8330 IS SET TO KILN 2 | None | PLC_DISCWRITE | B100/86 | DG 8330 IS SET TO KILN 2
DG8330TIMER1_SW | Stone_Feed | DG 8330 SWITCH TIMER | SEC | 120 | 0 | 0 | 0 | PLC_INTREAD | T4:283.ACC | DG 8330 SWITCH TIMER
DG8330TIMER1_TT | Stone_Feed | DG 330 TO KILN 1 | None | PLC_DISCREAD | T4:283.TT | DG 330 TO KILN 1
DG8330TIMER2_SW | Stone_Feed | DG 330 PURGE TIMER TIMING | SEC | 5000 | 0 | 0 | 0 | PLC_INTREAD | T4:449.ACC | DG 330 PURGE TIMER TIMING
DG8330TIMER2_TT | Stone_Feed | DG 330 TIMER TIMING | None | PLC_DISCREAD | T4:449.TT | DG 330 TIMER TIMING
DG8330TOK1MS_X | Stone_Feed | DG 8330 TO KILN 1 | None | PLC_DISCREAD | I:56/10 | DG 8330 TO KILN 1
DG8330TOK2MS_X | Stone_Feed | DG 8330 TO KILN 2 | None | PLC_DISCREAD | I:56/11 | DG 8330 TO KILN 2
FN8213_AUTO | Stone_Feed | FN 8-213 IN AUTO POSITION | None | PLC_DISCREAD | I:27/03 | FN 8-213 IN AUTO POSITION
FN8213_IM | Stone_Feed | FN 8213 INTERLOCKS MET | None | PLC_DISCREAD | B3:20/10 | FN 8213 INTERLOCKS MET
FN8213_PBS | Stone_Feed | FN 8213 PC START | None | PLC_DISCWRITE | B100/120 | FN 8213 PC START
FN8213_PBT | Stone_Feed | FN 8213 PC STOP | None | PLC_DISCWRITE | B100/121 | FN 8213 PC STOP
FN8213FTS_ALM | Stone_Feed | FN 213 FAILED TO START! | On | PLC_ALARM | B101/166 | FN 213 FAILED TO START!
FN8213MS_X | Stone_Feed | FN 8-213 AUX CONTACT | Off | PLC_DISCREAD | I:27/02 | FN 213 STOPPED!!
KILN1_BH_ALM_HORN | Stone_Feed | KILN1 BH SYSTEM START-UP ALARM HORN | None | KILN1_BH_READ | KILN1_BH_ALM_HORN
STONEESTOP_PBS | Stone_Feed | E-STOP FOR STONE FEED SYSTEM | None | PLC_DISCWRITE | B100/115 | E-STOP FOR STONE FEED SYSTEM
STONEFEEDTOTALIZER | Stone_Feed | TOTALIZER FOR STONE FEED TO BOTH KILNS | TONS | 10000 | 5 | 0 | 0 | PLC_FLTREAD | F8:13 | TOTALIZER FOR STONE FEED TO BOTH KILNS
STONEHORN | Stone_Feed | STONE SYSTEM START-UP HORN | None | PLC_ALARM | O:27/10 | STONE SYSTEM START-UP HORN
STONEHORN2 | Stone_Feed | STONE SYSTEM START-UP HORN - CHAT BIN | None | PLC_ALARM | O:27/11 | STONE SYSTEM START-UP HORN - CHAT BIN
STONEHORN3 | Stone_Feed | STONE SYSTEM START-UP HORN - BC 329 HP | None | PLC_ALARM | O:27/12 | STONE SYSTEM START-UP HORN - BC 329 HP
STONESTART_PBS | Stone_Feed | SYSTEM START FOR STONE FEED SYSTEM | None | PLC_DISCWRITE | B100/521
VF_301_MAX_FEEDERS_RUNNING | Stone_Feed | 2+ Rock Feeders Running | None | PLC_DISCREAD | B33:0/3
VF301_AUTO | Stone_Feed | VF 301 AUTO | Off | PLC_DISCWRITE | B100:7/1 | VF 301 AUTOMATIC FEED SYSTEM HAS STOPPED!
VF83011_AUTO | Stone_Feed | VF 301-1 IN AUTO POSITION | None | PLC_DISCREAD | I:55/00 | VF 301-1 IN AUTO POSITION
VF83011_IM | Stone_Feed | VF 301-1 INTERLOCKS MET | None | PLC_DISCREAD | B3:28/14 | VF 301-1 INTERLOCKS MET
VF83011_PBS | Stone_Feed | VF 301-1 PC START | None | PLC_DISCWRITE | B100:19/07 | VF 301-1 PC START
VF83011_PBT | Stone_Feed | VF 301-1 PC STOP | None | PLC_DISCWRITE | B100:7/0 | VF 301-1 PC STOP
VF83011_PCBYP | Stone_Feed | VF 301-1 PC FEEDER BYPASSED | On | PLC_DISCWRITE | B100/481 | VF 301-1 PC FEEDER BYPASSED
VF83011_SPEED | Stone_Feed | VF 301-1 VIBRATING FEEDER SPEED | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N111:20 | TE 1-305-13 READING PH 1305 RAM 13
VF83011FTS_ALM | Stone_Feed | VF 301-1 FAILED TO START | On | PLC_ALARM | B101/168 | VF 301-1 FAILED TO START
VF83011MS_X | Stone_Feed | VF 301-1 AUX FDBK | None | PLC_DISCREAD | I:54/0 | VF 301-1 AUX FDBK
VF83012_AUTO | Stone_Feed | VF 301-2 IN AUTO POSITION | None | PLC_DISCREAD | I:55/02 | VF 301-2 IN AUTO POSITION
VF83012_IM | Stone_Feed | VF 301-2 INTERLOCKS MET | None | PLC_DISCREAD | B3:28/15 | VF 301-2 INTERLOCKS MET
VF83012_PBS | Stone_Feed | VF 301-2 PC START | None | PLC_DISCWRITE | B100:9/06 | VF 301-2 PC START
VF83012_PBT | Stone_Feed | VF 301-2 PC STOP | None | PLC_DISCWRITE | B100:9/05 | VF 301-2 PC STOP
VF83012_PCBYP | Stone_Feed | VF 301-2 PC FEEDER BYPASSED | On | PLC_DISCWRITE | B100/482 | VF 301-2 PC FEEDER BYPASSED
VF83012_SPEED | Stone_Feed | VF 301-2 VIBRATING FEEDER SPEED | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N111:21 | TE 1-305-13 READING PH 1305 RAM 13
VF83012_START | Stone_Feed | VF 301-2 START TIME | SEC | 4000 | 0 | 0 | 0 | PLC_INTREAD | N7:0 | VF 301-2 START TIME
VF83012FTS_ALM | Stone_Feed | VF 301-2 FAILED TO START | On | PLC_ALARM | B101/169 | VF 301-2 FAILED TO START
VF83012MS_X | Stone_Feed | VF 301-2 AUX FDBK | None | PLC_DISCREAD | I:54/01 | VF 301-2 AUX FDBK
VF83013_AUTO | Stone_Feed | VF 301-3 IN AUTO POSITION | None | PLC_DISCREAD | I:55/04 | VF 301-3 IN AUTO POSITION
VF83013_IM | Stone_Feed | VF 301-3 INTERLOCKS MET | None | PLC_DISCREAD | B3:29/00 | VF 301-3 INTERLOCKS MET
VF83013_PBS | Stone_Feed | VF 301-3 PC START | None | PLC_DISCWRITE | B100:17/10 | VF 301-3 PC START
VF83013_PBT | Stone_Feed | VF 301-3 PC STOP | None | PLC_DISCWRITE | B100:17/06 | VF 301-3 PC STOP
VF83013_PCBYP | Stone_Feed | VF 301-3 PC FEEDER BYPASSED | On | PLC_DISCWRITE | B100/490 | VF 301-3 PC FEEDER BYPASSED
VF83013_SPEED | Stone_Feed | VF 301-3 VIBRATING FEEDER SPEED | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N111:22 | TE 1-305-13 READING PH 1305 RAM 13
VF83013_START | Stone_Feed | VF 301-3 START TIME | SEC | 4000 | 0 | 0 | 0 | PLC_INTREAD | N7:7 | VF 301-3 START TIME
VF83013FTS_ALM | Stone_Feed | VF 301-3 FAILED TO START | On | PLC_ALARM | B101/170 | VF 301-3 FAILED TO START
VF83013MS_X | Stone_Feed | VF 301-3 AUX FDBK | None | PLC_DISCREAD | I:54/02 | VF 301-3 AUX FDBK
VF83014_IM | Stone_Feed | VF 301-4 INTERLOCKS MET | None | PLC_DISCREAD | B3:29/01 | VF 301-4 INTERLOCKS MET
VF83014_PBS | Stone_Feed | VF 301-4 PC START | None | PLC_DISCWRITE | B100:17/14 | VF 301-4 PC START
VF83014_PBT | Stone_Feed | VF 301-4 PC STOP | None | PLC_DISCWRITE | B100:17/12 | VF 301-4 PC STOP
VF83014_PCBYP | Stone_Feed | VF 301-4 PC FEEDER BYPASSED | On | PLC_DISCWRITE | B100/491 | VF 301-4 PC FEEDER BYPASSED
VF83014_SPEED | Stone_Feed | VF 301-4 VIBRATING FEEDER SPEED | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N111:23 | TE 1-305-13 READING PH 1305 RAM 13
VF83014FTS_ALM | Stone_Feed | VF 301-4 FAILED TO START | On | PLC_ALARM | B101/171 | VF 301-4 FAILED TO START
VF83014MS_X | Stone_Feed | VF 301-4 AUX FDBK | None | PLC_DISCREAD | I:54/3 | VF 301-4 AUX FDBK
VF83015_IM | Stone_Feed | VF 301-5 INTERLOCKS MET | None | PLC_DISCREAD | B3:29/02 | VF 301-5 INTERLOCKS MET
VF83015_PBS | Stone_Feed | VF 301-5 PC START | None | PLC_DISCWRITE | B100:18/00 | VF 301-5 PC START
VF83015_PBT | Stone_Feed | VF 301-5 PC STOP | None | PLC_DISCWRITE | B100:17/15 | VF 301-5 PC STOP
VF83015_PCBYP | Stone_Feed | VF 301-5 PC FEEDER BYPASSED | On | PLC_DISCWRITE | B100/492 | VF 301-5 PC FEEDER BYPASSED
VF83015_SPEED | Stone_Feed | VF 301-5 VIBRATING FEEDER SPEED | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N111:1 | TE 1-305-13 READING PH 1305 RAM 13
VF83015_START | Stone_Feed | VF 8301-5 START TIME | SEC | 4000 | 0 | 0 | 0 | PLC_INTREAD | N7:1 | VF 8301-5 START TIME
VF83015FTS_ALM | Stone_Feed | VF 301-5 FAILED TO START | On | PLC_ALARM | B101/172 | VF 301-5 FAILED TO START
VF83015MS_X | Stone_Feed | VF 301-5 AUX FDBK | None | PLC_DISCREAD | I:54/4 | VF 301-5 AUX FDBK
VF83016_IM | Stone_Feed | VF 301-6 INTERLOCKS MET | None | PLC_DISCREAD | B3:29/03 | VF 301-6 INTERLOCKS MET
VF83016_PBS | Stone_Feed | VF 301-6 PC START | None | PLC_DISCWRITE | B100:18/04 | VF 301-6 PC START
VF83016_PBT | Stone_Feed | VF 301-6 PC STOP | None | PLC_DISCWRITE | B100:18/02 | VF 301-6 PC STOP
VF83016_PCBYP | Stone_Feed | VF 301-6 PC FEEDER BYPASSED | On | PLC_DISCWRITE | B100/495 | VF 301-6 PC FEEDER BYPASSED
VF83016_SPEED | Stone_Feed | VF 301-6 VIBRATING FEEDER SPEED | % | 100 | 0 | 0 | 0 | PLC_INTWRITE | N111:0 | TE 1-305-13 READING PH 1305 RAM 13
VF83016_START | Stone_Feed | VF 301-6 START TIME | SEC | 4000 | 0 | 0 | 0 | PLC_INTREAD | N7:10 | VF 301-6 START TIME
VF83016FTS_ALM | Stone_Feed | VF 301-6 FAILED TO START | On | PLC_ALARM | B101/173 | VF 301-6 FAILED TO START
VF83016MS_X | Stone_Feed | VF 301-6 AUX FDBK | None | PLC_DISCREAD | I:54/5 | VF 301-6 AUX FDBK
VF8301TIMERK1_ACC | Stone_Feed | KILN 1 VF 301 TIMER |  | 5000 | 0 | 0 | 0 | PLC_INTREAD | T4:82.ACC | KILN 1 VF 301 TIMER
VF8301TIMERK1_EN | Stone_Feed | VF 301 KILN 1 MASTER TIMER ENABLED | None | PLC_DISCREAD | T4:82.TT | VF 301 KILN 1 MASTER TIMER ENABLED
VF8301TIMERK1_SP | Stone_Feed | KILN 1 FEEDER START TIME | % | 5000 | 0 | 0 | 0 | PLC_FLTREAD | F28:1 | KILN 1 FEEDER START TIME
VF8301TIMERK2_ACC | Stone_Feed | KILN 2 VF 301 TIMER |  | 5000 | 0 | 0 | 0 | PLC_INTREAD | T4:356.ACC | KILN 2 VF 301 TIMER
VF8301TIMERK2_EN | Stone_Feed | KILN 2 VF 301 TIMER ENABLED | None | PLC_DISCREAD | T4:356.TT | KILN 2 VF 301 TIMER ENABLED
VF8301TIMERK2_SP | Stone_Feed | KILN 2 VF 301 START SEQUENCE SETPOINT | % | 5000 | 0 | 0 | 0 | PLC_FLTREAD | F28:2 | KILN 2 VF 301 START SEQUENCE SETPOINT
VS328_IT | Stone_Feed | VS 328 Amps | A | 20 | 0.25 | 0 | 0 | PLC_FLTREAD | F9:56 | VS 328 Amps Alarm!
VS8328_BYP | Stone_Feed | VS 8328 BYPASS IS ON | On | PLC_DISCWRITE | B100/51 | VS 8328 BYPASS IS ON
VS8328_IM | Stone_Feed | VS 328 INTERLOCKS MET | None | PLC_DISCREAD | B3:22/10 | VS 328 INTERLOCKS MET
VS8328_PBS | Stone_Feed | VS 8328 STONE FEED SYSTEM PC START | None | PLC_DISCWRITE | B100/46 | VS 8328 STONE FEED SYSTEM PC START
VS8328_PBT | Stone_Feed | VS 8328 STONE FEED SYSTEM PC STOP | None | PLC_DISCWRITE | B100/44 | VS 8328 STONE FEED SYSTEM PC STOP
VS8328MS_X | Stone_Feed | VS 328 AUX FDBK | Off | PLC_DISCREAD | I:27/05 | VS 328 STOPPED!!